Copyright 2006 AIA
MASTERSPEC Full Length
06/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15140 - DOMESTIC WATER PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Under-building slab and aboveground domestic water pipes, tubes, fittings, and specialties inside the building.

2. Encasement for piping.

3. Specialty valves.

4. Flexible connectors.

Retain one of first two subparagraphs below; delete both if water meters are furnished and installed by the utility company.

5. Water meters furnished by utility company for installation by Contractor.

6. Water meters.

7. Escutcheons.

8. Sleeves and sleeve seals.

9. Wall penetration systems.

B. Related Section:

Retain subparagraph below for requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 2 Section "Water Distribution" for water-service piping[ and water meters] outside the building from source to the point where water-service piping enters the building.

1.3 PERFORMANCE REQUIREMENTS

Revise this article to indicate specific loads determined by Project's structural engineer or see loads indicated on Drawings.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

A. Seismic Performance:  Domestic water piping and support and installation shall withstand effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

1.4 SUBMITTALS

First two paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For the following products:

1. Specialty valves.

2. Transition fittings.

3. Dielectric fittings.

4. Flexible connectors.

Retain first subparagraph below if water meters are furnished and installed by Contractor.

5. Water meters.

6. [Backflow preventers] [Vacuum breakers] [Backflow preventers and vacuum breakers].

7. Escutcheons.

8. Sleeves and sleeve seals.

9. Water penetration systems.

B. LEED Submittal:

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for solvent cements and adhesive primers.

1. Product Data for Credit EQ 4.1:  For solvent cements and adhesive primers, including printed statement of VOC content.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

C. Water Samples:  Specified in "Cleaning" Article.

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  For piping in equipment rooms and other congested areas, drawn to scale, on which the following items are shown and coordinated with each other, using input from Installers of the items involved:

Revise subparagraphs below to suit Project.

1. Fire-suppression-water piping.

2. Domestic water piping.

3. Compressed air piping.

4. HVAC hydronic piping.

5. <Insert item>.

E. Field quality-control reports.

1.5 QUALITY ASSURANCE

A. Piping materials shall bear label, stamp, or other markings of specified testing agency.

Retain first paragraph below if plastic piping materials are retained.

B. Comply with NSF 14 for plastic, potable domestic water piping and components.[ Include marking "NSF-pw" on piping.]

C. Comply with NSF 61 for potable domestic water piping and components.

1.6 PROJECT CONDITIONS

Retain this article if interruption of existing water service is required.

A. Interruption of Existing Water Service:  Do not interrupt water service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary water service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of water service.

2. Do not proceed with interruption of water service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.7 COORDINATION

Retain this article if large water meters will be mounted on concrete bases.

A. Coordinate sizes and locations of concrete bases with actual equipment provided.

PART 2 -  PRODUCTS

2.1 PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.  See "Piping Materials and Standards" Article in the Evaluations for a discussion of piping materials covered by referenced standards.

A. Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, fitting materials, and joining methods for specific services, service locations, and pipe sizes.

2.2 COPPER TUBE AND FITTINGS

Tube in first paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

A. Hard Copper Tube:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [and] [ASTM B 88, Type M (ASTM B 88M, Type C)] water tube, drawn temper.

Fittings in first subparagraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

1. Cast-Copper Solder-Joint Fittings:  ASME B16.18, pressure fittings.

Fittings in first subparagraph below are available in NPS 1/4 to NPS 8 (DN 8 to DN 200).

2. Wrought-Copper Solder-Joint Fittings:  ASME B16.22, wrought-copper pressure fittings.

Flanges in first subparagraph below are available in NPS 1/2 to NPS 12 (DN 15 to DN 300).

3. Bronze Flanges:  ASME B16.24, Class 150, with solder-joint ends.

Unions in first subparagraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100).

4. Copper Unions:  MSS SP-123, cast-copper-alloy, hexagonal-stock body, with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

Fittings in first subparagraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

5. Copper Pressure-Seal-Joint Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Elkhart Products Corporation; Industrial Division.

2) NIBCO INC.

3) Viega; Plumbing and Heating Systems.

4) <Insert manufacturer's name>.

b. NPS 2 (DN 50) and Smaller:  Wrought-copper fitting with EPDM-rubber O-ring seal in each end.

c. NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Cast-bronze or wrought-copper fitting with EPDM-rubber O-ring seal in each end.

Fittings in first subparagraph below are available in NPS 1/2 to NPS 2 (DN 15 to DN 50).

6. Copper Push-on-Joint Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) NVent LLC.

2) <Insert manufacturer's name>.

b. Description:  Cast-copper fitting complying with ASME B16.18 or wrought-copper fitting complying with ASME B 16.22; with stainless-steel teeth and EPDM-rubber O-ring seal in each end instead of solder-joint ends.

Extruded-tee connections in first subparagraph below can be used instead of tee fittings in copper tubing;  delete if prohibited.

7. Copper-Tube Extruded-Tee Connections:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) T-DRILL Industries Inc.

2) <Insert manufacturer's name>.

b. Description:  Tee formed in copper tube according to ASTM F 2014.

8. Grooved-Joint Copper-Tube Appurtenances:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Anvil International.

2) Shurjoint Piping Products.

3) Victaulic Company.

4) <Insert manufacturer's name>.

b. Copper Grooved-End Fittings:  ASTM B 75 (ASTM B 75M) copper tube or ASTM B 584 bronze castings.

AWWA C606 does not cover couplings in subparagraph below for grooved-end copper tubing.  At least one manufacturer makes this type of coupling with dimensions for copper tube and fittings.  Another manufacturer listed has a system for expanding the ends of copper tube and fittings so couplings for steel piping may be used.

c. Grooved-End-Tube Couplings:  Copper-tube dimensions and design similar to AWWA C606.  Include ferrous housing sections, EPDM-rubber gaskets suitable for hot and cold water, and bolts and nuts.

Tube in paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

B. Soft Copper Tube:  [ASTM B 88, Type K (ASTM B 88M, Type A)] [and] [ASTM B 88, Type L (ASTM B 88M, Type B)] water tube, annealed temper.

Fittings in first subparagraph below are available in NPS 1/4 to NPS 8 (DN 8 to DN 200).

1. Copper Solder-Joint Fittings:  ASME B16.22, wrought-copper pressure fittings.

Fittings in subparagraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

2. Copper Pressure-Seal-Joint Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Elkhart Products Corporation; Industrial Division.

2) NIBCO INC.

3) Viega; Plumbing and Heating Systems.

4) <Insert manufacturer's name>.

b. NPS 2 (DN 50) and Smaller:  Wrought-copper fitting with EPDM-rubber O-ring seal in each end.

c. NPS 3 and NPS 4 (DN 80 and DN 100):  Cast-bronze or wrought-copper fitting with EPDM-rubber O-ring seal in each end.

2.3 DUCTILE-IRON PIPE AND FITTINGS

Pipe in first paragraph below is available in NPS 3 to NPS 64 (DN 80 to DN 1600).

A. Mechanical-Joint, Ductile-Iron Pipe:  AWWA C151, with mechanical-joint bell and plain spigot end unless grooved or flanged ends are indicated.

Fittings in first subparagraph below are available in NPS 3 to NPS 48 (DN 80 to DN 1200).

1. Standard-Pattern, Mechanical-Joint Fittings:  AWWA C110, ductile or gray iron.

Fittings in subparagraph below are available in NPS 3 to NPS 24 (DN 80 to DN 600).

2. Compact-Pattern, Mechanical-Joint Fittings:  AWWA C153, ductile iron.

a. Glands, Gaskets, and Bolts:  AWWA C111, ductile- or gray-iron glands, rubber gaskets, and steel bolts.

Pipe in first paragraph below is available in NPS 3 to NPS 64 (DN 80 to DN 1600).

B. Push-on-Joint, Ductile-Iron Pipe:  AWWA C151, with push-on-joint bell and plain spigot end unless grooved or flanged ends are indicated.

Fittings in first subparagraph below are available in NPS 3 to NPS 48 (DN 80 to DN 1200).

1. Standard-Pattern, Push-on-Joint Fittings:  AWWA C110, ductile or gray iron.

a. Gaskets:  AWWA C111, rubber.

Fittings in subparagraph below are available in NPS 3 to NPS 24 (DN 80 to DN 600).

2. Compact-Pattern, Push-on-Joint Fittings:  AWWA C153, ductile iron.

a. Gaskets:  AWWA C111, rubber.

Pipe in paragraph below is available in NPS 3 to NPS 64 (DN 80 to DN 1600).

C. Plain-End, Ductile-Iron Pipe:  AWWA C151.

1. Grooved-Joint, Ductile-Iron-Pipe Appurtenances:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Anvil International.

2) Shurjoint Piping Products.

3) Star Pipe Products.

4) Victaulic Company.

5) <Insert manufacturer's name>.

b. Grooved-End, Ductile-Iron Fittings:  ASTM A 47/A 47M, malleable-iron castings or ASTM A 536, ductile-iron castings with dimensions matching pipe.

Couplings in subparagraph below are available in NPS 4 to NPS 24 (DN 100 to DN 600).  Other AWWA pipe size couplings in NPS 3 to NPS 36 (DN 80 to DN 900) are also available.

c. Grooved-End, Ductile-Iron-Pipe Couplings:  AWWA C606 for ductile-iron-pipe dimensions.  Include ferrous housing sections, EPDM-rubber gaskets suitable for hot and cold water, and bolts and nuts.

2.4 GALVANIZED-STEEL PIPE AND FITTINGS

Pipe in paragraph below is available in NPS 1/8 to NPS 26 (DN 6 to DN 650).

A. Galvanized-Steel Pipe:  ASTM A 53/A 53M, [Type E] <Insert type>, [Grade B] <Insert grade>, Standard Weight.  Include ends matching joining method.

Nipples in first subparagraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

1. Galvanized-Steel Pipe Nipples:  ASTM A 733, made of ASTM A 53/A 53M or ASTM A 106/A 106M, Standard Weight, seamless steel pipe with threaded ends.

Fittings in first subparagraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

2. Galvanized, Gray-Iron Threaded Fittings:  ASME B16.4, Class 125, standard pattern.

Unions in first subparagraph below are available in NPS 1/8 to NPS 4 (DN 6 to DN 100).

3. Malleable-Iron Unions:  ASME B16.39, Class 150, hexagonal-stock body with ball-and-socket, metal-to-metal, bronze seating surface, and female threaded ends.

Flanges in first subparagraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

4. Flanges:  ASME B16.1, Class 125, cast iron.

5. Grooved-Joint, Galvanized-Steel-Pipe Appurtenances:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1) Anvil International.

2) Shurjoint Piping Products.

3) Star Pipe Products.

4) Victaulic Company.

5) <Insert manufacturer's name>.

b. Galvanized, Grooved-End Fittings for Galvanized-Steel Piping:  ASTM A 47/A 47M, malleable-iron casting; ASTM A 106/A 106M, steel pipe; or ASTM A 536, ductile-iron casting; with dimensions matching steel pipe.

AWWA C606 covers couplings in subparagraph below in NPS 3/4 to NPS 24 (DN 20 to DN 600).

c. Grooved-End-Pipe Couplings for Galvanized-Steel Piping:  AWWA C606 for steel-pipe dimensions.  Include ferrous housing sections, EPDM-rubber gaskets suitable for hot and cold water, and bolts and nuts.

2.5 CPVC PIPING

Retain one of three paragraphs below.

Pipe in first paragraph below is available in NPS 1/4 to NPS 16 (DN 8 to DN 400).

A. CPVC Pipe:  ASTM F 441/F 441M, [Schedule 40] [and] [Schedule 80].

Fittings in first subparagraph below are available in NPS 1/4 to NPS 6 (DN 8 to DN 150).

1. CPVC Socket Fittings:  [ASTM F 438 for Schedule 40] [and] [ASTM F 439 for Schedule 80].

Socket fittings are available in NPS 1/4 to NPS 8 (DN 8 to DN 200).

Fittings in subparagraph below are available in NPS 1/4 to NPS 6 (DN 8 to DN 150).

2. CPVC Threaded Fittings:  ASTM F 437, Schedule 80.

Piping in first paragraph below is available in NPS 1-1/2 and NPS 2 (DN 40 and DN 50).

B. CPVC Piping System:  ASTM D 2846/D 2846M, SDR 11, pipe and socket fittings.

Tubing in paragraph below is available in NPS 1/4 to NPS 2 (DN 8 to DN 50).

C. CPVC Tubing System:  ASTM D 2846/D 2846M, SDR 11, tube and socket fittings.

2.6 PEX TUBE AND FITTINGS

Tubing in this article is available in NPS 1/8 to NPS 6 (DN 6 to DN 150).  Section Text limits PEX tubing to NPS 1 (DN 25) for use with metal fittings specified.

A. PEX Distribution System:  ASTM F 877, SDR 9 tubing.

Fittings in first subparagraph below are available in NPS 3/8 to NPS 1 (DN 10 to DN 25).

1. Fittings for PEX Tube:  ASTM F 1807, metal-insert type with copper or stainless-steel crimp rings and matching PEX tube dimensions.

2. Manifold:  Multiple-outlet, plastic or corrosion-resistant-metal assembly complying with ASTM F 877; with plastic or corrosion-resistant-metal valve for each outlet.

2.7 PVC PIPE AND FITTINGS

Pipe in this article is available in NPS 1/8 to NPS 24 (DN 6 to DN 600).

A. PVC Pipe:  ASTM D 1785, [Schedule 40] [and] [Schedule 80].

Fittings in first subparagraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

1. PVC Socket Fittings:  [ASTM D 2466 for Schedule 40] [and] [ASTM D 2467 for Schedule 80].

Fittings in subparagraph below are available in NPS 1/8 to NPS 6 (DN 6 to DN 150).

2. PVC Schedule 80 Threaded Fittings:  ASTM D 2464.

2.8 PIPING JOINING MATERIALS

A. Pipe-Flange Gasket Materials:  AWWA C110, rubber, flat face, 1/8 inch (3.2 mm) thick or ASME B16.21, nonmetallic and asbestos free, unless otherwise indicated; full-face or ring type unless otherwise indicated.

B. Metal, Pipe-Flange Bolts and Nuts:  ASME B18.2.1, carbon steel unless otherwise indicated.

C. Solder Filler Metals:  ASTM B 32, lead-free alloys.  Include water-flushable flux according to ASTM B 813.

D. Brazing Filler Metals:  AWS A5.8/A5.8M, BCuP Series, copper-phosphorus alloys for general-duty brazing unless otherwise indicated.

E. Solvent Cements for Joining CPVC Piping and Tubing:  ASTM F 493.

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1. Use CPVC solvent cement that has a VOC content of 490 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2. Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

F. Solvent Cements for Joining PVC Piping:  ASTM D 2564.  Include primer according to ASTM F 656.

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1. Use PVC solvent cement that has a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2. Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

G. Plastic, Pipe-Flange Gaskets, Bolts, and Nuts:  Type and material recommended by piping system manufacturer unless otherwise indicated.

2.9 ENCASEMENT FOR PIPING

A. Standard:  ASTM A 674 or AWWA C105.

B. Form:  [Sheet] [or] [Tube].

C. Material:  [LLDPE film of 0.008-inch (0.20-mm)] [LLDPE film of 0.008-inch (0.20-mm) minimum thickness or high-density, cross-laminated PE film of 0.004-inch (0.10-mm)] [High-density, cross-laminated PE film of 0.004-inch (0.10-mm)] minimum thickness.

D. Color:  [Black] [or] [Natural] <Insert color>.

2.10 SPECIALTY VALVES

A. Comply with requirements in Division 15 Section "General-Duty Valves for Plumbing Piping" for general-duty metal valves.

B. Comply with requirements in Division 15 Section "Domestic Water Piping Specialties" for balancing valves, drain valves, backflow preventers, and vacuum breakers.

Caution:  MSS SP-122 is a standard for plastic ball valves, but it is not comprehensive and additional data may be required for certain applications.  In general, end types and pressure and temperature ratings are required.  No applicable standards are available for plastic butterfly or check valves.  CPVC and PEX piping in this Section are rated for up to 180 deg F (82 deg C).  This Section assumes a maximum operating temperature of 140 deg F (60 deg C) for domestic water piping.  Verify that plastic valves are adequate for operating temperature of piping systems in this Project.

MSS SP-122 covers plastic ball valves in first paragraph below in NPS 1/4 to NPS 4 (DN 8 to DN 100).  Verify that valve selections are available from manufacturers retained.

C. CPVC Union Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Asahi/America, Inc.

c. Colonial Engineering, Inc.

d. Fischer, George Inc.

e. Hayward Flow Control Systems; Hayward Industrial Products, Inc.

f. IPEX Inc.

g. NIBCO INC.

h. Sloane, George Fischer, Inc.

i. Spears Manufacturing Company.

j. Thermoplastic Valves Inc.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-122.

b. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

c. Body Material:  CPVC.

d. Body Design:  Union type.

e. End Connections for Valves NPS 2 (DN 50) and Smaller:  Detachable, [socket] [or] [threaded].

f. End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Detachable, [socket] [socket or threaded] [threaded] [flanged].

g. Ball:  CPVC; full port.

h. Seals:  PTFE or EPDM-rubber O-rings.

i. Handle:  Tee shaped.

Valves in first paragraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100).  Verify that valve selections are available from manufacturers retained.

D. PVC Union Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Asahi/America, Inc.

c. Colonial Engineering, Inc.

d. Fischer, George Inc.

e. Hayward Flow Control Systems; Hayward Industrial Products, Inc.

f. IPEX Inc.

g. Jomar International, LTD.

h. King Bros. Industries.

i. Legend Valve.

j. McDonald, A.Y. Mfg. Co.

k. NIBCO INC.

l. Sloane, George Fischer, Inc.

m. Spears Manufacturing Company.

n. Thermoplastic Valves Inc.

o. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-122.

b. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

c. Body Material:  PVC.

d. Body Design:  Union type.

e. End Connections for Valves NPS 2 (DN 50) and Smaller:  Detachable, [socket] [or] [threaded].

f. End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Detachable, [socket] [socket or threaded] [threaded] [flanged].

g. Ball:  PVC; full port.

h. Seals:  PTFE or EPDM-rubber O-rings.

i. Handle:  Tee shaped.

Valves in first paragraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100).  Verify that valve selections are available from manufacturers retained.

E. CPVC Non-Union Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Asahi/America, Inc.

c. King Bros. Industries.

d. Legend Valve.

e. NIBCO INC.

f. Spears Manufacturing Company.

g. Thermoplastic Valves Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-122.

b. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

c. Body Material:  CPVC.

d. Body Design:  Non-union type.

e. End Connections:  Socket or threaded.

f. Ball:  CPVC; full or reduced port.

g. Seals:  PTFE or EPDM-rubber O-rings.

h. Handle:  Tee shaped.

Valves in first paragraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100).  Verify that valve selections are available from manufacturers retained.

F. PVC Non-Union Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Asahi/America, Inc.

c. Colonial Engineering, Inc.

d. Hayward Flow Control Systems; Hayward Industrial Products, Inc.

e. IPEX Inc.

f. Jomar International, LTD.

g. King Bros. Industries.

h. Legend Valve.

i. McDonald, A.Y. Mfg. Co.

j. NIBCO INC.

k. Sloane, George Fischer, Inc.

l. Spears Manufacturing Company.

m. Thermoplastic Valves Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-122.

b. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

c. Body Material:  PVC.

d. Body Design:  Non-union type.

e. End Connections:  Socket or threaded.

f. Ball:  PVC; full or reduced port.

g. Seals:  PTFE or EPDM-rubber O-rings.

h. Handle:  Tee shaped.

No standard is available for valves in first paragraph below.  Butterfly valves in this Section are limited to NPS 4 (DN 100).  Verify that valve selections are available from manufacturers retained.

G. CPVC Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Fischer, George Inc.

b. Hayward Flow Control Systems; Hayward Industrial Products, Inc.

c. NIBCO INC.

d. Sloane, George Fischer, Inc.

e. Spears Manufacturing Company.

f. Thermoplastic Valves Inc.

g. <Insert manufacturer's name>.

2. Description:

a. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

b. Body Material:  CPVC.

c. Body Design:  Lug or wafer type.

d. Seat:  EPDM rubber.

e. Seals:  PTFE or EPDM-rubber O-rings.

f. Disc:  CPVC.

g. Stem:  Stainless steel.

h. Handle:  Lever.

No standard is available for valves in first paragraph below.  Butterfly valves in this Section are limited to NPS 4 (DN 100).  Verify that valve selections are available from manufacturers retained.

H. PVC Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Asahi/America, Inc.

c. Colonial Engineering, Inc.

d. Fischer, George Inc.

e. Hayward Flow Control Systems; Hayward Industrial Products, Inc.

f. IPEX Inc.

g. Legend Valve.

h. NIBCO INC.

i. Sloane, George Fischer, Inc.

j. Spears Manufacturing Company.

k. Thermoplastic Valves Inc.

l. <Insert manufacturer's name>.

2. Description:

a. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

b. Body Material:  PVC.

c. Body Design:  Lug or wafer type.

d. Seat:  EPDM rubber.

e. Seals:  PTFE or EPDM-rubber O-rings.

f. Disc:  PVC.

g. Stem:  Stainless steel.

h. Handle:  Lever.

I. CPVC Ball Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Asahi/America, Inc.

c. Colonial Engineering, Inc.

d. Fischer, George Inc.

e. Hayward Flow Control Systems; Hayward Industrial Products, Inc.

f. IPEX Inc.

g. NIBCO INC.

h. Sloane, George Fischer, Inc.

i. Spears Manufacturing Company.

j. Thermoplastic Valves Inc.

k. <Insert manufacturer's name>.

2. Description:

a. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

b. Body Material:  CPVC.

c. Body Design:  Union-type ball check.

d. End Connections for Valves NPS 2 (DN 50) and Smaller:  Detachable, [socket] [or] [threaded].

e. End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Detachable, [socket] [socket or threaded] [threaded] [flanged].

f. Ball:  CPVC.

g. Seals:  EPDM- or FKM-rubber O-rings.

J. PVC Ball Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Asahi/America, Inc.

c. Colonial Engineering, Inc.

d. Fischer, George Inc.

e. Hayward Flow Control Systems; Hayward Industrial Products, Inc.

f. IPEX Inc.

g. Legend Valve.

h. NIBCO INC.

i. Sloane, George Fischer, Inc.

j. Spears Manufacturing Company.

k. Thermoplastic Valves Inc.

l. <Insert manufacturer's name>.

2. Description:

a. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

b. Body Material:  PVC.

c. Body Design:  Union-type ball check.

d. End Connections for Valves NPS 2 (DN 50) and Smaller:  Detachable, [socket] [or] [threaded].

e. End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Detachable, [socket] [socket or threaded] [threaded] [flanged].

f. Ball:  PVC.

g. Seals:  EPDM- or FKM-rubber O-rings.

K. CPVC Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Sloane, George Fischer, Inc.

b. Spears Manufacturing Company.

c. <Insert manufacturer's name>.

2. Description:

a. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

b. Body Material:  CPVC.

c. Body Design:  Nonrising stem.

d. End Connections for Valves NPS 2 (DN 50) and Smaller:  [Socket] [or] [Threaded].

e. End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  [Socket] [Socket or threaded] [Threaded] [Flanged].

f. Gate and Stem:  Plastic.

g. Seals:  EPDM rubber.

h. Handle:  Wheel.

L. PVC Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Asahi/America, Inc.

b. King Bros. Industries.

c. Sloane, George Fischer, Inc.

d. Spears Manufacturing Company.

e. <Insert manufacturer's name>.

2. Description:

a. Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> at [73 deg F (23 deg C)] <Insert temperature>.

b. Body Material:  PVC.

c. Body Design:  Nonrising stem.

d. End Connections for Valves NPS 2 (DN 50) and Smaller:  [Socket] [or] [Threaded].

e. End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  [Socket] [Socket or threaded] [Threaded] [Flanged].

f. Gate and Stem:  Plastic.

g. Seals:  EPDM rubber.

h. Handle:  Wheel.

2.11 TRANSITION FITTINGS

A. General Requirements:

1. Same size as pipes to be joined.

2. Pressure rating at least equal to pipes to be joined.

3. End connections compatible with pipes to be joined.

B. Fitting-Type Transition Couplings:  Manufactured piping coupling or specified piping system fitting.

Couplings in first paragraph below are available in NPS 1/2 to NPS 144 (DN 15 to DN 3600).

C. Sleeve-Type Transition Coupling:  AWWA C219.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cascade Waterworks Manufacturing.

b. Dresser, Inc.; Dresser Piping Specialties.

c. Ford Meter Box Company, Inc. (The).

d. JCM Industries.

e. Romac Industries, Inc.

f. Smith-Blair, Inc; a Sensus company.

g. Viking Johnson; c/o Mueller Co.

h. <Insert manufacturer's name>.

Fittings in first paragraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

D. Plastic-to-Metal Transition Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Charlotte Pipe and Foundry Company.

b. Harvel Plastics, Inc.

c. Spears Manufacturing Company.

d. <Insert manufacturer's name>.

2. Description:  [CPVC] [or] [PVC] one-piece fitting with manufacturer's Schedule 80 equivalent dimensions; one end with threaded brass insert and one solvent-cement-socket[ or threaded] end.

Unions in paragraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

E. Plastic-to-Metal Transition Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Colonial Engineering, Inc.

b. NIBCO INC.

c. Spears Manufacturing Company.

d. <Insert manufacturer's name>.

2. Description:  [CPVC] [or] [PVC] four-part union.  Include brass[ or stainless-steel] threaded end, solvent-cement-joint[ or threaded] plastic end, rubber O-ring, and union nut.

2.12 DIELECTRIC FITTINGS

A. General Requirements:  Assembly of copper alloy and ferrous materials or ferrous material body with separating nonconductive insulating material suitable for system fluid, pressure, and temperature.

Unions in first paragraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

B. Dielectric Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Capitol Manufacturing Company.

b. Central Plastics Company.

c. EPCO Sales, Inc.

d. Hart Industries International, Inc.

e. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

f. Zurn Plumbing Products Group; Wilkins Water Control Products.

g. <Insert manufacturer's name>.

2. Description:

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

a. Pressure Rating:  [150 psig (1035 kPa)] [250 psig (1725 kPa)] at 180 deg F (82 deg C).

b. End Connections:  Solder-joint copper alloy and threaded ferrous.

Flanges in first paragraph below are available in at least NPS 1-1/2 to NPS 4 (DN 40 to DN 100).

C. Dielectric Flanges:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Capitol Manufacturing Company.

b. Central Plastics Company.

c. EPCO Sales, Inc.

d. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

e. <Insert manufacturer's name>.

2. Description:

a. Factory-fabricated, bolted, companion-flange assembly.

Revise pressure rating in first subparagraph below to suit Project, or insert other options for specific applications.

b. Pressure Rating:  [150 psig (1035 kPa)] [175 psig (1200 kPa) minimum] [300 psig (2070 kPa)].

c. End Connections:  Solder-joint copper alloy and threaded ferrous; threaded solder-joint copper alloy and threaded ferrous.

Flanges in first paragraph below are available in at least NPS 1/2 to NPS 48 (DN 15 to DN 1200).

D. Dielectric-Flange Kits:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Advance Products & Systems, Inc.

b. Calpico, Inc.

c. Central Plastics Company.

d. Pipeline Seal and Insulator, Inc.

e. <Insert manufacturer's name>.

2. Description:

a. Nonconducting materials for field assembly of companion flanges.

Revise pressure rating in first subparagraph below to suit Project, or insert other options for specific applications.

b. Pressure Rating:  [150 psig (1035 kPa)] <Insert pressure>.

c. Gasket:  Neoprene or phenolic.

d. Bolt Sleeves:  Phenolic or polyethylene.

e. Washers:  Phenolic with steel backing washers.

Couplings in first paragraph below are available in at least NPS 1/2 to NPS 3 (DN 15 to DN 80).

E. Dielectric Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Calpico, Inc.

b. Lochinvar Corporation.

c. <Insert manufacturer's name>.

2. Description:

a. Galvanized-steel coupling.

Revise pressure rating and temperature in first subparagraph below to suit Project.

b. Pressure Rating:  300 psig (2070 kPa) at 225 deg F (107 deg C).

c. End Connections:  Female threaded.

d. Lining:  Inert and noncorrosive, thermoplastic.

Nipples in paragraph below are available in at least NPS 1/2 to NPS 4 (DN 15 to DN 100).

F. Dielectric Nipples:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Perfection Corporation; a subsidiary of American Meter Company.

b. Precision Plumbing Products, Inc.

c. Victaulic Company.

d. <Insert manufacturer's name>.

2. Description:

a. Electroplated steel nipple complying with ASTM F 1545.

b. Pressure Rating:  [300 psig (2070 kPa) at 225 deg F (107 deg C)] <Insert pressure and temperature>.

c. End Connections:  Male threaded or grooved.

d. Lining:  Inert and noncorrosive, propylene.

2.13 FLEXIBLE CONNECTORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Flex-Hose Co., Inc.

2. Flexicraft Industries.

3. Flex Pression, Ltd.

4. Flex-Weld, Inc.

5. Hyspan Precision Products, Inc.

6. Mercer Rubber Co.

7. Metraflex, Inc.

8. Proco Products, Inc.

9. Tozen Corporation.

10. Unaflex, Inc.

11. Universal Metal Hose; a Hyspan company

12. <Insert manufacturer's name>.

B. Bronze-Hose Flexible Connectors:  Corrugated-bronze tubing with bronze wire-braid covering and ends brazed to inner tubing.

1. Working-Pressure Rating:  Minimum [200 psig (1380 kPa)] [250 psig (1725 kPa)].

2. End Connections NPS 2 (DN 50) and Smaller:  Threaded copper pipe or plain-end copper tube.

3. End Connections NPS 2-1/2 (DN 65) and Larger:  Flanged copper alloy.

C. Stainless-Steel-Hose Flexible Connectors:  Corrugated-stainless-steel tubing with stainless-steel wire-braid covering and ends welded to inner tubing.

1. Working-Pressure Rating:  Minimum [200 psig (1380 kPa)] [250 psig (1725 kPa)].

2. End Connections NPS 2 (DN 50) and Smaller:  Threaded steel-pipe nipple.

3. End Connections NPS 2-1/2 (DN 65) and Larger:  Flanged steel nipple.

2.14 WATER METERS

LEED Credit EA 5 requires water meters to measure fixture use versus irrigation.

Retain this article if Contractor is to furnish water meters and water meters are to be installed inside the building.  Verify type of water meter required by the utility company and authorities having jurisdiction.

Retain first paragraph below for water meters NPS 2 (DN 50) and smaller.  Displacement-type meters with plastic cases and complying with AWWA C 710 are also available.

A. Displacement-Type Water Meters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. AALIANT; a Venture Measurement Product Line.

b. ABB.

c. Badger Meter, Inc.

d. Carlon Meter.

e. Mueller Company; Water Products Division.

f. Schlumberger Limited; Water Division.

g. Sensus Metering Systems.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  AWWA C700.

b. Pressure Rating:  150-psig (1035-kPa) working pressure.

c. Body Design:  Nutating disc; totalization meter.

d. Registration:  In gallons (liters) or cubic feet (cubic meters) as required by utility.

e. Case:  Bronze.

f. End Connections:  Threaded.

Retain first paragraph below for water meters NPS 1-1/2 to NPS 10 (DN 40 to DN 250).

B. Turbine-Type Water Meters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. AALIANT; a Venture Measurement Product Line.

b. ABB.

c. Badger Meter, Inc.

d. Hays Fluid Controls.

e. Master Meter, Inc.

f. McCrometer.

g. Mueller Company; Water Products Division.

h. Schlumberger Limited; Water Division.

i. SeaMetrics Inc.

j. Sensus Metering Systems.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  AWWA C701.

b. Pressure Rating:  [150-psig (1035-kPa)] <Insert pressure> working pressure.

c. Body Design:  Turbine; totalization meter.

d. Registration:  In gallons (liters) or cubic feet (cubic meters) as required by utility company .

e. Case:  Bronze.

f. End Connections for Meters NPS 2 (DN 50) and Smaller:  Threaded.

g. End Connections for Meters NPS 2-1/2 (DN 65) and Larger:  Flanged.

Retain first paragraph below for water meters NPS 3 (DN 80) and larger.  NPS 2 (DN 50) meters are also available.

C. Compound-Type Water Meters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABB.

b. Badger Meter, Inc.

c. Master Meter, Inc.

d. Mueller Company; Water Products Division.

e. Schlumberger Limited; Water Division.

f. Sensus Metering Systems.

g. <Insert manufacturer's name>.

2. Description:

a. Standard:  AWWA C702.

b. Pressure Rating:  150-psig (1035-kPa) working pressure.

c. Body Design:  With integral mainline and bypass meters; totalization meter.

d. Registration:  In gallons (liters) or cubic feet (cubic meters) as required by utility company.

e. Case:  Bronze.

f. Pipe Connections:  Flanged.

Retain first paragraph below for combined domestic and fire-protection water service.

D. Fire-Service-Type Water Meters:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Badger Meter, Inc.

b. Mueller Company; Water Products Division.

c. Schlumberger Limited; Water Division.

d. Sensus Metering Systems.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  AWWA C703 and UL listing.

b. Pressure Rating:  175-psig (1200-kPa) working pressure.

c. Body Design:

Retain one of first two subparagraphs below for body design of water meter.

1) Proportional, Detector-Type Water Meters:  With meter on bypass.

a) Bypass Meter:  [AWWA C701, turbine] [AWWA C702, compound] type with bronze case; size not less than one-half nominal size of main-line meter.

2) Turbine-Type Water Meters:  With strainer, and with meter on bypass.

a) Strainer:  Full size, matching water meter.

b) Bypass Meter:  AWWA C701, turbine type with bronze case; not less than NPS 2 (DN 50).

d. Registration:  In gallons (liters) or cubic feet (cubic meters) as required by utility company.

e. Case:  Bronze.

f. Pipe Connections for Meters NPS 2 (DN 50) and Smaller:  Threaded.

g. Pipe Connections for Meters NPS 2-1/2 (DN 65) and Larger:  Flanged.

Retain one of two paragraphs below; delete both if not required.

E. Remote Registration System:  Direct-reading type complying with AWWA C706; modified with signal transmitting assembly, low-voltage connecting wiring, and remote register assembly as required by utility company.

F. Remote Registration System:  Encoder type complying with AWWA C707; modified with signal transmitting assembly, low-voltage connecting wiring, and remote register assembly as required by utility company.

2.15 ESCUTCHEONS

A. General:  Manufactured ceiling, floor, and wall escutcheons and floor plates.

B. One Piece, Cast Brass:  [Polished, chrome-plated] [or] [rough-brass] finish with setscrews.

C. One Piece, Deep Pattern:  Deep-drawn, box-shaped brass with chrome-plated finish.

D. One Piece, Stamped Steel:  Chrome-plated finish with [setscrew] [or] [spring clips].

E. Split Casting, Cast Brass:  [Polished, chrome-plated] [or] [rough-brass] finish with concealed hinge and setscrew.

F. Split Plate, Stamped Steel:  Chrome-plated finish with [concealed] [exposed-rivet] hinge, [setscrew] [or] [spring clips].

G. One-Piece Floor Plates:  Cast-iron flange[ with holes for fasteners].

H. Split-Casting Floor Plates:  Cast brass with concealed hinge.

2.16 SLEEVES

Wall-pipe sleeves in first paragraph below are available with many end variations.

A. Cast-Iron Wall Pipes:  Fabricated of cast iron, and equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop unless otherwise indicated.

B. Galvanized-Steel-Sheet Sleeves:  0.0239-inch (0.6-mm) minimum thickness; round tube closed with welded longitudinal joint.

C. Molded-PE Sleeves:  Reusable, PE, tapered-cup shaped, and smooth outer surface with nailing flange for attaching to wooden forms.

PVC sleeves in first two paragraphs below may be prohibited by fire authorities having jurisdiction.

D. Molded-PVC Sleeves:  Permanent, with nailing flange for attaching to wooden forms.

E. PVC-Pipe Sleeves:  ASTM D 1785, Schedule 40.

F. Galvanized-Steel-Pipe Sleeves:  ASTM A 53/A 53M, Type E, Grade B, Schedule 40, zinc-coated, with plain ends.

Sleeve in paragraph below is without seepage holes and cannot be used as a replacement for a floor drain.

G. Stack Sleeve Fittings:  Manufactured, cast-iron sleeve with integral clamping flange.  Include clamping ring and bolts and nuts for membrane flashing.

Retain subparagraph below if required.

1. Underdeck Clamp:  Clamping ring with setscrews.

2.17 SLEEVE SEALS

Retain this article if sleeve seals are required; if retaining, delete "Wall Penetration Systems" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Advance Products & Systems, Inc.

2. Calpico, Inc.

3. Metraflex, Inc.

4. Pipeline Seal and Insulator, Inc.

5. <Insert manufacturer's name>.

B. Description:  Modular sealing element unit, designed for field assembly, used to fill annular space between pipe and sleeve.

Retain "EPDM-rubber" option in first subparagraph below unless NBR gasket material is required because hydrocarbons are present in the soil.

1. Sealing Elements:  [EPDM-rubber] [NBR] interlocking links shaped to fit surface of pipe.  Include type and number required for pipe material and size of pipe.

2. Pressure Plates:  [Carbon steel] [Plastic] [Stainless steel].

3. Connecting Bolts and Nuts:  [Carbon steel, with corrosion-resistant coating,] [Stainless steel] of length required to secure pressure plates to sealing elements.

2.18 WALL PENETRATION SYSTEMS

Retain this article if wall penetration systems are required; if retaining, delete "Sleeve Seals" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. SIGMA.

2. <Insert manufacturer's name>.

B. Description:  Wall-sleeve assembly, consisting of housing and gland, gaskets, and pipe sleeve.

1. Carrier-Pipe Deflection:  Up to 5 percent without leakage.

2. Housing:  Ductile-iron casting with hub, waterstop, anchor ring, and locking devices.  Include gland, bolts, and nuts.

Retain "EPDM rubber" option in first two subparagraphs below unless NBR gasket material is required because hydrocarbons are present in the soil.

3. Housing-to-Sleeve Gasket:  [EPDM rubber] [NBR].

4. Housing-to-Carrier-Pipe Gasket:  AWWA C111, [EPDM rubber] [NBR].

5. Pipe Sleeve:  AWWA C151, ductile-iron pipe[ or ASTM A 53/A 53M, Schedule 40, zinc-coated steel pipe].

2.19 GROUT

A. Standard:  ASTM C 1107, Grade B, post-hardening and volume-adjusting, dry, hydraulic-cement grout.

B. Characteristics:  Nonshrink; recommended for interior and exterior applications.

C. Design Mix:  5000-psi (34.5-MPa), 28-day compressive strength.

D. Packaging:  Premixed and factory packaged.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Comply with requirements in Division 2 Section "Earthwork" for excavating, trenching, and backfilling.

3.2 PIPING INSTALLATION

See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of domestic water piping.  Indicated locations and arrangements are used to size pipe and calculate friction loss, expansion, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

B. Install copper tubing under building slab according to CDA's "Copper Tube Handbook."

C. Install ductile-iron piping under building slab with restrained joints according to AWWA C600 and AWWA M41.

D. Install underground [copper tube] [and] [ductile-iron pipe] in PE encasement according to ASTM A 674 or AWWA C105.

E. Install shutoff valve, hose-end drain valve, strainer, pressure gage, and test tee with valve, inside the building at each domestic water service entrance.  Comply with requirements in Division 15 Section "Meters and Gages for Plumbing Piping" for pressure gages and Division 15 Section "Domestic Water Piping Specialties" for drain valves and strainers.

F. Install shutoff valve immediately upstream of each dielectric fitting.

Retain first paragraph below if booster pumps are not required.

G. Install water-pressure-reducing valves downstream from shutoff valves.  Comply with requirements in Division 15 Section "Domestic Water Piping Specialties" for pressure-reducing valves.

H. Install domestic water piping level [with 0.25 percent slope downward toward drain] [without pitch] and plumb.

Retain first paragraph below if water meters are inside the building.

I. Rough-in domestic water piping for water-meter installation according to utility company's requirements.

Retain first paragraph below if piping is required to withstand seismic design loads.

J. Install seismic restraints on piping.  Comply with requirements in Division 15 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment" for seismic-restraint devices.

K. Install piping concealed from view and protected from physical contact by building occupants unless otherwise indicated and except in equipment rooms and service areas.

L. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

M. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal, and coordinate with other services occupying that space.

N. Install piping adjacent to equipment and specialties to allow service and maintenance.

O. Install piping to permit valve servicing.

P. Install nipples, unions, special fittings, and valves with pressure ratings the same as or higher than system pressure rating used in applications below unless otherwise indicated.

Q. Install piping free of sags and bends.

R. Install fittings for changes in direction and branch connections.

S. Install PEX piping with loop at each change of direction of more than 90 degrees.

T. Install unions in copper tubing at final connection to each piece of equipment, machine, and specialty.

U. Install pressure gages on suction and discharge piping from each plumbing pump and packaged booster pump.  Comply with requirements in Division 15 Section "Meters and Gages for Plumbing Piping" for pressure gages.

Retain first paragraph below if hot-water circulation pumps are controlled by thermostats.

V. Install thermostats in hot-water circulation piping.  Comply with requirements in Division 15 Section "Domestic Water Pumps" for thermostats.

W. Install thermometers on[ inlet and] outlet piping from each water heater.  Comply with requirements in Division 15 Section "Meters and Gages for Plumbing Piping" for thermometers.

3.3 JOINT CONSTRUCTION

A. Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

B. Remove scale, slag, dirt, and debris from inside and outside of pipes, tubes, and fittings before assembly.

C. Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads.

2. Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.

D. Brazed Joints:  Join copper tube and fittings according to CDA's "Copper Tube Handbook," "Brazed Joints" Chapter.

E. Soldered Joints:  Apply ASTM B 813, water-flushable flux to end of tube.  Join copper tube and fittings according to ASTM B 828 or CDA's "Copper Tube Handbook."

F. Pressure-Sealed Joints:  Join copper tube and pressure-seal fittings with tools recommended by fitting manufacturer.

G. Copper-Tubing, Push-on Joints:  Clean end of tube.  Measure insertion depth with manufacturer's depth gage.  Join copper tube and push-on-joint fittings by inserting tube to measured depth.

H. Extruded-Tee Connections:  Form tee in copper tube according to ASTM F 2014.  Use tool designed for copper tube; drill pilot hole, form collar for outlet, dimple tube to form seating stop, and braze branch tube into collar.

I. Copper-Tubing Grooved Joints:  Roll groove end of tube.  Assemble coupling with housing, gasket, lubricant, and bolts.  Join copper tube and grooved-end fittings according to AWWA C606 for roll-grooved joints.

J. Ductile-Iron-Piping Grooved Joints:  Cut groove end of pipe.  Assemble coupling with housing, gasket, lubricant, and bolts.  Join ductile-iron pipe and grooved-end fittings according to AWWA C606 for ductile-iron-pipe, cut-grooved joints.

K. Steel-Piping Grooved Joints:  [Cut] [Cut or roll] [Roll] groove end of pipe.  Assemble coupling with housing, gasket, lubricant, and bolts.  Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe grooved joints.

L. Flanged Joints:  Select appropriate asbestos-free, nonmetallic gasket material in size, type, and thickness suitable for domestic water service.  Join flanges with gasket and bolts according to ASME B31.9.

M. Plastic Piping Solvent-Cement Joints:  Clean and dry joining surfaces.  Join pipe and fittings according to the following:

1. Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.  Apply primer.

2. CPVC Piping:  Join according to ASTM D 2846/D 2846M Appendix.

3. PVC Piping:  Join according to ASTM D 2855.

N. PEX Piping Joints:  Join according to ASTM F 1807.

O. Dissimilar-Material Piping Joints:  Make joints using adapters compatible with materials of both piping systems.

3.4 VALVE INSTALLATION

A. General-Duty Valves:  Comply with requirements in Division 15 Section "General-Duty Valves for Plumbing Piping" for valve installations.

B. Install shutoff valve close to water main on each branch and riser serving plumbing fixtures or equipment, on each water supply to equipment, and on each water supply to plumbing fixtures that do not have supply stops.  Use ball or gate valves for piping NPS 2 (DN 50) and smaller.  Use butterfly or gate valves for piping NPS 2-1/2 (DN 65) and larger.

NPS 1/2 or NPS 3/4 (DN 15 or DN 20) inlet hose-end drain valves may be adequate for application in first paragraph below.

C. Install drain valves for equipment at base of each water riser, at low points in horizontal piping, and where required to drain water piping.  Drain valves are specified in Division 15 Section "Domestic Water Piping Specialties."

1. Hose-End Drain Valves:  At low points in water mains, risers, and branches.

2. Stop-and-Waste Drain Valves:  Instead of hose-end drain valves where indicated.

Retain one of two paragraphs below.

D. Install balancing valve in each hot-water circulation return branch and discharge side of each pump and circulator.  Set balancing valves partly open to restrict but not stop flow.  Use ball valves for piping NPS 2 (DN 50) and smaller and butterfly valves for piping NPS 2-1/2 (DN 65) and larger.  Comply with requirements in Division 15 Section "Domestic Water Piping Specialties" for balancing valves.

E. Install calibrated balancing valves in each hot-water circulation return branch and discharge side of each pump and circulator.  Set calibrated balancing valves partly open to restrict but not stop flow.  Comply with requirements in Division 15 Section "Domestic Water Piping Specialties" for calibrated balancing valves.

3.5 TRANSITION FITTING INSTALLATION

A. Install transition couplings at joints of dissimilar piping.

B. Transition Fittings in Underground Domestic Water Piping:

1. NPS 1-1/2 (DN 40) and Smaller:  Fitting-type coupling.

2. NPS 2 (DN 50) and Larger:  Sleeve-type coupling.

C. Transition Fittings in Aboveground Domestic Water PipingNPS 2 (DN 50) and Smaller:  Plastic-to-metal transition [fittings] [or] [unions].

3.6 DIELECTRIC FITTING INSTALLATION

A. Install dielectric fittings in piping at connections of dissimilar metal piping and tubing.

B. Dielectric Fittings for [NPS 2 (DN 50)] <Insert pipe size> and Smaller:  Use dielectric [couplings] [couplings or nipples] [nipples] [unions].

C. Dielectric Fittings for [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>:  Use dielectric [flanges] [flange kits] [nipples].

D. Dielectric Fittings for [NPS 5 (DN 125)] <Insert pipe size> and Larger:  Use dielectric flange kits.

3.7 FLEXIBLE CONNECTOR INSTALLATION

A. Install flexible connectors in suction and discharge piping connections to each domestic water pump[ and in suction and discharge manifold connections to each domestic water booster pump].

B. Install bronze-hose flexible connectors in copper domestic water tubing.

C. Install stainless-steel-hose flexible connectors in steel domestic water piping.

3.8 WATER METER INSTALLATION

Retain this article to require Contractor to install water meters inside the building.

A. Rough-in domestic water piping [for water meter installation] [, and install water meters] according to utility company's requirements.

Retain one of first two paragraphs below.

B. Water meters will be furnished and installed by utility company.

C. Install water meters according to AWWA M6, utility company's requirements, and the following:

Retain one of first four paragraphs below.  Coordinate with meter descriptions retained in Part 2 for meters furnished and installed by Contractor; coordinate with utility company for meters provided by the utility company for installation by Contractor.

D. Install displacement-type water meters with shutoff valve on water-meter inlet.  Install valve on water-meter outlet and valved bypass around meter unless prohibited by authorities having jurisdiction.

E. Install turbine-type water meters with shutoff valve on water-meter inlet.  Install valve on water-meter outlet and valved bypass around meter unless prohibited by authorities having jurisdiction.

F. Install compound-type water meters with shutoff valves on water-meter inlet and outlet and on valved bypass around meter.  Support meters, valves, and piping on brick or concrete piers.

G. Install fire-service water meters with shutoff valves on water-meter inlet and outlet and on full-size valved bypass around meter.  Support meter, valves, and piping on brick or concrete piers.

Retain paragraph below if remote registration system is retained in "Water Meters" Article.

H. Install remote registration system according to standards of utility company and of authorities having jurisdiction.

3.9 HANGER AND SUPPORT INSTALLATION

Retain first paragraph below if Project is in a seismic area.

A. Comply with requirements in Division 15 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment" for seismic-restraint devices.

B. Comply with requirements in Division 15 Section "Hangers and Supports for Plumbing Piping and Equipment" for pipe hanger and support products and installation.

1. Vertical Piping:  MSS Type 8 or 42, clamps.

2. Individual, Straight, Horizontal Piping Runs:

a. 100 Feet (30 m) and Less:  MSS Type 1, adjustable, steel clevis hangers.

b. Longer Than 100 Feet (30 m):  MSS Type 43, adjustable roller hangers.

c. Longer Than 100 Feet (30 m) If Indicated:  MSS Type 49, spring cushion rolls.

3. Multiple, Straight, Horizontal Piping Runs 100 Feet (30 m) or Longer:  MSS Type 44, pipe rolls.  Support pipe rolls on trapeze.

4. Base of Vertical Piping:  MSS Type 52, spring hangers.

C. Support vertical piping and tubing at base and at each floor.

D. Rod diameter may be reduced one size for double-rod hangers, to a minimum of 3/8 inch (10 mm).

E. Install hangers for copper tubing with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 3/4 (DN 20) and Smaller:  60 inches (1500 mm) with 3/8-inch (10-mm) rod.

2. NPS 1 and NPS 1-1/4 (DN 25 and DN 32):  72 inches (1800 mm) with 3/8-inch (10-mm) rod.

3. NPS 1-1/2 and NPS 2 (DN 40 and DN 50):  96 inches (2400 mm) with 3/8-inch (10-mm) rod.

4. NPS 2-1/2 (DN 65):  108 inches (2700 mm) with 1/2-inch (13-mm) rod.

5. NPS 3 to NPS 5 (DN 80 to DN 125):  10 feet (3 m) with 1/2-inch (13-mm) rod.

6. NPS 6 (DN 150):  10 feet (3 m) with 5/8-inch (16-mm) rod.

7. NPS 8 (DN 200):  10 feet (3 m) with 3/4-inch (19-mm) rod.

F. Install supports for vertical copper tubing every 10 feet (3 m).

G. Install hangers for steel piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1-1/4 (DN 32) and Smaller:  84 inches (2100 mm) with 3/8-inch (10-mm) rod.

2. NPS 1-1/2 (DN 40):  108 inches (2700 mm) with 3/8-inch (10-mm) rod.

3. NPS 2 (DN 50):  10 feet (3 m) with 3/8-inch (10-mm) rod.

4. NPS 2-1/2 (DN 65):  11 feet (3.4 m) with 1/2-inch (13-mm) rod.

5. NPS 3 and NPS 3-1/2 (DN 80 and DN 90):  12 feet (3.7 m) with 1/2-inch (13-mm) rod.

6. NPS 4 and NPS 5 (DN 100 and DN 125):  12 feet (3.7 m) with 5/8-inch (16-mm) rod.

7. NPS 6 (DN 150):  12 feet (3.7 m) with 3/4-inch (19-mm) rod.

8. NPS 8 to NPS 12 (DN 200 to DN 300):  12 feet (3.7 m) with 7/8-inch (22-mm) rod.

H. Install supports for vertical steel piping every 15 feet (4.5 m).

I. Install vinyl-coated hangers for CPVC piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1 (DN 25) and Smaller:  36 inches (900 mm) with 3/8-inch (10-mm) rod.

2. NPS 1-1/4 to NPS 2 (DN 32 to DN 50):  48 inches (1200 mm) with 3/8-inch (10-mm) rod.

3. NPS 2-1/2 to NPS 3-1/2 (DN 65 to DN 90):  48 inches (1200 mm) with 1/2-inch (13-mm) rod.

4. NPS 4 and NPS 5 (DN 100 and DN 125):  48 inches (1200 mm) with 5/8-inch (16-mm) rod.

5. NPS 6 (DN 150):  48 inches (1200 mm) with 3/4-inch (19-mm) rod.

6. NPS 8 (DN 200):  48 inches (1200 mm) with 7/8-inch (22-mm) rod.

J. Install supports for vertical CPVC piping every 60 inches (1500 mm) for NPS 1 (DN 25) and smaller, and every 72 inches (1800 mm) for NPS 1-1/4 (DN 32) and larger.

K. Install vinyl-coated hangers for PEX piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 1 (DN 25) and Smaller:  32 inches (815 mm) with 3/8-inch (10-mm) rod.

L. Install hangers for vertical PEX piping every 48 inches (1200 mm).

M. Install vinyl-coated hangers for PVC piping with the following maximum horizontal spacing and minimum rod diameters:

1. NPS 2 (DN 50) and Smaller:  48 inches (1200 mm) with 3/8-inch (10-mm) rod.

2. NPS 2-1/2 to NPS 3-1/2 (DN 65 to DN 90):  48 inches (1200 mm) with 1/2-inch (13-mm) rod.

3. NPS 4 and NPS 5 (DN 100 and DN 125):  48 inches (1200 mm) with 5/8-inch (16-mm) rod.

4. NPS 6 (DN 150):  48 inches (1200 mm) with 3/4-inch (19-mm) rod.

5. NPS 8 (DN 200):  48 inches (1200 mm) with 7/8-inch (22-mm) rod.

N. Install supports for vertical PVC piping every 48 inches (1200 mm).

O. Support piping and tubing not listed in this article according to MSS SP-69 and manufacturer's written instructions.

3.10 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to equipment and machines to allow service and maintenance.

C. Connect domestic water piping to exterior water-service piping.  Use transition fitting to join dissimilar piping materials.

D. Connect domestic water piping to water-service piping with shutoff valve; extend and connect to the following:

1. Domestic Water Booster Pumps:  Cold-water suction and discharge piping.

2. Water Heaters:  Cold-water inlet and hot-water outlet piping in sizes indicated, but not smaller than sizes of water heater connections.

3. Plumbing Fixtures:  Cold- and hot-water supply piping in sizes indicated, but not smaller than required by plumbing code.  Comply with requirements in Division 15 plumbing fixture Sections for connection sizes.

4. Equipment:  Cold- and hot-water supply piping as indicated, but not smaller than equipment connections.  Provide shutoff valve and union for each connection.  Use flanges instead of unions for NPS 2-1/2 (DN 65) and larger.

3.11 ESCUTCHEON INSTALLATION

A. Install escutcheons for penetrations of walls, ceilings, and floors.

B. Escutcheons for New Piping:

1. Piping with Fitting or Sleeve Protruding from Wall:  One piece, deep pattern.

2. Bare Piping at Wall and Floor Penetrations in Finished Spaces:  One piece, [cast brass with polished chrome-plated finish] [stamped steel with set screw] [stamped steel with set screw or spring clips] [stamped steel with spring clips].

3. Bare Piping at Ceiling Penetrations in Finished Spaces:  [One piece, cast brass with polished chrome-plated finish] [One piece or split casting, cast brass with polished chrome-plated finish] [Split casting, cast brass with polished chrome-plated finish] [One piece, stamped steel with set screw] [One piece or split plate, stamped steel with set screw] [Split plate, stamped steel with set screw].

4. Bare Piping in Unfinished Service Spaces:  One piece, [cast brass with polished chrome-plated finish] [cast brass with rough-brass finish] [stamped steel with set screw] [stamped steel with spring clips] [stamped steel with set screw or spring clips].

5. Bare Piping in Equipment Rooms:  One piece, [cast brass] [stamped steel with set screw] [stamped steel with spring clips] [stamped steel with set screw or spring clips].

6. Bare Piping at Floor Penetrations in Equipment Rooms:  One-piece floor plate.

C. Escutcheons for Existing Piping:

1. Chrome-Plated Piping:  Split casting, cast brass with chrome-plated finish.

2. Insulated Piping:  Split plate, stamped steel with [concealed] [exposed-rivet] [concealed or exposed-rivet] hinge and spring clips.

3. Bare Piping at Wall and Floor Penetrations in Finished Spaces:  Split [casting, cast brass with chrome-plated finish] [plate, stamped steel with concealed hinge and spring clips].

4. Bare Piping at Ceiling Penetrations in Finished Spaces:  Split [casting, cast brass with chrome-plated finish] [plate, stamped steel with concealed hinge and set screw].

5. Bare Piping in Unfinished Service Spaces:  Split [casting, cast brass with polished chrome-plated finish] [casting, cast brass with rough-brass finish] [plate, stamped steel with concealed hinge and set screw or spring clips] [plate, stamped steel with concealed or exposed-rivet hinge and set screw or spring clips] [plate, stamped steel with exposed-rivet hinge and set screw or spring clips].

6. Bare Piping in Equipment Rooms:  Split [casting, cast brass] [plate, stamped steel with set screw or spring clips].

7. Bare Piping at Floor Penetrations in Equipment Rooms:  Split-casting floor plate.

3.12 SLEEVE INSTALLATION

A. General Requirements:  Install sleeves for pipes and tubes passing through penetrations in floors, partitions, roofs, and walls.

B. Sleeves are not required for core-drilled holes.

C. Permanent sleeves are not required for holes formed by removable PE sleeves.

D. Cut sleeves to length for mounting flush with both surfaces unless otherwise indicated.

E. Install sleeves in new partitions, slabs, and walls as they are built.

F. For interior wall penetrations, seal annular space between sleeve and pipe or pipe insulation using joint sealants appropriate for size, depth, and location of joint.  Comply with requirements in Division 7 Section "Joint Sealants" for joint sealants.

G. For exterior wall penetrations above grade, seal annular space between sleeve and pipe using joint sealants appropriate for size, depth, and location of joint.  Comply with requirements in Division 7 Section "Joint Sealants" for joint sealants.

H. For exterior wall penetrations below grade, seal annular space between sleeve and pipe using [sleeve seals] [wall penetration systems] specified in this Section.

I. Seal space outside of sleeves in concrete slabs and walls with grout.

Revise first paragraph below as required for seismic design conditions.  Coordinate sleeve requirements with pipe insulation specified in Division 15 Section "Plumbing Insulation."

J. Install sleeves that are large enough to provide [1/4-inch (6.4-mm)] <Insert dimension> annular clear space between sleeve and pipe or pipe insulation unless otherwise indicated.

K. Install sleeve materials according to the following applications:

1. Sleeves for Piping Passing through Concrete Floor Slabs:  [Molded PE] [Molded PVC] [Steel pipe] <Insert type>.

2. Sleeves for Piping Passing through Concrete Floor Slabs of Mechanical Equipment Areas or Other Wet Areas:  [Steel pipe] [Stack sleeve fittings] <Insert type>.

a. Extend sleeves [2 inches (50 mm)] <Insert dimension> above finished floor level.

b. For pipes penetrating floors with membrane waterproofing, extend cast-iron sleeve fittings below floor slab as required to secure clamping ring if ring is specified.  Secure flashing between clamping flanges.  Install section of cast-iron soil pipe to extend sleeve to [2 inches (50 mm)] <Insert dimension> above finished floor level.  Comply with requirements in Division 7 Section "Sheet Metal Flashing and Trim" for flashing.

3. Sleeves for Piping Passing through Gypsum-Board Partitions:

a. [PVC pipe] [Steel pipe] <Insert type> sleeves for pipes smaller than NPS 6 (DN 150).

b. [Galvanized-steel sheet] <Insert type> sleeves for pipes NPS 6 (DN 150) and larger.

c. Exception:  Sleeves are not required for water supply tubes and waste pipes for individual plumbing fixtures if escutcheons will cover openings.

4. Sleeves for Piping Passing through Concrete Roof Slabs:  [Molded PE] [Molded PVC] [Steel pipe] <Insert type>.

5. Sleeves for Piping Passing through Exterior Concrete Walls:

a. [Steel pipe] <Insert type> sleeves for pipes smaller than NPS 6 (DN 150).

b. [Cast-iron wall pipe] <Insert type> sleeves for pipes NPS 6 (DN 150) and larger.

c. Install sleeves that are large enough to provide [1-inch (25-mm)] <Insert dimension> annular clear space between sleeve and pipe or pipe insulation when sleeve seals are used.

d. Do not use sleeves when wall penetration systems are used.

6. Sleeves for Piping Passing through Interior Concrete Walls:

a. [PVC pipe] [Steel pipe] <Insert type> sleeves for pipes smaller than NPS 6 (DN 150).

b. [Galvanized-steel sheet] <Insert type> sleeves for pipes NPS 6 (DN 150) and larger.

L. Fire-Barrier Penetrations:  Maintain indicated fire rating of walls, partitions, ceilings, and floors at pipe penetrations.  Seal pipe penetrations with firestop materials.  Comply with requirements in Division 7 Section "Through-Penetration Firestop Systems" for firestop materials and installations.

3.13 SLEEVE SEAL INSTALLATION

If retaining this article, delete "Wall Penetration System Installation" Article.  Sleeve seals in this article are used in exterior concrete and masonry walls for a watertight seal around water-service piping entries into the building.  These seals typically require installation in a sleeve for proper operation.

A. Install sleeve seals in sleeves in exterior concrete walls at water-service piping entries into building.

B. Select type and number of sealing elements required for pipe material and size.  Position pipe in center of sleeve.  Assemble sleeve seal components and install in annular space between pipe and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

3.14 WALL PENETRATION SYSTEM INSTALLATION

If retaining this article, delete "Sleeve Seal Installation" Article.  Wall penetration systems in this article are used in new, exterior concrete walls for a watertight seal around water-service piping entries into the building.  Do not specify a separate sleeve for locations where these units are used.

A. Install wall penetration systems in new, exterior concrete walls.

B. Assemble wall penetration system components with sleeve pipe.  Install so that end of sleeve pipe and face of housing are flush with wall.  Adjust locking devices to secure sleeve pipe in housing.

3.15 IDENTIFICATION

A. Identify system components.  Comply with requirements in Division 15 Section "Identification for Plumbing Piping and Equipment" for identification materials and installation.

B. Label pressure piping with system operating pressure.

3.16 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.  Portions of testing and inspecting requirements in this article are taken from model plumbing codes.  Verify requirements are applicable to location of this Project.

B. Piping Inspections:

1. Do not enclose, cover, or put piping into operation until it has been inspected and approved by authorities having jurisdiction.

2. During installation, notify authorities having jurisdiction at least one day before inspection must be made.  Perform tests specified below in presence of authorities having jurisdiction:

a. Roughing-in Inspection:  Arrange for inspection of piping before concealing or closing-in after roughing-in and before setting fixtures.

b. Final Inspection:  Arrange final inspection for authorities having jurisdiction to observe tests specified below and to ensure compliance with requirements.

3. Reinspection:  If authorities having jurisdiction find that piping will not pass tests or inspections, make required corrections and arrange for reinspection.

4. Reports:  Prepare inspection reports and have them signed by authorities having jurisdiction.

C. Piping Tests:

1. Fill domestic water piping.  Check components to determine that they are not air bound and that piping is full of water.

2. Test for leaks and defects in new piping and parts of existing piping that have been altered, extended, or repaired.  If testing is performed in segments, submit a separate report for each test, complete with diagram of portion of piping tested.

3. Leave new, altered, extended, or replaced domestic water piping uncovered and unconcealed until it has been tested and approved.  Expose work that was covered or concealed before it was tested.

4. Cap and subject piping to static water pressure of 50 psig (345 kPa) above operating pressure, without exceeding pressure rating of piping system materials.  Isolate test source and allow to stand for four hours.  Leaks and loss in test pressure constitute defects that must be repaired.

5. Repair leaks and defects with new materials and retest piping or portion thereof until satisfactory results are obtained.

6. Prepare reports for tests and for corrective action required.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements.  See Division 1 Section "Execution Requirements" for requirements for correcting the Work.

D. Domestic water piping will be considered defective if it does not pass tests and inspections.

E. Prepare test and inspection reports.

3.17 ADJUSTING

A. Perform the following adjustments before operation:

1. Close drain valves, hydrants, and hose bibbs.

2. Open shutoff valves to fully open position.

3. Open throttling valves to proper setting.

4. Adjust balancing valves in hot-water-circulation return piping to provide adequate flow.

a. Manually adjust ball-type balancing valves in hot-water-circulation return piping to provide flow of hot water in each branch.

b. Adjust calibrated balancing valves to flows indicated.

5. Remove plugs used during testing of piping and for temporary sealing of piping during installation.

6. Remove and clean strainer screens.  Close drain valves and replace drain plugs.

7. Remove filter cartridges from housings and verify that cartridges are as specified for application where used and are clean and ready for use.

8. Check plumbing specialties and verify proper settings, adjustments, and operation.

3.18 CLEANING

Portions of disinfecting requirements in this article are taken from model plumbing codes; revise if requirements vary.  Option in first paragraph below is for disinfection of non-potable domestic water piping.

A. Clean and disinfect potable[ and non-potable] domestic water piping as follows:

1. Purge new piping and parts of existing piping that have been altered, extended, or repaired before using.

2. Use purging and disinfecting procedures prescribed by authorities having jurisdiction; if methods are not prescribed, use procedures described in either AWWA C651 or AWWA C652 or follow procedures described below:

a. Flush piping system with clean, potable water until dirty water does not appear at outlets.

b. Fill and isolate system according to either of the following:

1) Fill system or part thereof with water/chlorine solution with at least 50 ppm (50 mg/L) of chlorine.  Isolate with valves and allow to stand for 24 hours.

2) Fill system or part thereof with water/chlorine solution with at least 200 ppm (200 mg/L) of chlorine.  Isolate and allow to stand for three hours.

c. Flush system with clean, potable water until no chlorine is in water coming from system after the standing time.

d. Submit water samples in sterile bottles to authorities having jurisdiction.  Repeat procedures if biological examination shows contamination.

Retain first paragraph below if disinfection of non-potable domestic water piping is not required.  If disinfection is required, delete first paragraph below and revise paragraph above.

B. Clean non-potable domestic water piping as follows:

1. Purge new piping and parts of existing piping that have been altered, extended, or repaired before using.

2. Use purging procedures prescribed by authorities having jurisdiction or; if methods are not prescribed, follow procedures described below:

a. Flush piping system with clean, potable water until dirty water does not appear at outlets.

b. Submit water samples in sterile bottles to authorities having jurisdiction.  Repeat procedures if biological examination shows contamination.

C. Prepare and submit reports of purging and disinfecting activities.

D. Clean interior of domestic water piping system.  Remove dirt and debris as work progresses.

3.19 PIPING SCHEDULE

A. Transition and special fittings with pressure ratings at least equal to piping rating may be used in applications below unless otherwise indicated.

B. Flanges and unions may be used for aboveground piping joints unless otherwise indicated.

Delete first paragraph below if prohibited.

C. Fitting Option:  Extruded-tee connections and brazed joints may be used on aboveground copper tubing.

The "Piping Schedule" Article below is organized to first present the service and pipe size or size range; then to present optional piping materials and joining methods.  Retain the services and sizes and size ranges applicable to the Project, then retain the selected piping materials and joining methods.  Coordinate selection of piping materials and joining methods with piping materials described in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.  Piping for this application matches exterior underground water service piping specified in Division 2 Section "Water Distribution."

D. Under-building-slab, domestic water, building service piping, [NPS 3 (DN 80) and smaller] <Insert pipe size range>, shall be[ one of] the following:

1. Soft copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper solder-joint fittings; and brazed] [copper pressure-seal fittings; and pressure-sealed] joints.

2. PVC, [Schedule 40 pipe; PVC, Schedule 40] [Schedule 80 pipe; PVC, Schedule 80] socket fittings; and solvent-cemented joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.  Piping for this application matches exterior underground water-service piping specified in Division 2 Section "Water Distribution."

E. Under-building-slab, domestic water, building-service piping, [NPS 4 to NPS 8 (DN 100 to DN 200) and larger] <Insert pipe size range>, shall be[ one of] the following:

1. Soft copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; wrought-copper solder-joint fittings; and brazed joints.

Caution:  Ductile-iron piping in first two subparagraphs below must be installed with restrained joints.

2. Mechanical-joint, ductile-iron pipe; [standard-] [or] [compact-] pattern mechanical-joint fittings; and mechanical joints.

3. Push-on-joint, ductile-iron pipe; [standard-] [or] [compact-] pattern push-on-joint fittings; and gasketed joints.

4. Plain-end, ductile-iron pipe; grooved-joint, ductile-iron-pipe appurtenances; and grooved joints.

5. PVC, [Schedule 40 pipe; PVC, Schedule 40] [Schedule 80 pipe; PVC, Schedule 80] socket fittings; and solvent-cemented joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.  Piping for the application below matches exterior underground combined water-service and fire-service-main piping specified in Division 15 Section "Water Distribution."

F. Under-building slab, combined domestic water, building-service, and fire-service-main piping, [NPS 6 to NPS 12 (DN 150 to DN 300)] <Insert pipe size range>, shall be[ one of] the following:

Caution:  Ductile-iron piping in first two subparagraphs below must be installed with restrained joints.

1. Mechanical-joint, ductile-iron pipe; [standard-] [or] [compact-] pattern mechanical-joint fittings; and mechanical joints.

2. Push-on-joint, ductile-iron pipe; [standard-] [or] [compact-] pattern push-on-joint fittings; and gasketed joints.

3. Plain-end, ductile-iron pipe; grooved-joint, ductile-iron-pipe appurtenances; and grooved joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

G. Under-building-slab, domestic water piping, [NPS 2 (DN 50) and smaller] <Insert pipe size range>, shall be[ one of] the following:

1. [Hard] [Hard or soft] [Soft] copper tube, ASTM B 88, Type L (ASTM B 88M, Type B); [wrought-copper solder-joint fittings; and brazed] [copper pressure-seal-joint fittings; and pressure-sealed] joints.

2. PVC, [Schedule 40 pipe; PVC, Schedule 40] [Schedule 80 pipe; PVC, Schedule 80] socket fittings; and solvent-cemented joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

H. Aboveground domestic water piping, [NPS 2 (DN 50) and smaller] <Insert pipe size range>, shall be[ one of] the following:

1. Galvanized-steel pipe and nipples; galvanized, gray-iron threaded fittings; and threaded joints.

2. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M, Type C)]; [cast-] [or] [wrought-] copper solder-joint fittings; and [brazed] [soldered] joints.

3. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [or] [ASTM B 88, Type M (ASTM B 88M, Type C)]; copper pressure-seal-joint fittings; and pressure-sealed joints.

4. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [or] [ASTM B 88, Type M (ASTM B 88M, Type C)]; copper push-on-joint fittings; and push-on joints.

5. CPVC, [Schedule 40 pipe; CPVC, Schedule 40] [Schedule 80 pipe; CPVC, Schedule 80] socket fittings; and solvent-cemented joints.

6. CPVC, Schedule 80 pipe; CPVC, Schedule 80 threaded fittings; and threaded joints.

7. CPVC Tubing System:  CPVC tube; CPVC socket fittings; and solvent-cemented joints.  [NPS 1-1/2 (DN 40) and NPS 2 (DN 50) CPVC pipe with CPVC socket fittings may be used instead of tubing.]

Tubing in first subparagraph below is available only in NPS 1 (DN 25) and smaller.

8. PEX Tube, NPS 1 (DN 25) and smaller; fittings for PEX tube; and crimped joints.

9. PVC, [Schedule 40 pipe; PVC, Schedule 40] [Schedule 80 pipe; PVC, Schedule 80] socket fittings; and solvent-cemented joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

I. Aboveground domestic water piping, [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, shall be[ one of] the following:

1. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M, Type C)]; [cast-] [or] [wrought-] copper solder-joint fittings; and [brazed] [soldered] joints.

2. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [or] [ASTM B 88, Type M (ASTM B 88M, Type C)]; copper pressure-seal-joint fittings; and pressure-sealed joints.

3. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [or] [ASTM B 88, Type M (ASTM B 88M, Type C)]; grooved-joint copper-tube appurtenances; and grooved joints.

4. Galvanized-steel pipe and nipples; galvanized, gray-iron threaded fittings; and threaded joints.

5. Galvanized-steel pipe; grooved-joint, galvanized-steel-pipe appurtenances; and grooved joints.

6. CPVC, [Schedule 40 pipe; CPVC, Schedule 40] [Schedule 80 pipe; CPVC, Schedule 80] socket fittings; and solvent-cemented joints.

7. CPVC, Schedule 80 pipe; CPVC, Schedule 80 threaded fittings; and threaded joints.

8. PVC, [Schedule 40 pipe; PVC, Schedule 40] [Schedule 80 pipe; PVC, Schedule 80] socket fittings; and solvent-cemented joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

J. Aboveground domestic water piping, [NPS 5 to NPS 8 (DN 125 to DN 200)] <Insert pipe size range>, shall be[ one of] the following:

1. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M, Type C)]; [cast-] [or] [wrought-] copper solder-joint fittings; and [brazed] [soldered] joints.

2. Hard copper tube, [ASTM B 88, Type L (ASTM B 88M, Type B)] [or] [ASTM B 88, Type M (ASTM B 88M, Type C)]; grooved-joint copper-tube appurtenances; and grooved joints.

3. Galvanized-steel pipe and nipples; galvanized, gray-iron threaded fittings; and threaded joints.

4. Galvanized-steel pipe; grooved-joint, galvanized-steel-pipe appurtenances; and grooved joints.

Schedule 40 pipe fittings in first subparagraph below are available only in NPS 6 (DN 150) and smaller.

5. CPVC, [Schedule 40 pipe; CPVC, Schedule 40] [Schedule 80 pipe; CPVC, Schedule 80] socket fittings; and solvent-cemented joints.

6. CPVC, Schedule 80 pipe; CPVC, Schedule 80 threaded fittings; and threaded joints.

7. PVC, [Schedule 40 pipe; PVC, Schedule 40] [Schedule 80 pipe; PVC, Schedule 80] socket fittings; and solvent-cemented joints.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

K. Aboveground, combined domestic-water-service and fire-service-main piping, [NPS 6 to NPS 12 (DN 150 to DN300)] <Insert pipe size range>, shall be[ one of] the following:

1. Plain-end, ductile-iron pipe; grooved-joint, ductile-iron-pipe appurtenances; and grooved joints.

2. Galvanized-steel pipe and nipples; galvanized, gray-iron threaded fittings; and threaded joints.

3. Galvanized-steel pipe; grooved-joint, galvanized-steel-pipe appurtenances; and grooved joints.

3.20 VALVE SCHEDULE

A. Drawings indicate valve types to be used.  Where specific valve types are not indicated, the following requirements apply:

1. Shutoff Duty:  Use ball or gate valves for piping NPS 2 (DN 50) and smaller.  Use butterfly, ball, or gate valves with flanged ends for piping NPS 2-1/2 (DN 65) and larger.

2. Throttling Duty:  Use ball or globe valves for piping NPS 2 (DN 50) and smaller.  Use butterfly or ball valves with flanged ends for piping NPS 2-1/2 (DN 65) and larger.

3. Hot-Water Circulation Piping, Balancing Duty:  [Calibrated] [Memory-stop] balancing valves.

4. Drain Duty:  Hose-end drain valves.

B. Use check valves to maintain correct direction of domestic water flow to and from equipment.

C. Iron grooved-end valves may be used with grooved-end piping.

Delete paragraph below and use metal valves if temperature rating may be exceeded.  Coordinate selection of "CPVC" or "PVC" option with "Specialty Valves" Article.

D. [CPVC] [and] [PVC] valves matching piping materials may be used.

END OF SECTION 15140

DOMESTIC WATER PIPING
15140 - 1

