Copyright 2001 AIA
MASTERSPEC
09/01 (R 12/02)

Copyright 2001 (R 12/02), The American Institute of Architects (AIA)

SECTION 15446 - SUMP PUMPS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following sump pumps and accessories, inside the building, for building storm drainage systems:

1. Wet-pit-mounted, vertical sump pumps.

2. Submersible sump pumps.

3. Sump pump [basins] [basins and pits] [pits].

4. Packaged, [pedestal] [pedestal and submersible] [submersible], drainage pump units.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Sewage Pumps" for application in sanitary drainage systems.

1.3 SUBMITTALS

A. Product Data:  For each type and size of sump pump specified.  Include certified performance curves with operating points plotted on curves, and rated capacities of selected models, furnished specialties, and accessories.

B. Shop Drawings:  Diagram power, signal, and control wiring.

C. Operation and Maintenance Data:  For each sump pump to include in emergency, operation, and maintenance manuals.

1.4 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of sump pumps and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Retain shipping flange protective covers and protective coatings during storage.

B. Protect bearings and couplings against damage.

C. Comply with pump manufacturer's written rigging instructions for handling.

1.6 COORDINATION

Select from options in paragraph below depending on whether Part 2 "Sump Pump Pits" or "Packaged Drainage Pump Units" Article is retained.

A. Coordinate size and location of concrete [bases] [bases and pits] [pits].  Concrete, reinforcement, and formwork requirements are specified in Division 3.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Refer to the Sump Pump Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 WET-PIT-MOUNTED, VERTICAL SUMP PUMPS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Alyan Pump Company.

2. Armstrong Pumps Inc.

3. Aurora Pump; Pentair Pump Group (The).

4. Chicago Pump Company; a division of Yeomans Chicago Corporation.

5. Deming Pumps; Crane Pumps & Systems.

6. Federal Pump Corp.

7. Ingersoll-Dresser Pumps.

8. Paco Pumps, Inc.

9. Sterling Peerless; Sterling Fluid Systems Group.

10. Swaby Manufacturing Co.

11. Tramco Pump Company.

12. Vertiflo Pump Company.

13. Weil Pump Company, Inc.

14. Weinman Div.; Crane Pumps & Systems.

15. Yeomans Chicago Corporation.

16. <Insert manufacturer's name.>

B. Description:  Factory-assembled and -tested, single-stage, centrifugal, end-suction sump pumps complying with UL 778.  Vertical, separately coupled, suspended pumps complying with HI 1.1-1.2 and HI 1.3 for wet-pit-volute sump pumps.

1. Pump Arrangement:  [Simplex] [Duplex] [Multiplex].

2. Casing:  Cast iron, with screened inlet and threaded connection for NPS 2 (DN 50) and smaller and flanged connection for NPS 2-1/2 (DN 65) and larger discharge piping.

3. Impeller:  [ASTM A 48/A 48M, Class No. 25 A or higher cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze]; statically and dynamically balanced[ nonclog design]; overhung, single suction, keyed and secured to shaft.

4. Pump Shaft and Sleeve Bearings:  [Stainless-steel] [Stainless-steel or steel] [Steel] shaft with bronze sleeve bearings.  Include oil-lubricated, intermediate sleeve bearings at 48-inch (1200-mm) maximum intervals if basin depth is more than 48 inches (1200 mm), and grease-lubricated, ball-type thrust bearings.

5. Pump and Motor Shaft Coupling:  Flexible, capable of absorbing torsional vibration and shaft misalignment.

C. Pump Discharge Piping:  Manufacturer's standard galvanized-steel or bronze pipe.

Select from options in first paragraph below depending on whether "Sump Pump Basins" or "Sump Pump Pits" Article is retained.

D. [Basin] [Pit] Cover:  Cast iron or steel with bituminous coating and strong enough to support pumps, motors, and controls.  See Part 2 "Sump Pump [Basins] [Pits]" Article for requirements.

E. Cover Shaft Seal:  Stuffing box, with graphite-impregnated braided-yarn rings and bronze packing gland.

F. Motor:  Single speed; grease-lubricated ball bearings.  Comply with requirements in Division 15 Section "Motors" with built-in thermal-overload protection appropriate for motor size and duty.

1. Mounting:  On vertical, cast-iron pedestal.

Controls in paragraph below are rod-and-float type.  Micropressure and mercury-float switches are also available.  Retain last option for duplex pump units.

G. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal-mounted float switches; with floats, float rods, and rod buttons.[ Include automatic alternator to alternate operation of pump units on successive cycles and to operate multiple units if one pump cannot handle load.]

Feature in subparagraph below is required for controlling turbulence in deep basins with rod-and-float-type controls.

1. Float Guide:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

Verify availability of alarm types with manufacturer.

2. High-Water Alarm:  Cover-mounted, [compression-probe] [mechanical-float-switch] [mercury-float-switch] [micropressure-switch] alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

H. Capacity and Characteristics:

1. System Capacity:  <Insert gpm (L/minute).>

2. Number of Pumps:  [One] [Two] <Insert other>.

3. Each Pump:

a. Capacity:  <Insert gpm (L/minute).>

b. Total Dynamic Head:  <Insert feet (kPa).>

c. Speed:  <Insert rpm.>

d. Discharge Pipe Size:  <Insert NPS (DN).>

e. Motor Horsepower:  <Insert value.>

f. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value.>

2) Phases:  [Single] [Three].

3) Hertz:  60.

g. Unit Electrical Characteristics:

1) Full-Load Amperes:  <Insert value.>

2) Minimum Circuit Ampacity:  <Insert value.>

3) Maximum Overcurrent Protection:  <Insert value.>

4. Alternator Control Required:  [Yes] [No].

2.3 SUBMERSIBLE SUMP PUMPS

Select sump pump basins and pits from "Sump Pump Basins" and "Sump Pump Pits" articles.

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. ABS Pumps, Inc.

2. Aermotor Pumps, Inc.

3. Barnes; Crane Pumps & Systems.

4. Bell & Gossett Domestic Pump; ITT Industries.

5. BJM Corporation.

6. EBARA International Corporation; Standard Pump Division.

7. Federal Pump Corp.

8. Gorman-Rupp Company (The).

9. Goulds Pumps; ITT Industries.

10. Grundfos Pumps Corp.

11. Liberty Pumps.

12. Little Giant Pump Co.

13. McDonald, A. Y. Mfg. Co.

14. Metropolitan Industries, Inc.

15. Myers, F. E.; Pentair Pump Group (The).

16. Paco Pumps, Inc.

17. Stancor, Inc.

18. Sta-Rite Industries, Inc.

19. Swaby Manufacturing Co.

20. Weil Pump Company, Inc.

21. Weinman Div.; Crane Pumps & Systems.

22. Zoeller Company.

23. <Insert manufacturer's name.>

Caution:  Verify that pump materials, features, and options are available for pumps selected.  See Editing Instruction No. 3 in the Evaluations for explanation of the terms "conventional" and "economy" used in the editor's notes and for guidance on selecting optional features for various levels of quality of submersible sump pumps.

In paragraph below, economy sump pumps are available in simplex only.

B. Description:  Factory-assembled and -tested, [simplex] [duplex] <Insert other>, single-stage, centrifugal, end-suction, submersible, direct-connected sump pumps complying with UL 778 and HI 1.1-1.2 and HI 1.3 for submersible sump pumps.

C. Casing:  Cast iron; with cast-iron inlet strainer, legs that elevate pump to permit flow into impeller, and vertical discharge with companion flange for piping connection.

D. Impeller:  [ASTM A 48/A 48M, Class No. 25 A or higher cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze] [stainless steel]; statically and dynamically balanced, semiopen nonclog design, overhung, single suction, keyed and secured to shaft.

Retain two paragraphs above or first two paragraphs below for conventional sump pumps.

E. Casing:  Stainless steel; with stainless-steel inlet strainer, legs that elevate pump to permit flow into impeller, and vertical discharge with companion flange suitable for piping connection.

F. Impeller:  Stainless steel or other corrosion-resistant material.

G. Casing and Impeller:  Cast-iron casing with metal inlet strainer and brass, bronze, or cast-iron impeller.

Retain paragraph above or below for economy sump pumps.

H. Casing and Impeller:  Cast-iron or plastic casing with inlet strainer and metal or plastic impeller.

Retain two paragraphs below for either conventional or economy sump pumps.

I. Pump and Motor Shaft:  [Stainless steel] [Steel], with factory-sealed, grease-lubricated ball bearings[ and double-mechanical seals].

J. Motor:  Hermetically sealed, capacitor-start type, with built-in overload protection; three-conductor waterproof power cable of length required, and with grounding plug and cable-sealing assembly for connection at pump.  Comply with requirements in Division 15 Section "Motors."

Retain subparagraph below only for conventional sump pumps and only if availability has been verified for pump selected.

1. Moisture-Sensing Probe:  Internal moisture sensor with moisture alarm.

K. Pump Discharge Piping:  Factory or field fabricated, [ASTM A 53/A 53M, Schedule 40, galvanized-steel pipe] [bronze pipe] [copper tube] <Insert other pipe material>.

Select from options in paragraph below depending on whether "Sump Pump Basins" or "Sump Pump Pits" Article is retained.

L. [Basin] [Pit] Cover:  Cast iron or steel with bituminous coating and strong enough to support controls.  See Part 2 "Sump Pump [Basins] [Pits]" Article for other requirements.

Retain one of four paragraphs and associated subparagraphs below for conventional sump pumps.

Controls in first two paragraphs below are rod-and-float type; use compression-probe, high-water alarm with this type of control.  Retain "Float Guide" Subparagraph for deep basins.

Retain paragraph below for simplex pump units.

M. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal-mounted float switch; with float, float rod, and rod buttons.

Retain paragraph below for duplex pump units.  Edit if unit includes three or more pumps.

N. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal-mounted float switch; with float, float rod, and rod buttons.  Include automatic alternator to alternate operation of pump units on successive cycles and to operate multiple units if one pump cannot handle load.

Controls in two paragraphs below are float- and micropressure-switch types.  Use matching-type high-water alarm with this type of control.

Retain paragraph below for simplex pump units.

O. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal mounted unless wall mounting is indicated; with two [mechanical- or mercury-float or micropressure] [mechanical-float] [mercury-float] [micropressure] switches in NEMA 250, Type 6 enclosures; mounting rod; and electric cables.

Retain paragraph below for duplex pump units.  Edit if unit includes three or more pumps.

P. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal mounted unless wall mounting is indicated; with three [mechanical- or mercury-float or micropressure] [mechanical-float] [mercury-float] [micropressure] switches in NEMA 250, Type 6 enclosures; mounting rod; and electric cables.  Include automatic alternator to alternate operation of pump units on successive cycles and to operate multiple units if one pump cannot handle load.

Feature in subparagraph below is required for controlling turbulence in deep basins with rod-and-float-type controls.

1. Float Guide:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

Retain one of two subparagraphs below.  Match mercury-float- or micropressure-switch alarm to its corresponding control.

2. High-Water Alarm:  Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

3. High-Water Alarm:  Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical- or mercury-float or micropressure] [mechanical-float] [mercury-float] [micropressure]-switch alarm matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Retain paragraph below for economy sump pumps.

Q. Controls:  NEMA 250, Type 6, 120-V ac, float switch, mounted on discharge piping.

If Project has more than one type of pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

R. Capacity and Characteristics:

1. System Capacity:  <Insert gpm (L/minute).>

2. Number of Pumps:  [One] [Two] <Insert other>.

3. Each Pump:

a. Capacity:  <Insert gpm (L/minute).>

b. Total Dynamic Head:  <Insert feet (kPa).>

c. Speed:  <Insert rpm.>

d. Discharge Pipe Size:  <Insert NPS (DN).>

e. Motor Horsepower:  <Insert value.>

f. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value.>

2) Phases:  [Single] [Three].

3) Hertz:  60.

g. Unit Electrical Characteristics:

1) Full-Load Amperes:  <Insert value.>

2) Minimum Circuit Ampacity:  <Insert value.>

3) Maximum Overcurrent Protection:  <Insert value.>

4. Alternator Control Required:  [Yes] [No].

2.4 SUMP PUMP BASINS

Sump pump basins and covers in this Article are usually round with openings for simplex and multiplex pump installation.

A. Description:  Factory fabricated basin with sump, pipe connections, and separate cover.

B. Sump:  Fabricate watertight, with sidewall openings for pipe connections.

Use cast-iron, fiberglass, or other material sumps with cast-iron or steel covers for large installations.  Welded-steel basins are available but require special coatings and may require anode protection.

Retain one of three options in first subparagraph below or delete if in schedules.

1. Material:  [Cast iron] [Cast iron or fiberglass] [Fiberglass] <Insert other>.

2. Reinforcement:  Mounting plates for pumps, fittings, and accessories.

Retain subparagraph below if required to anchor basin to concrete slab in case of ground-water problems.

3. Anchor Flange:  Same material as or compatible with sump, cast in or attached to sump, in location and of size required to anchor basin in concrete slab.

C. Cover:  Fabricate with openings having gaskets, seals, and bushings, for access to pumps, pump shafts, control rods, discharge piping, vent connections, and power cables.

1. Material:  [Cast iron] [Cast iron or steel with bituminous coating] [Steel with bituminous coating].

2. Reinforcement:  Steel or cast iron, capable of supporting foot traffic for basins installed in foot-traffic areas.

If Project has more than one pump basin, delete paragraph and subparagraphs below and add basin characteristics to pump schedule on Drawings.

D. Capacity and Characteristics:

1. Material:  [Cast iron] [Fiberglass] <Insert other>.

2. Capacity:  <Insert gal (L).>

3. Diameter:  <Insert inches (mm).>

4. Depth:  <Insert inches (mm).>

5. Inlet No. 1:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Flanged] [Hubbed] [Threaded] outside.

6. Inlet No. 2:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Flange] [Hubbed] [Threaded] outside.

7. Inlet No. 3:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Flanged] [Hubbed] [Threaded] outside.

8. Sidewall Outlet:

a. Discharge Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Hubbed inside] [Hubbed outside] <Insert other>.

9. Cover:

a. Material:  [Cast iron] [Steel with bituminous coating].

b. Diameter:  <Insert inches (mm).>

c. Manhole Required:  [Yes] [No].

d. Vent Size:  <Insert NPS (DN).>

2.5 SUMP PUMP PITS

Sump pump pits and covers in this Article are usually square or rectangular with openings for simplex and multiplex pumps.

A. Description:  Concrete pit with sump, pipe connections, curb frame, and separate cover.

B. Sump:  Construct of watertight, cast-in-place, reinforced concrete with sidewall openings for pipe connections.  Cast-in-place concrete, formwork, and reinforcement are specified in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

1. Pipe Connections:  Sleeved openings large enough for mechanical sleeve seals for drainage piping.  Sleeves and mechanical sleeve seals are specified in Division 15 Section "Basic Mechanical Materials and Methods," and drainage piping is specified in Division 15 Section "Storm Drainage Piping."

C. Curb Frame and Cover:

1. Curb Frame Material:  Galvanized steel or steel with bituminous coating.

a. Pattern:  [Angle-cross-section shape with flat top surface] [Z-cross-section shape with raised outer rim of height matching cover, for recessed mounting having installed cover flush with top of floor slab].

2. Cover:  Fabricate with openings having gaskets, seals, and bushings, for access to pumps, pump shafts, control rods, discharge piping, vent connections, and power cables.

a. Material:  [Cast iron] [Cast iron or steel with bituminous coating] [Steel with bituminous coating].

b. Reinforcement:  Steel or cast iron, capable of supporting foot traffic for pits installed in foot-traffic areas.

If Project has more than one pump pit, delete paragraph and subparagraphs below and add pit characteristics to pump schedule on Drawings.

D. Capacity and Characteristics:

1. Capacity:  <Insert gal (L).>

2. Inside Dimensions:  <Insert inches (mm).>

3. Depth:  <Insert inches (mm).>

4. Inlet No. 1:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

5. Inlet No. 2:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

6. Inlet No. 3:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

7. Sidewall Outlet:

a. Discharge Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

8. Curb Frame:

a. Material:  [Galvanized] [Bituminous-coated] steel.

b. Pattern:  <Insert pattern.>

9. Cover:

a. Material:  [Cast iron] [Steel with bituminous coating].

b. Dimensions:  <Insert inches (mm).>

c. Manhole Required:  [Yes] [No].

d. Vent Size:  <Insert NPS (DN).>

2.6 PACKAGED DRAINAGE PUMP UNITS

A. Pedestal Units:  Factory-assembled and -tested, single-stage, centrifugal, end-suction, automatic-operation, freestanding drainage pump unit.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Aermotor Pumps, Inc.

b. American Machine & Tool Co.

c. Goulds Pumps; ITT Industries.

d. Liberty Pumps.

e. Little Giant Pump Co.

f. Myers, F. E.; Pentair Pump Group (The).

g. Sta-Rite Industries, Inc.

h. Zoeller Company.

i. <Insert manufacturer's name.>

2. Pump Body:  Corrosion-resistant material.

3. Impeller:  [Aluminum or brass] [Aluminum, brass, or plastic].

4. Motor:  With built-in overload protection and mounted vertically on sump pump column.  Comply with requirements in Division 15 Section "Motors."

5. Power Cord:  Three-conductor, waterproof cable of length required but not less than 72 inches (1830 mm), with grounding plug and cable-sealing assembly for connection at pump.

6. Control:  Float switch.

B. Submersible Units:  Factory-assembled and -tested, single-stage, centrifugal, end-suction, automatic-operation, submersible, drainage pump unit.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ABS Pumps, Inc.

b. Bell & Gossett Domestic Pump; ITT Industries.

c. Goulds Pumps; ITT Industries.

d. Grundfos Pumps Corp.

e. Liberty Pumps.

f. Little Giant Pump Co.

g. McDonald, A. Y. Mfg. Co.

h. Myers, F. E.; Pentair Pump Group (The).

i. Sta-Rite Industries, Inc.

j. Zoeller Company.

k. <Insert manufacturer's name.>

2. Pump Body:  Metal.

3. Impeller:  Brass.

Retain two subparagraphs above or first two subparagraphs below.

4. Pump Body:  Plastic.

5. Impeller:  Plastic.

6. Pump Seals:  Mechanical type.

7. Motor:  Hermetically sealed, capacitor-start type, with built-in overload protection.  Comply with requirements in Division 15 Section "Motors."

8. Power Cord:  Three-conductor, waterproof cable of length required but not less than 72 inches (1830 mm), with grounding plug and cable-sealing assembly for connection at pump.

9. Control:  Motor-mounted float switch.

10. Basin:  Plastic.

a. Capacity:  [2 gal (7.6 L)] [5 gal (18.9 L)] <Insert other> minimum.

b. Inlet Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacity and Characteristics:

1. Capacity:  <Insert gpm (L/minute).>

2. Total Dynamic Head:  <Insert feet (kPa).>

3. Speed:  <Insert rpm.>

4. Discharge Pipe Size:  <Insert NPS (DN).>

5. Motor Horsepower:  <Insert value.>

6. Electrical Characteristics:

a. Volts:  [120] [240] [277] [480] <Insert value.>

b. Phases:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

Retain subparagraph and associated subparagraphs below for submersible units; delete for pedestal units.

7. Basin:

a. Material:  Plastic.

b. Capacity:  [2 gal (7.6 L)] [5 gal (18.9 L)] <Insert other> minimum.

c. Inlet Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

2.7 FLEXIBLE CONNECTORS

Delete this Article if flexible connectors are specified in Division 15 Section "Storm Drainage Piping" or if not required.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Anamet, Inc.

2. Flex-Hose Co., Inc.

3. Flexicraft Industries.

4. Flex-Pression, Ltd.

5. Flex-Weld, Inc.

6. Hyspan Precision Products, Inc.

7. Mercer Rubber.

8. Metraflex, Inc.

9. Proco Products, Inc.

10. Tozen America Corporation.

11. Unaflex Inc.

12. <Insert manufacturer's name.>

B. Description:  [125-psig (860-kPa)] <Insert other> minimum working-pressure rating and ends matching pump connection:

1. Bronze Flexible Connectors:  Corrugated, bronze inner tubing covered with bronze wire braid.  Include copper-tube ends or bronze flanged ends, braze welded to tubing.

2. Stainless-Steel Flexible Connectors:  Corrugated, stainless-steel inner tubing covered with stainless-steel wire braid.  Include stainless-steel nipples or flanges, welded to tubing.

2.8 BUILDING AUTOMATION SYSTEM INTERFACE

A. Provide auxiliary contacts in pump controllers for interface to building automation system.  Include the following:

1. On-off status of each pump.

2. Alarm status.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in of plumbing piping to verify actual locations of storm drainage piping connections before sump pump installation.

3.2 CONCRETE

Retain this Article if Part 2 "Sump Pump Pits" or "Packaged Drainage Pump Units" Article is retained.  Coordinate sizes and locations of concrete bases and pits and verify requirements with structural engineer.

A. Install concrete bases of dimensions indicated for pumps and controllers.  Refer to Division 15 Section "Basic Mechanical Materials and Methods."

Revise four subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

B. Cast-in-place concrete materials and placement requirements are specified in Division 3.

3.3 SUMP PUMP INSTALLATION

A. Excavating, trenching, and backfilling are specified in Division 2 Section "Earthwork."

B. Install sump pumps according to applicable requirements in HI 1.4.

C. Install pumps and arrange to provide access for maintenance including removal of motors, impellers, couplings, and accessories.

Retain first paragraph below for wet-pit-mounted, vertical sump pumps.

D. Suspend wet-pit-mounted, vertical sump pumps from [basin] [basin and pit] [pit] covers.  Make direct connections to storm drainage piping.

E. Set submersible sump pumps on [basin] [basin or pit] [pit] floor.  Make direct connections to storm drainage piping.

F. Install sump pump basins and connect to drainage piping.  Brace interior of basins according to manufacturer's written instructions to prevent distortion or collapse during concrete placement.  Set basin cover and fasten to basin top flange.  Install cover so top surface is flush with finished floor.

G. Construct sump pump pits and connect to drainage piping.  Set pit curb frame recessed in and anchored to concrete.  Fasten pit cover to pit curb flange.  Install cover so top surface is flush with finished floor.

Retain first paragraph below for packaged, pedestal, drainage pump units.

H. Install packaged, pedestal, drainage pump units and make direct connection to storm drainage piping.

I. Install packaged, submersible, drainage pump unit basins on floor or concrete base unless recessed installation is indicated.  Make direct connections to storm drainage piping.

J. Support piping so weight of piping is not supported by pumps.

3.4 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in Division 15 Section "Storm Drainage Piping."  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to sump pumps to allow service and maintenance.

C. Connect storm drainage piping to pumps.  Install discharge piping equal to or greater than size of pump discharge piping.  Refer to Division 15 Section "Storm Drainage Piping."

Retain two subparagraphs below only if Part 2 "Wet-Pit-Mounted, Vertical Sump Pumps," "Submersible Sump Pumps," or "Packaged Drainage Pump Units" Article is retained.

1. Install flexible connectors adjacent to pumps in discharge piping.

2. Install check and shutoff valves on discharge piping from each pump.  Install unions on pumps having threaded pipe connections.  Install valves same size as connected piping.  Refer to Division 15 Section "Valves" for general-duty valves for drainage piping.

D. Ground equipment according to Division 16 Section "Grounding and Bonding."

E. Connect wiring according to Division 16 Section "Conductors and Cables."

3.5 STARTUP SERVICE

Delete first paragraph and subparagraphs below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Verify bearing lubrication.

3. Disconnect couplings and check motors for proper direction of rotation.

4. Verify that each pump is free to rotate by hand.  If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

5. Verify that pump controls are correct for required application.

6. <Insert additional startup steps if any.>

B. Start pumps without exceeding safe motor power:

1. Start motors.

2. Open discharge valves slowly.

3. Check general mechanical operation of pumps and motors.

C. Test and adjust controls and safeties.

D. Remove and replace damaged and malfunctioning components.

Insert specific liquid levels to start and stop pumps and energize alarms to suit design requirements.

1. Pump Controls:  Set pump controls for automatic start, stop, and alarm operation as required for system application.

2. Set field-adjustable switches and circuit-breaker trip ranges as indicated, or if not indicated, for normal operation.

E. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to two visits to Project outside normal occupancy hours for this purpose.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain[ controls and] pumps.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15446

SUMP PUMPS
15446 - 15

