Copyright 2002 AIA
MASTERSPEC
06/02

Copyright 2002, The American Institute of Architects (AIA)

SECTION 15450 - POTABLE-WATER STORAGE TANKS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes potable-water storage tanks and related accessories for indoor installation.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. FRP:  Fiberglass-reinforced plastic.

B. HDPE:  High-density polyethylene plastic.

C. LDPE:  Low-density polyethylene plastic.

D. PE:  Polyethylene plastic.

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories.  Indicate dimensions, wall thickness, insulation, finishes and coatings, required clearances, methods of assembly of components, and piping connections.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."  Coordinate with steel, potable-water storage tank articles for seismic requirements.

B. Manufacturer Seismic Qualification Certification:  Submit certification that indicated steel, potable-water storage tanks, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls."

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

C. Manufacturer Certificates:  Signed by manufacturers certifying that potable-water storage tanks comply with requirements.

D. Source quality-control test reports.

E. Purging and disinfecting reports.

1.5 QUALITY ASSURANCE

Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of potable-water storage tanks and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

Retain one or both paragraphs below only if ASME-code tanks are specified.

B. ASME Compliance for Steel Tanks:  Fabricate and label steel, potable-water storage tanks to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, where indicated.

C. ASME Compliance for FRP Tanks:  Fabricate and label FRP, potable-water storage tanks to comply with ASME Boiler and Pressure Vessel Code:  Section X, where indicated.

Retain first paragraph below if any plastic tanks are specified.

D. Comply with NSF 14, "Plastics Piping Components and Related Materials," for plastic potable-water storage tanks and components.  Include appropriate NSF marking.

E. Comply with NSF 61, "Drinking Water System Components--Health Effects, Sections 1 to 9," for potable-water storage tanks.  Include appropriate NSF marking.

1.6 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 STEEL, PRESSURE, POTABLE-WATER STORAGE TANKS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Adamson Global Technology Corporation.

2. Aldrich Co.

3. Armstrong Pumps, Inc.

4. Cemline Corporation.

5. GSW Water Heating Company.

6. HESco Industries, Inc.

7. Lochinvar Corp.

8. Precision Parts Corp.

9. PVI Industries, LLC.

10. Raypak, Inc.

11. RBI Water Heaters; A Mestek, Inc. Company.

12. RECO USA.

13. Smith, A. O. Water Products Co.

14. State Industries, Inc.

15. Weben Jarco.

16. Wessels Co.

17. Wood, John Co.

18. <Insert manufacturer's name.>

B. Description:  Steel, [horizontal] [vertical] pressure-rated tank with cylindrical sidewalls.

Retain first paragraph below for projects in seismic areas.

C. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

D. Construction:  [ASME code, steel] [Steel], constructed with nontoxic welded joints, for [125-psig (860-kPa)] [150-psig (1035-kPa)] <Insert other> working pressure.

Indicate manhole location on Drawings.

E. Manhole:  Watertight, for tank more than [36 inches (915 mm)] <Insert dimension> in diameter; same pressure rating as tank.

Retain second option in first paragraph below if ASME label is required.

F. Tappings:  Factory-fabricated[ stainless] steel, welded to tank[ before testing and labeling].

1. NPS 2 (DN 50) and Smaller:  ASME B1.20.1, with female thread.

2. NPS 2-1/2 (DN 65) and Larger:  ASME B16.5, flanged.

G. Specialties and Accessories:  Include tappings in tank and the following:

Retain specialties in subparagraphs below to suit Project.

1. Pressure relief valve.

2. Pressure gage.

3. Thermometer.

4. Air-charging connection.

5. Gage glass, brass fittings, compression stops, and gage-glass guard.

Retain paragraph below or specify cast-in-place concrete saddles and detail on Drawings.  Retain option if ASME label is required.

H. Horizontal Tank Supports:  Factory-fabricated steel saddles, welded to tank[ before testing and labeling].

Retain option in first paragraph below if ASME label is required.

I. Vertical Tank Supports:  Factory-fabricated steel legs or steel skirt, welded to tank[ before testing and labeling].

J. Tank Interior Finish:  Materials and thicknesses complying with NSF 61 barrier materials for potable-water tank linings.  Extend finish into and through tank fittings and outlets.

Retain one of two subparagraphs below.

1. Lining Material:  [Cement] [Copper] <Insert material>.

2. Coating:  [Epoxy resin] [Galvanized] [Glass] [Nickel] <Insert coating>.

Retain paragraph below to require tanks to have exterior coating.

K. Exterior Coating:  [Galvanized] [Manufacturer's standard enamel paint] [Primer paint] <Insert coating>.

2.3 STEEL, NONPRESSURE, POTABLE-WATER STORAGE TANKS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Adamson Global Technology Corporation.

2. Highland Tank & Mfg. Co.

3. Peabody TecTank, Inc.

4. RECO USA.

5. Steel Tank and Fabricating Co., Inc.

6. Wood, John Co.

7. <Insert manufacturer's name.>

B. Description:  Steel, [horizontal] [vertical] nonpressure-rated tank with cylindrical sidewalls.

Retain first paragraph below for projects in seismic areas.

C. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

D. Construction:  Steel, constructed with nontoxic welded joints.

Indicate manhole location on Drawings.

E. Manhole:  Watertight, for tank more than [36 inches (915 mm)] <Insert dimension> in diameter.

F. Cover for Open Tank:  [Plastic] [Steel, with lining same as or similar to tank lining and] with shape that encloses top of tank.

G. Tappings:  Factory-fabricated[ stainless] steel, welded to tank.

1. NPS 2 (DN 50) and Smaller:  ASME B1.20.1, with female thread.

2. NPS 2-1/2 (DN 65) and Larger:  ASME B16.5, flanged.

H. Specialties and Accessories:  Include tappings in the tank and the following:

Retain specialties in subparagraphs below to suit Project.

1. Vacuum relief valve.

2. Free air vent with insect screen.

3. Thermometer.

4. Gage glass, brass fittings, compression stops, and gage-glass guard.

Retain paragraph below or specify cast-in-place concrete saddles and detail on Drawings.  Retain option if ASME label is required.

I. Horizontal Tank Supports:  Factory-fabricated steel saddles, welded to tank[ before testing and labeling].

Retain option in first paragraph below if ASME label is required.

J. Vertical Tank Supports:  Factory-fabricated steel legs or steel skirt, welded to tank[ before testing and labeling].

K. Tank Interior Finish:  Materials and thicknesses complying with NSF 61 barrier materials for potable-water tank linings.  Extend finish into and through tank fittings and outlets.

Retain one of two subparagraphs below.

1. Lining Material:  [Cement] [Copper] <Insert material>.

2. Coating:  [Epoxy resin] [Galvanized] [Glass] [Nickel] <Insert coating>.

Retain paragraph below to require tanks to have exterior coating.

L. Exterior Coating:  [Galvanized] [Manufacturer's standard enamel paint] [Primer paint] <Insert coating>.

2.4 STEEL, FLOATING-WAFER, PRESSURE, POTABLE-WATER STORAGE TANKS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Cemline Corporation.

2. State Industries, Inc.

3. Wood, John Co.

4. <Insert manufacturer's name.>

B. Description:  Steel, vertical, pressure-rated tank with cylindrical sidewalls and with floating-wafer separator.

Retain first paragraph below for projects in seismic areas.

C. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

D. Construction:  [ASME code, steel] [Steel], constructed with nontoxic welded joints, for [125-psig (860-kPa)] [150-psig (1035-kPa)] <Insert other> working pressure.

Indicate manhole location on Drawings.

E. Manhole:  Watertight, for tank more than [36 inches (915 mm)] <Insert dimension> in diameter; same pressure rating as tank.

F. Floating Wafer:  Nontoxic plastic, of diameter to match tank.

Retain second option in first paragraph below if ASME label is required.

G. Tappings:  Factory-fabricated[ stainless] steel, welded to tank[ before testing and labeling].

1. NPS 2 (DN 50) and Smaller:  ASME B1.20.1, with female thread.

2. NPS 2-1/2 (DN 65) and Larger:  ASME B16.5, flanged.

H. Specialties and Accessories:  Include tappings in tank and the following:

Retain specialties in subparagraphs below to suit Project.

1. Pressure relief valve.

2. Pressure gage.

3. Thermometer.

4. Air-charging connection.

5. Gage glass, brass fittings, compression stops, and gage-glass guard.

Retain option in first paragraph below if ASME label is required.

I. Vertical Tank Supports:  Factory-fabricated steel legs or steel skirt, welded to tank[ before testing and labeling].

J. Tank Interior Finish:  Materials and thicknesses complying with NSF 61 barrier materials for potable-water tank linings.  Extend finish into and through tank fittings and outlets.

Retain one of two subparagraphs below.

1. Lining Material:  [Cement] [Copper] <Insert material>.

2. Coating:  [Epoxy resin] [Galvanized] [Glass] [Nickel] <Insert coating>.

Retain paragraph below to require tanks to have exterior coating.

K. Exterior Coating:  [Galvanized] [Manufacturer's standard enamel paint] [Primer paint] <Insert coating>.

2.5 STEEL, PRECHARGED, PRESSURE, POTABLE-WATER STORAGE TANKS

A. Steel, Precharged, Diaphragm, Water Storage Tanks:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. AMTROL, Inc.

b. Armstrong Pumps, Inc.

c. Flexcon Industries; Plumbing & Heating Division.

d. Myers, F. E..

e. Smith, A. O.; Aqua-Air Div.

f. State Industries, Inc.

g. Taco, Inc.

h. Wessels Co.

i. <Insert manufacturer's name.>

2. Description:  Steel, vertical, pressured-rated tank with cylindrical sidewalls and with air-charging valve and air precharge.

Retain first subparagraph below for projects in seismic areas.

3. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

4. Operation:  Factory-installed, butyl-rubber diaphragm.

Retain paragraph and subparagraphs above or below.

B. Steel, Precharged, Bladder, Water Storage Tanks:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Armstrong Pumps, Inc.

b. Taco, Inc.

c. Wessels Co.

d. Wood, John Co.

e. <Insert manufacturer's name.>

2. Description:  Steel, vertical, pressured-rated tank with cylindrical sidewalls and with air-charging valve and air precharge.

Retain first subparagraph below for projects in seismic areas.

3. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

4. Operation:  Factory-installed, butyl-rubber bladder.

Retain remaining paragraphs and subparagraphs with either tank type selected above.

C. Construction:  [ASME code, steel] [Steel], constructed with nontoxic welded joints, for [125-psig (860-kPa)] [150-psig (1035-kPa)] <Insert other> working pressure.

Retain second option in first paragraph below if ASME label is required.

D. Tappings:  Factory-fabricated[ stainless] steel, welded to tank[ before testing and labeling].

1. NPS 2 (DN 50) and Smaller:  ASME B1.20.1, with female thread.

2. NPS 2-1/2 (DN 65) and Larger:  ASME B16.5, flanged.

E. Specialties and Accessories:  Include tappings in tank and the following:

Verify availability of required options.

1. Pressure gage.

2. <Insert required options.>

Retain option in first paragraph below if ASME label is required.

F. Vertical Tank Supports:  Factory-fabricated steel legs or steel skirt, welded to tank[ before testing and labeling].

G. Tank Interior Finish:  Materials and thicknesses complying with NSF 61 barrier materials for potable-water tank linings.  Extend finish into and through tank fittings and outlets.

Retain one of two subparagraphs below.

1. Lining Material:  [Cement] [Copper] <Insert material>.

2. Coating:  [Epoxy resin] [Galvanized] [Glass] [Nickel] <Insert coating>.

Retain paragraph below to require tanks to have exterior coating.

H. Exterior Coating:  [Galvanized] [Manufacturer's standard enamel paint] [Primer paint] <Insert coating>.

2.6 INSULATED, STEEL, PRESSURE, POTABLE-WATER STORAGE TANKS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. American Water Heater Company.

2. GSW Water Heating Company.

3. HESco Industries, Inc.

4. K-TAM Manufacturing, Inc.

5. Lochinvar Corp.

6. Precision Parts Corp.

7. PVI Industries, LLC.

8. RBI Water Heaters: A Mestek, Inc. Company.

9. Rheem Manufacturing Co.; Rheem Water Heater Div.

10. Smith, A. O. Water Products Co.

11. State Industries, Inc.

12. Teledyne Laars.

13. Wessels Co.

14. <Insert manufacturer's name.>

B. Description:  Steel, vertical, pressure-rated tank with cylindrical sidewalls.

Retain first paragraph below for projects in seismic areas.

C. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

D. Construction:  [ASME code, steel] [Steel], constructed with nontoxic welded joints, for [125-psig (860-kPa)] [150-psig (1035-kPa)] <Insert other> working pressure.

Indicate manhole location on Drawings.

E. Manhole:  Watertight, for tank more than [36 inches (915 mm)] <Insert dimension> in diameter; same pressure rating as tank.

Retain second option in first paragraph below if ASME label is required.

F. Tappings:  Factory-fabricated[ stainless] steel, welded to tank[ before testing and labeling].

1. NPS 2 (DN 50) and Smaller:  ASME B1.20.1, with female thread.

2. NPS 2-1/2 (DN 65) and Larger:  ASME B16.5, flanged.

G. Specialties and Accessories:  Include tappings in tank and the following:

Retain specialties in subparagraphs below to suit Project.

1. Pressure relief valve.

2. Pressure gage.

3. Thermometer.

4. Air-charging connection.

5. Gage glass, brass fittings, compression stops, and gage-glass guard.

Retain option in first paragraph below if ASME label is required.

H. Vertical Tank Supports:  Factory-fabricated steel legs or steel skirt, welded to tank[ before testing and labeling].

I. Tank Interior Finish:  Materials and thicknesses complying with NSF 61 barrier materials for potable-water tank linings.  Extend finish into and through tank fittings and outlets.

Retain one of two subparagraphs below.

1. Lining Material:  [Cement] [Copper] <Insert material>.

2. Coating:  [Epoxy resin] [Galvanized] [Glass] [Nickel] <Insert coating>.

J. Insulation:  Factory-installed, fiberglass or polyurethane foam; surrounding entire tank except connections and other openings; suitable for tank operating temperature; and complying with ASHRAE/IESNA 90.1.

K. Jacket:  Steel, with manufacturer's standard finish, unless otherwise indicated.

2.7 STEEL, GRAVITY, NONPRESSURE, POTABLE-WATER STORAGE TANKS

A. Description:  Steel, [horizontal] [vertical] nonpressure-rated tank with [cylindrical] [rectangular] sidewalls.

Retain first paragraph below for projects in seismic areas.

B. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

C. Construction:  Nonpressure rated, [factory] [factory or field] [field] fabricated from ASTM A 794 steel sheets, with nontoxic welded joints.

D. Reinforcement:  ASTM A 36/A 36M, structural-steel shapes, welded to tank as required to maintain tank shape.

Indicate manhole location on Drawings.

E. Manhole:  Watertight, for tank more than [36 inches (915 mm)] <Insert dimension> [in diameter] [wide].

F. Tappings:  Factory-fabricated[ stainless] steel, welded to tank.

1. NPS 2 (DN 50) and Smaller:  ASME B1.20.1, with female thread.

2. NPS 2-1/2 (DN 65) and Larger:  ASME B16.5, flanged.

G. Specialties and Accessories:  Include tappings in tank and the following:

Retain specialties in subparagraphs below to suit Project.

1. Vacuum relief valve.

2. Free air vent with insect screen.

3. Thermometer.

4. Gage glass, brass fittings, compression stops, and gage-glass guard.

Retain first paragraph below or specify cast-in-place concrete saddles and detail on Drawings.

H. Horizontal Tank Supports:  Factory-fabricated steel saddles or legs, welded to tank.

I. Vertical Tank Supports:  Factory-fabricated steel legs or steel skirt, welded to tank.

J. Tank Interior Finish:  Materials and thicknesses complying with NSF 61 barrier materials for potable-water tank linings.  Extend finish into and through tank fittings and outlets.

Retain one of two subparagraphs below.

1. Lining Material:  [Cement] [Copper] <Insert material>.

2. Coating:  [Epoxy resin] [Galvanized] [Glass] [Nickel] <Insert coating>.

Retain paragraph below to require tanks to have exterior coating.

K. Exterior Coating:  [Galvanized] [Manufacturer's standard enamel paint] [Primer paint] <Insert coating>.

2.8 PLASTIC, PRESSURE, POTABLE-WATER STORAGE TANKS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Park International Corp.

2. Structural North America.

3. Tankinetics, Inc.

4. <Insert manufacturer's name.>

B. Description:  FRP, vertical, pressure-rated tank with cylindrical sidewalls.

C. Construction:  [ASME code, composite FRP] [Composite FRP], [contact-molded] [contact-molded or filament-wound] [filament-wound], thermosetting-resin tank for [100-psig (690-kPa)] [125-psig (860-kPa)] [150-psig (1035-kPa)] <Insert other> working pressure.

1. Tank Lining Material:  Nontoxic [HDPE] [LDPE] <Insert material> complying with NSF 61 barrier materials for potable-water tanks.

Indicate manhole location on Drawings.

D. Manhole:  Watertight, for tank more than [36 inches (915 mm)] <Insert dimension> in diameter; same pressure rating as tank.

E. Tappings:  Factory-fabricated, reinforced FRP flanged-end nozzle.

1. NPS 2 (DN 50) and Smaller:  Include plastic-to-steel transition fitting from tank nozzle flange to ASME B1.20.1, female thread.

2. NPS 2-1/2 (DN 65) and Larger:  ASME B16.5, flanged.

F. Specialties and Accessories:  Include tappings in tank and the following:

Retain specialties in subparagraphs below to suit Project.

1. Pressure relief valve.

2. Pressure gage.

3. Thermometer.

G. Vertical Tank Supports:  Factory-fabricated steel legs or reinforced FRP skirt attached by FRP brackets to tank sidewall.

H. Tank Interior Finish:  Materials and thicknesses complying with NSF 61 barrier materials for potable-water tank linings.  Extend finish into and through tank fittings and outlets.

2.9 PLASTIC, NONPRESSURE, POTABLE-WATER STORAGE TANKS

A. FRP, Potable-Water Storage Tanks:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Associated Fiberglass Enterprises.

b. Belding Tank Technologies, Inc.

c. L. F. Manufacturing, Inc.

d. Palmer Manufacturing & Tank, Inc.

e. Raven Industries Inc.; Plastics Div.

f. Viatec Inc.

g. <Insert manufacturer's name.>

2. Description:  FRP, vertical, nonpressure-rated water tank; complying with NSF 61 barrier materials for potable-water tanks.

3. Construction:  [ASTM D 3299, filament-wound] [ASTM D 3299, filament-wound or ASTM D 4097, contact-molded] [ASTM D 4097, contact-molded] FRP.

4. Tappings:  Factory-fabricated, FRP flanged-end nozzle.

a. NPS 2 (DN 50) and Smaller:  Include plastic-to-steel transition fitting from tank nozzle flange to ASME B1.20.1, female thread.

1) [Exception:  Tappings may be threaded FRP coupling integral with nozzle for connections for plastic piping.]

b. NPS 2-1/2 (DN 65) and Larger:  Flanged.

Retain subparagraph below only if a stand is required.

5. Vertical Tank Support:  Separate factory-fabricated steel stand, capable of supporting tank.

Retain paragraph and subparagraphs above or below.

B. PE, Potable-Water Storage Tanks:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Assmann Corporation of America.

b. Chem-Tainer Industries.

c. Nalge Nunc International.

d. Poly Processing Company.

e. Premier Plastics Ltd.

f. Raven Industries Inc.; Plastics Div.

g. Steel Tank and Fabricating Co., Inc.

h. TolPlast Co., Inc.

i. <Insert manufacturer's name.>

2. Description:  PE, vertical, flat-bottom, nonpressure-rated water tank; complying with NSF 61 barrier materials for potable-water tanks.

3. Construction:  ASTM D 1998, molded PE.

4. Tappings:  Factory-fabricated bulkhead fittings, attached to tank.

a. NPS 2 (DN 50) and Smaller:  With female thread.

b. NPS 2-1/2 (DN 65) and Larger:  Flanged.

Retain subparagraph below only if a stand is required.  Tanks are specified as flat-bottom shape and may be installed directly on a base.

5. Vertical Tank Support:  Separate factory-fabricated steel stand, capable of supporting entire bottom of tank.

Retain remaining paragraphs and subparagraphs with either tank material selected above.

Indicate manhole location on Drawings.

C. Manhole:  Watertight, for tank more than [36 inches (915 mm)] <Insert dimension> in diameter.

D. Cover for Open Tank:  Plastic, same as or similar to tank material and with shape that encloses top of tank.

E. Specialties and Accessories:  Include tappings in the tank and the following:

Retain specialties in subparagraphs below to suit Project.

1. Vacuum relief valve.

2. Free air vent with insect screen.

3. Thermometer.

4. Gage glass, brass fittings, compression stops, and gage-glass guard.

2.10 SOURCE QUALITY CONTROL

A. Test and inspect potable-water storage tanks according to the following tests and inspections and prepare test reports:

1. Pressure Testing for ASME-Code, Potable-Water Storage Tanks:  Hydrostatically test to ensure structural integrity and freedom from leaks.  Fill tanks with water, vent air, pressurize to 1-1/2 times tank pressure rating, disconnect test equipment, hold pressure for 30 minutes with no drop in pressure, and check for leaks.  Replace tanks that fail test with new tanks, and repeat until test is satisfactory.

2. Pressure Testing for Non-ASME-Code, Pressure, Potable-Water Storage Tanks:  Hydrostatically test to ensure structural integrity and freedom from leaks at pressure of [50 psig (345 kPa)] <Insert measurement> above system operating pressure, but not less than [150 psig (1035 kPa)] <Insert measurement>.  Fill tanks with water, vent air, pressurize tanks, disconnect test equipment, hold pressure for two hours with no drop in pressure, and check for leaks.  Repair or replace tanks that fail test with new tanks and repeat until test is satisfactory.

3. Nonpressure Testing for Potable-Water Storage Tanks:  Fill tanks to water operating level to ensure structural integrity and freedom from leaks.  Hold water level for two hours with no drop in water level.  Repair or replace tanks that fail test with new tanks, and repeat until test is satisfactory.

PART 3 -  EXECUTION

3.1 CONCRETE BASES

Coordinate sizes and locations of concrete bases with tanks selected.  Verify structural requirements with structural engineer.

A. Install concrete bases of dimensions indicated for tanks.  Refer to Division 15 Section "Basic Mechanical Materials and Methods."

Revise subparagraphs below based on installed tanks.  Indicate dowel-rod quantity, size, and spacing on Drawings.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For supported tanks, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported tanks.

B. Cast-in-place concrete materials and placement requirements are specified in Division 3.

3.2 INSTALLATION

A. Install water storage tanks on concrete bases, level and plumb, firmly anchored.  Arrange so devices needing servicing are accessible.

1. Install horizontal tanks on [concrete piers and factory-fabricated] [fabricated steel supports and] saddles.

B. Anchor tank supports and tanks to substrate.

1. Use steel or FRP straps over or around plastic tanks.

Retain first paragraph below if required.  Add special requirements or detail on Drawings.

C. Install tank seismic restraints.

D. Install thermometers and pressure gages on water storage tanks and piping, if indicated.  Thermometers and pressure gages are specified in Division 15 Section "Meters and Gages."

Revise first paragraph and subparagraphs below to suit Project; coordinate with Drawings.

E. Install the following devices on tanks where indicated:

1. Pressure relief valves.

2. Temperature and pressure relief valves.

3. Vacuum relief valves.

4. Tank vents on nonpressure tanks.

5. Connections to accessories.

F. After installing tanks with factory finish, inspect finishes and repair damages to finishes.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to potable-water storage tanks to allow service and maintenance.

C. Connect water piping to water storage tanks with unions or flanges and with shutoff valves.  Connect tank drains with shutoff valves and discharge over closest floor drains.

1. General-duty valves are specified in Division 15 Section "Valves."

a. Valves NPS 2 (DN 50) and Smaller:  Gate or ball.

b. Valves NPS 2-1/2 (DN 65) and Larger:  Gate or butterfly.

c. Drain Valves:  NPS 3/4 (DN 20) gate or ball valve.  Include outlet with, or nipple in outlet with, ASME B1.20.7, 3/4-11.5NH thread for garden-hose service, threaded cap, and chain.

2. Water Piping Connections:  Make connections to dissimilar metals with dielectric fittings.  Dielectric fittings are specified in Division 15 Section "Basic Mechanical Materials and Methods."

Retain subparagraph below for hydropneumatic booster systems with air supply.

3. Connect air piping to hydropneumatic tanks with unions or flanges and gate or ball valves.  Make connections to dissimilar metals with dielectric fittings, which are specified in Division 15 Section "Basic Mechanical Materials and Methods."

3.4 FIELD QUALITY CONTROL

A. Perform the following final checks before filling:

1. Verify that air precharge in precharged tanks is correct.

2. Test operation of tank accessories and devices.

3. Verify that pressure relief valves have correct setting.

a. Manually operate pressure relief valves.

b. Adjust pressure settings.

4. Verify that vacuum relief valves are correct size.

a. Manually operate vacuum relief valves.

b. Adjust vacuum settings.

B. Filling Procedures:  Follow manufacturer's written procedures.  Fill tanks with water to operating level.

3.5 CLEANING

Retain this Article if disinfecting tanks is required.  Requirements below were taken from plumbing codes.  Revise to suit Project.

A. Clean and disinfect potable-water storage tanks.

B. Use purging and disinfecting procedure prescribed by authorities having jurisdiction or, if method is not prescribed, use procedure described in AWWA C652 or as described below:

1. Purge water storage tanks with potable water.

2. Disinfect tanks by one of the following methods:

a. Fill tanks with water-chlorine solution containing at least 50 ppm (50 mg/L) of chlorine.  Isolate tanks and allow to stand for 24 hours.

b. Fill tanks with water-chlorine solution containing at least 200 ppm (200 mg/L) of chlorine.  Isolate tanks and allow to stand for three hours.

3. Flush tanks, after required standing time, with clean, potable water until chlorine is not present in water coming from tank.

4. Submit water samples in sterile bottles to authorities having jurisdiction.  Repeat procedure if biological examination made by authorities having jurisdiction shows evidence of contamination.

C. Prepare written reports for purging and disinfecting activities.

END OF SECTION 15450

POTABLE-WATER STORAGE TANKS
15450 - 17

