Copyright 2002 AIA
MASTERSPEC
06/02

Copyright 2002, The American Institute of Architects (AIA)

SECTION 15469 - WATER SOFTENERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes [household] [commercial] water softeners.

Adjust list below to suit Project.

1. Chemicals.

2. Water testing kits.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. FRP:  Fiberglass-reinforced plastic.

C. PE:  Polyethylene plastic.

D. PVC:  Polyvinyl chloride plastic.

1.4 SUBMITTALS

A. Product Data:  For the following:

1. Water Softeners.  Include rated capacities, operating characteristics, furnished specialties, and accessories.

2. Water testing kits.

B. Shop Drawings:  For water softeners.  Include plans, elevations, sections, details, and connections to piping systems.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."  Coordinate with Part 2 "Commercial Water Softeners" Article and with steel mineral tanks for seismic requirements.

C. Manufacturer Seismic Qualification Certification:  Submit certification that indicated steel mineral tanks, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Manufacturer Certificates:  Signed by manufacturers certifying that water softeners comply with requirements.

E. Source quality-control test reports.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For water softeners to include in emergency, operation, and maintenance manuals.

H. Warranty:  Special warranty specified in this Section.

I. Maintenance service agreement.

1.5 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of water softeners and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain one or both paragraphs below only if ASME-code mineral tanks are specified.

C. ASME Compliance for Steel Tanks:  Fabricate and label mineral tanks to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, where indicated.

D. ASME Compliance for FRP Tanks:  Fabricate and label mineral tanks to comply with ASME Boiler and Pressure Vessel Code:  Section X, where indicated.

1.6 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of water softener that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Structural failures of mineral and brine tanks.

b. Faulty operation of controls.

c. Deterioration of metals, metal finishes, and other materials beyond normal use.

d. Attrition loss of resin exceeding 3 percent per year.

e. Mineral washed out of system during service run or backwashing period.

f. Effluent turbidity greater and color darker than incoming water.

g. Fouling of underdrain system, gravel, and resin, with turbidity or by dirt, rust, or scale from softener equipment or soft water, while operating according to manufacturer's written operating instructions.

Verify available warranties on water softeners and insert number in first subparagraph below.

2. Household Water Softener, Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

3. Commercial Water Softener, Warranty Period:  From date of Substantial Completion.

Verify available warranties on water softeners and insert number in subparagraphs below.

a. Mineral Tanks:  [Five] [10] <Insert number> years.

b. Brine Tanks:  [Three] [Five] <Insert number> years.

c. Controls:  [Five] [10] <Insert number> years.

d. Underdrain Systems:  [Three] [Five] <Insert number> years.

1.8 MAINTENANCE SERVICE

Delete this Article if Owner will maintain system or will contract separately for maintenance service.

A. Maintenance:  Submit [four] <Insert number> copies of manufacturer's "Agreement for Continued Service and Maintenance," before Substantial Completion, for Owner's acceptance.  Offer terms and conditions for furnishing chemicals and providing continued testing and servicing to include replacing materials and equipment.  Include one-year term of agreement with option for one-year renewal.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Salt for Brine Tanks:  Furnish same form as and at least [four] <Insert number> times original load, but not less than [200 lb (90.7 kg)] [1000 lb (453.6 kg)] <Insert weight>.  Deliver on pallets according to the following:

Retain one or more of first four subparagraphs below and edit package size as required.

a. Food-Grade Pellet Salt:  In [40- or 50-lb (18.1- or 22.7-kg)] [80-lb (36.3-kg)] <Insert weight> packages.

b. Plain Pellet Salt:  In [40- or 50-lb (18.1- or 22.7-kg)] [80-lb (36.3-kg)] <Insert weight> packages.

c. Crystallized Solar Salt:  In [40- or 50-lb (18.1- or 22.7-kg)] [80-lb (36.3-kg)] <Insert weight> packages.

d. Plain, Brine Block Salt:  In [50-lb (22.7-kg)] <Insert weight> blocks.

2. Store salt on raised platform where directed by Owner.  Do not store in contact with concrete floor.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 HOUSEHOLD WATER SOFTENERS

Refer to the Water Softener Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Alamo Water Refiners, Inc.

2. CSI Water Treatment Systems; a division of Chandler Systems, Inc.

3. Culligan International Company.

4. CUNO Incorporated.

5. Diamond Water Conditioning.

6. EcoWater Systems, Inc.

7. Flint & Walling, Inc.; a subsidiary of Zoeller Co.

8. Ion Exchange Products, Inc.

9. Kinetico Incorporated.

10. Marlo, Inc.

11. Plymouth Products, Inc.

12. Rainsoft Div.; Aquion Partners L.P.

13. Springsoft Intl., Inc.

14. Water Soft, Inc.

15. <Insert manufacturer's name.>

Copy and edit paragraph and subparagraphs below for each different type of household water softener.  Water softeners described in this Article are appropriate for service flow rate between 4 and 12 gpm (0.25 to 0.76 L/s).

B. Description:  Factory-assembled, fully-automatic, pressure-type water softener.

1. Configuration:  Unit with one mineral tank and one brine tank[ or cabinet-style, combination mineral and brine tank unit with equivalent characteristics].

2. Mineral Tank:  Steel or FRP, with coating or liner suitable for potable-water service and [125-psig (860-kPa)] <Insert pressure> minimum pressure rating.

3. Comply with NSF 61, "Drinking Water System Components--Health Effects."

4. Controls:  For fully automatic operation.

5. Brine Tank:  Combination measuring and wet-salt storing system.

a. Tank and Cover Material:  FRP or molded PE.

b. Brine Valve:  Float operated and plastic fitted for automatic control of brine withdrawn and freshwater refill.

c. Size:  Large enough for at least two regenerations at full salting.

6. Factory-Installed Accessories:

a. Piping, valves, tubing, and drains.

b. Sampling cock.

c. Main-operating-valve position indicator.

If more than one household water softener is on Project, delete paragraph and subparagraphs below and schedule household water softeners on Drawings.

C. Capacity and Characteristics:

1. Service:  Household.

2. Water Analysis:

a. Hardness:  <Insert grains/gal. or ppm (mg/L).>

b. Iron:  <Insert ppm (mg/L).>

c. Dissolved Solids:  <Insert ppm (mg/L).>

d. Concentration:  <Insert pH.>

e. Inlet Water Pressure:  <Insert psig (kPa).>

f. Water Temperature:  <Insert deg F (deg C).>

3. Continuous Service Flow Rate:  <Insert number> gpm at 15-psig (<Insert number> L/s at 104-kPa) pressure drop.

4. Peak Service Flow Rate:  <Insert number> gpm at 25-psig (<Insert number> L/s at 173-kPa) pressure drop.

5. Mineral Quantity:  <Insert cu. ft. (cu. m).>

6. Mineral Exchange Capacity:  <Insert grains/cu. ft. per lb (kg/cu. m per kg) of salt.>

7. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phases:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

8. Salt Capacity:  <Insert lb (kg).>

2.3 COMMERCIAL WATER SOFTENERS

Revise this Article to include features and accessories for water softeners.  If more than one type is required, identify specific features and accessories for each type in a schedule on Drawings using terms in this Article.  Water softeners described in this Article are appropriate for service flow rate of 8 gpm (0.5 L/s) and larger, for commercial or industrial applications.

A. Description:  Factory-assembled, pressure-type water softener.

Refer to the Water Softener Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alamo Water Treatment; Ecodyne Water Treatment.

b. Columbia Water Conditioning Systems, Inc.

c. CSI Water Treatment Systems; a division of Chandler Systems, Inc.

d. Culligan International Company.

e. CUNO Incorporated.

f. Diamond Water Conditioning.

g. Diamond Water Systems, Inc.

h. Environmental Dynamics Corporation.

i. Hungerford & Terry, Inc.

j. Ion Exchange Products, Inc.

k. Kinetico Incorporated.

l. Marlo, Inc.

m. Parker Boiler Co.

n. Plymouth Products, Inc.

o. Rainsoft Div.; Aquion Partners L.P.

p. Springsoft Intl., Inc.

q. Water & Power Technologies, Inc.

r. Water King, Inc.

s. Water Soft, Inc.

t. <Insert manufacturer's name.>

Retain first subparagraph below for potable water or delete if not required.

2. Comply with NSF 61, "Drinking Water System Components--Health Effects."

3. Configuration:  [Single unit with one mineral tank] [Twin unit with two mineral tanks] [Triple unit with three mineral tanks] <Insert configuration> and one brine tank[, factory mounted on skids].

Retain one of two "Mineral Tanks" subparagraphs and associated subparagraphs below.

4. Mineral Tanks:  FRP, pressure-vessel quality.

a. Construction:  [Non-ASME code.] [Fabricated and stamped to comply with ASME Boiler and Pressure Vessel Code:  Section X, "Fiber-Reinforced Plastic Pressure Vessels."]

First option in first subparagraph below is usual minimum pressure rating; use higher rating if required.

b. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] <Insert pressure> minimum.

c. Wetted Components:  Suitable for water temperatures from [40 to at least 100 deg F (5 to at least 38 deg C)] [40 to at least 120 deg F (5 to at least 49 deg C)] [40 to at least 150 deg F (5 to at least 66 deg C)] <Insert temperature>.

d. Freeboard:  50 percent minimum for backwash expansion above normal resin bed level.

e. Support Legs or Skirt:  Constructed of structural steel, welded to tank[ before testing and labeling].

f. Upper Distribution System:  Single, point type, fabricated from galvanized-steel pipe and fittings.

g. Lower Distribution System:  Hub and radial-arm or header-lateral type; fabricated from nonmetallic pipe and fittings with individual, fine-slotted, nonclogging plastic strainers; arranged for even flow distribution through resin bed.

Retain first subparagraph below for potable water.

h. Liner:  PE, ABS, or other material suitable for potable water.

5. Mineral Tanks:  [Steel] [Stainless steel], electric welded; pressure-vessel quality.

Retain first subparagraph below for projects in seismic areas.

a. Fabricate supports and attachments to tank with reinforcement strong enough to resist tank movement during seismic event when tank supports are anchored to building structure.

b. Construction:  [Non-ASME code.] [Fabricated and stamped to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, "Pressure Vessels."]

First option in first subparagraph below is usual minimum pressure rating; use higher rating if required.

c. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> minimum.

d. Wetted Components:  Suitable for water temperatures from [40 to at least 100 deg F (5 to at least 38 deg C)] [40 to at least 120 deg F (5 to at least 49 deg C)] [40 to at least 150 deg F (5 to at least 66 deg C)] <Insert temperature>.

e. Freeboard:  50 percent minimum for backwash expansion above normal resin bed level.

Revise tank size in first two subparagraphs below to suit Project.  Some manufacturers offer manholes in smaller-diameter tanks.

f. Handholes:  4 inches (102 mm) round or 4 by 6 inches (102 by 152 mm) elliptical, in top head and lower sidewall of tanks 30 inches (762 mm) and smaller in diameter.

g. Manhole:  11 by 15 inches (280 by 380 mm) in top head of tanks larger than 30 inches (762 mm) in diameter.

h. Support Legs or Skirt:  Constructed of structural steel, welded to tank[ before testing and labeling].

Retain one of first two subparagraphs below; delete both if tanks are stainless steel.

i. Finish:  Hot-dip galvanized on exterior and interior of tank after fabrication unless tank is stainless steel.

j. Finish:  Exterior of tank spray painted with rust-resistant prime coat, 2- to 3-mil (0.051- to 0.076-mm) dry film thickness.  Interior sandblasted and lined with epoxy-polyamide coating, 8- to 10-mil (0.203- to 0.254-mm) dry film thickness.

k. Upper Distribution System:  Single, point type, fabricated from galvanized-steel pipe and fittings.

l. Lower Distribution System:  Hub and radial-arm or header-lateral type; fabricated from PVC pipe and fittings with individual, fine-slotted, nonclogging PE strainers; arranged for even flow distribution through resin bed.

Retain subparagraph below for potable water; delete if tanks are stainless steel.

m. Liner:  PE, ABS, or other material suitable for potable water.

Retain one of first two subparagraphs and associated subparagraphs below.  Retain first subparagraph and associated subparagraphs for operation where regeneration must be started manually.  Operations subsequent to regeneration are performed automatically.

6. Controls:  Automatic; factory mounted on unit and factory wired.

a. Adjustable duration of various regeneration steps.

b. Push-button start and complete manual operation.

c. Electric time clock and switch for automatic operation, except for manual return to service.

d. Sequence of Operation:  Program multiport pilot-control valve to automatically pressure-actuate main operating valve through steps of regeneration.

e. Pointer on pilot-control valve shall indicate cycle of operation.

f. Means of manual operation of pilot-control valve if power fails.

Retain first subparagraph and associated subparagraphs below for operation where first regeneration must be started manually.  Operations subsequent to regeneration and return to service are performed automatically.  Regeneration operations subsequent to first regeneration are performed automatically.

7. Controls:  Fully automatic; factory mounted on unit and factory wired.

a. Adjustable duration of various regeneration steps.

b. Push-button start and complete manual operation.

c. Electric time clock and switch for fully automatic operation, adjustable to initiate regeneration at any hour of day and any day of week or at fixed intervals.

d. Sequence of Operation:  Program multiport pilot-control valve to automatically pressure-actuate main operating valve through steps of regeneration and return to service.

e. Pointer on pilot-control valve shall indicate cycle of operation.

f. Means of manual operation of pilot-control valve if power fails.

Retain subparagraphs and associated subparagraphs below with either "Controls" subparagraph above.

g. Main Operating Valves:  Industrial, automatic, multiport, diaphragm type with the following features:

1) Slow opening and closing, nonslam operation.

2) Diaphragm guiding on full perimeter from fully open to fully closed.

3) Isolated dissimilar metals within valve.

4) Self-adjusting, internal, automatic brine injector that draws brine and rinses at constant rate independent of pressure.

Retain first subparagraph below only for single mineral-tank units.

5) Valve for single mineral-tank unit with internal automatic bypass of raw water during regeneration.

6) Sampling cocks for soft water.

7) Special tools are not required for service.

h. Flow Control:  Automatic, to control backwash and flush rates over wide variations in operating pressures, and that does not require field adjustments.

Retain one of first six subparagraphs below.

1) Meter Control:  Equip each mineral tank with signal-register-head water meter that will produce electrical signal indicating need for regeneration on reaching hand-set total in gallons (liters).  Design so signal will continue until reset.

Retain subparagraph below only for single mineral-tank units.

2) Demand-Initiated Control:  Equip single mineral-tank units with automatic-reset-head water meter that electrically activates cycle controller to initiate regeneration at preset total in gallons (liters).  Design so head automatically resets to preset total in gallons (liters) for next service run.

Retain subparagraph below only for twin mineral-tank units.

3) Demand-Initiated Control:  Equip each mineral tank of twin mineral-tank units with automatic-reset-head water meters that electrically activate cycle controllers to initiate regeneration at preset total in gallons (liters).  Design so heads automatically reset to preset total in gallons (liters) for next service run.  Include electrical lockout to prevent simultaneous regeneration of both tanks.

Retain subparagraph below only for twin mineral-tank units.

4) Demand-Initiated Control:  Equip each mineral tank of twin mineral-tank units with automatic-reset-head water meter in common outlet header that electrically activates cycle controller to automatically regenerate one mineral tank at preset total in gallons (liters) and divert flow to other tank.  Set to repeat with other tank.  Include electrical lockout to prevent simultaneous regeneration of both tanks.

Retain subparagraph below only for units with three or more mineral tanks.

5) Demand-Initiated Control:  Equip each mineral tank of multiple mineral-tank units with automatic-reset-head water meters that electrically activate cycle controllers to automatically regenerate at preset total in gallons (liters).  Design so heads automatically reset to preset total in gallons (liters) for next service run.  Include electrical lockouts to prevent simultaneous regeneration of more than one tank.

First subparagraph below may be used with any multiple mineral-tank arrangement.

6) Demand-Initiated Control:  Equip each mineral tank of multiple mineral-tank units with automatic-reset-head water meter in common outlet header that electrically activates cycle controller to automatically regenerate one mineral tank at preset total in gallons (liters) and divert flow to other tanks.  Set to repeat with other tanks.  Include electrical lockouts to prevent simultaneous regeneration of more than one tank.

8. Brine Tank:  Combination measuring and wet-salt storing system.

a. Tank and Cover Material:  Fiberglass, 3/16 inch (4.8 mm) thick; or molded PE, 3/8 inch (9.5 mm) thick.

b. Brine Valve:  Float operated and plastic fitted for automatic control of brine withdrawn and freshwater refill.

c. Size:  Large enough for at least four regenerations at full salting.

9. Factory-Installed Accessories:

a. Piping, valves, tubing, and drains.

b. Sampling cocks.

c. Main-operating-valve position indicators.

d. Water meters.

If more than one commercial water softener is on Project, delete paragraph and subparagraphs below and schedule commercial water softeners on Drawings.

B. Capacity and Characteristics:

1. Service:  [Cold] [Hot] water.

2. Water Analysis:

a. Hardness:  <Insert grains/gal. or ppm (mg/L).>

b. Iron:  <Insert ppm (mg/L).>

c. Dissolved Solids:  <Insert ppm (mg/L).>

d. Concentration:  <Insert pH.>

e. Inlet Water Pressure:  <Insert psig (kPa).>

f. Water Temperature:  <Insert deg F (deg C).>

3. Continuous Service Flow Rate:  <Insert number> gpm at 15-psig (<Insert number> L/s at 104-kPa) pressure drop.

4. Peak Service Flow Rate:  <Insert number> gpm at 25-psig (<Insert number> L/s at 173-kPa) pressure drop.

5. Water Meter Size:  <Insert NPS (DN).>

6. Manifold Pipe Size:  <Insert NPS (DN).>

7. Backwash to Drain Pipe Size:  <Insert NPS (DN).>

8. Water Consumption:  <Insert gal./day (cu. m/day).>

9. Water Demand:  <Insert hours/day.>

10. Number of Mineral Tanks:  [One] [Two] [Three] <Insert number>.

11. Mineral Quantity, Each Tank:  <Insert cu. ft. (cu. m).>

12. Mineral Exchange Capacity:  <Insert grains/cu. ft. per lb (kg/cu. m per kg) of salt.>

13. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phases:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

14. Salt Capacity:  <Insert lb (kg).>

15. Minimum Number of Regenerations per Refill:  <Insert number.>

16. Floor Area Required:  <Insert sq. ft. (sq. m).>

17. Height Required:  <Insert inches (mm).>

2.4 CHEMICALS

Insert more capacity in first paragraph below for high-temperature water or other applications as required.  Natural zeolite minerals that cost less may also be used but require replacement more frequently than resin.

A. Mineral:  High-capacity, sulfonated-polystyrene ion-exchange resin that is stable over entire pH range with good resistance to bead fracture from attrition or shock.

1. Exchange Capacity:  [30,000 grains/cu. ft. (69 kg/cu. m)] <Insert capacity> of calcium carbonate of resin when regenerated with 15 lb (6.8 kg) of salt.

B. Salt for Brine Tanks:  High-purity sodium chloride, free of dirt and foreign material.  Rock and granulated forms are not acceptable.

1. Form:  Processed, [food-grade salt pellets] [plain salt pellets] [crystallized solar salt from shallow ponds and milled into irregular particles] [plain, brine block salt].

2.5 WATER TESTING SETS

A. Description:  Manufacturer's standard water-hardness testing apparatus and chemicals with testing procedure instructions.  Include metal container suitable for wall mounting.

2.6 SOURCE QUALITY CONTROL

A. Hydrostatically test mineral tanks before shipment to minimum of one and one-half times pressure rating.

B. Prepare test reports.

PART 3 -  EXECUTION

3.1 CONCRETE BASES

Coordinate sizes and locations of concrete bases.  Verify structural requirements with structural engineer.

A. Install concrete bases of dimensions indicated for commercial water softeners.  Refer to Division 15 Section "Basic Mechanical Materials and Methods."

Revise subparagraphs below based on installed equipment.  Indicate dowel-rod quantity, size, and spacing on Drawings.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevation required for proper attachment to supported equipment.

B. Cast-in-place concrete materials and placement requirements are specified in Division 3.

3.2 WATER SOFTENER INSTALLATION

A. Install household water softeners on floor.[ Anchor water softener and brine tanks to substrate.]

B. Install commercial water softener equipment on concrete bases, level and plumb.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices that require servicing are accessible.  Anchor mineral and brine tanks and floor-mounting accessories to substrate.

Retain first paragraph below for Project in a seismic area.  Add special requirements for seismic restraints here or detail on Drawings.

C. Install seismic restraints for tanks and floor-mounting accessories and anchor to building structure.

D. Install brine lines and fittings furnished by equipment manufacturer but not specified to be factory installed.

E. Prepare mineral-tank distribution system and underbed for minerals and place specified mineral into mineral tanks.

F. Install water testing sets mounted on wall, unless otherwise indicated, and near water softeners.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to equipment to allow service and maintenance.

C. Make piping connections between water-softener-unit headers and dissimilar-metal water piping with dielectric fittings.  Dielectric fittings are specified in Division 15 Section "Basic Mechanical Materials and Methods."

D. Install shutoff valves on raw-water inlet and soft-water outlet piping of each mineral tank[, and on inlet and outlet headers].

1. Metal general-duty valves are specified in Division 15 Section "Valves."

2. Plastic valves are specified in Division 15 Section "Domestic Water Piping."

Retain subparagraph below if factory-installed valves are acceptable.

3. Exception:  Water softeners with factory-installed shutoff valves at locations indicated.

E. Install pressure gages on raw-water inlet and soft-water outlet piping of each mineral tank.  Pressure gages are specified in Division 15 Section "Meters and Gages."

Retain subparagraph below if factory-installed valves are acceptable.

1. Exception:  Water softeners with factory-installed pressure gages at locations indicated.

Retain one or both subparagraphs below only if pressure gages are not required.

2. Exception:  Household water softeners.

3. Exception:  Water softeners in hot-water service.

F. Install valved bypass water piping around water softeners.

1. Metal general-duty valves are specified in Division 15 Section "Valves."

2. Plastic valves are specified in Division 15 Section "Domestic Water Piping."

3. Water piping is specified in Division 15 Section "Domestic Water Piping."

Retain one or both subparagraphs below only if bypass is not required.

4. Exception:  Household water softeners.

5. Exception:  Water softeners in hot-water service.

G. Install drains as indirect wastes to spill into open drains or over floor drains.

H. Ground equipment according to Division 16 Section "Grounding and Bonding."

I. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

2. Operational Test:  After electrical circuitry has been energized, start units to confirm proper unit operation.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning water softeners that do not pass tests and inspections and retest as specified above.

3.5 STARTUP SERVICE

Retain first paragraph and subparagraph below if factory-authorized service representative is required.

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

B. Add water to brine tanks and fill with salt.

1. Household Water Softeners:  Processed [food-grade salt pellets] [plain salt pellets] [crystallized solar salt] <Insert salt form>.

2. Commercial Water Softeners:  [Plain salt pellets] [Crystallized solar salt] [Plain, brine block salt] [Food-grade salt pellets] <Insert salt form>.

C. Sample water softener effluent after startup and at three consecutive seven-day intervals (total of four samples), and prepare certified test reports for required water performance characteristics.  Comply with the following:

Revise list below to suit Project.

1. ASTM D 859, "Test Method for Silica in Water."

2. ASTM D 1067, "Test Methods for Acidity or Alkalinity of Water."

3. ASTM D 1068, "Test Methods for Iron in Water."

4. ASTM D 1126, "Test Method for Hardness in Water."

5. ASTM D 1129, "Terminology Relating to Water."

6. ASTM D 3370, "Practices for Sampling Water from Closed Conduits."

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain water softeners.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15469

WATER SOFTENERS
15469 - 14

