Copyright 2004 AIA
MASTERSPEC Full Length
06/04 (R 06/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15543 - FUEL-FIRED UNIT HEATERS
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include fuel-fired unit heaters may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes [gas] [oil]-fired unit heaters.

1.3 SUBMITTALS

A. Product Data:  For each type of fuel-fired unit heater indicated.  Include rated capacities, operating characteristics, and accessories.

In paragraph below, retain first option if equipment is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Shop Drawings:  [For fuel-fired unit heaters; signed and sealed by a qualified professional engineer.  Include] [For fuel-fired unit heaters.  Include] plans, elevations, sections, details, and attachments to other work.

1. Prepared by or under the supervision of a qualified professional engineer detailing fabrication and assembly of fuel-fired unit heaters, as well as procedures and diagrams.

2. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

3. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain option in subparagraph below if thermostat is specified in this Section; delete if thermostats for these units are specified in Division 15 Section "HVAC Instrumentation and Controls."

4. Wiring Diagrams:  Power[, signal, and control] wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Plans, elevations, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Structural members to which equipment will be attached.

2. Items penetrating roof and the following:

a. Vent and gas piping rough-ins and connections.

b. <Insert item.>

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

D. Manufacturer Seismic Qualification Certification:  Submit certification that fuel-fired unit heaters, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For fuel-fired unit heaters to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

B. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace heat exchanger of fuel-fired unit heater that fails in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below.  Two-year warranty is applicable to aluminized heat exchangers; five-year warranty, to stainless-steel heat exchangers.

1. Warranty Period:  [Two] [Five] <Insert number> years from date of Substantial Completion.

1.6 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraph below to suit Project.

1. Fan Belts:  [One] <Insert number> for each belt-driven fan size.

PART 2 -  PRODUCTS

2.1 GAS-FIRED UNIT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Lennox Industries, Inc.

2. Modine Manufacturing Company.

3. Reznor/Thomas & Betts Corporation.

4. Sterling HVAC Products; Div. of Mestek Technology Inc.

5. <Insert manufacturer's name.>

D. Description:  Factory assembled, piped, and wired, and complying with ANSI Z83.8/CSA 2.6.

E. Fuel Type:  Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

Retain first paragraph below unless more than one type of venting is required; in which case, delete below and indicate type of venting in a schedule on Drawings.  See the sample schedule in the Evaluations.

F. Type of Venting:  [Gravity] [Powered] [Indoor, separated combustion, power] vented.

G. Housing:  Steel, with integral draft hood and inserts for suspension mounting rods.

1. External Casings and Cabinets:  [Baked enamel] [Powder coating] over corrosion-resistant-treated surface.

Retain subparagraph and associated subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

2. Suspension Attachments:  Reinforce suspension attachments at connection to fuel-fired unit heaters.

a. Seismic Fabrication Requirements:  Fabricate suspension attachments of fuel-fired unit heaters, accessories mountings, and components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when fuel-fired unit heater is anchored to building structure.

Retain paragraph below unless more than one heat-exchanger material is required; in which case, delete below and indicate heat-exchanger material in a schedule on Drawings.  See the sample schedule in the Evaluations.

H. Heat Exchanger:  [Aluminized] [Stainless] steel.

Retain paragraph below unless more than one burner material is required; in which case, delete below and indicate burner material in a schedule on Drawings.  See the sample schedule in the Evaluations.

I. Burner Material:  [Aluminized steel with stainless-steel inserts] [Stainless steel].

Retain one or both of first two paragraphs and associated subparagraphs below, or revise to suit selected equipment.  If multiple units are required and some units require propeller fans and some require centrifugal fans, indicate fan type in a schedule on Drawings.  See the sample schedule in the Evaluations.

J. Unit Fan:  [Formed-steel] [Aluminum] propeller blades riveted to heavy-gage steel spider bolted to cast-iron hub, dynamically balanced, and resiliently mounted.

1. Fan-Blade Guard:  Galvanized steel, complying with OSHA specifications, removable for maintenance.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

2. General requirements for motors are specified in Division 15 Section "Motors."

a. Motors:  Totally enclosed with internal thermal-overload protection and complying with Division 15 Section "Motors."

b. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

c. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

K. Unit Fan:  Steel, centrifugal fan dynamically balanced and resiliently mounted.

1. Belt-Driven Drive Assembly:  Resiliently mounted to housing, with the following features:

a. Fan Shaft:  Turned, ground, and polished steel; keyed to wheel hub.

b. Shaft Bearings:  Permanently lubricated, permanently sealed, self-aligning ball bearings.

c. Pulleys:  Cast-iron, adjustable-pitch motor pulley.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

2. General requirements for motors are specified in Division 15 Section "Motors."

a. Motors:  Totally enclosed with internal thermal-overload protection and complying with Division 15 Section "Motors."

b. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

c. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

L. Controls:  Regulated redundant gas valve containing pilot solenoid valve, electric gas valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff all in one body.

1. Gas Control Valve:  [Single stage] [Two stage] [Modulating].

2. Ignition:  [Standing pilot] [Electronically controlled electric spark with flame sensor].

3. Fan Thermal Switch:  Operates fan on heat-exchanger temperature.

First option in first subparagraph below is for gravity-vented units; second option is for units with a power venter.

4. Vent Flow Verification:  [Flame rollout switch] [Differential pressure switch to verify open vent].

5. Control transformer.

6. High Limit:  Thermal switch or fuse to stop burner.

7. Thermostats:  Devices and wiring are specified in Division 15 Section "HVAC Instrumentation and Controls."

Retain subparagraph above or one of four subparagraphs below, or revise to suit selected equipment.

8. Thermostat:  Single-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

9. Thermostat:  2-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

10. Thermostat:  Single-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

11. Thermostat:  2-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

M. Discharge Louvers:  Independently adjustable horizontal blades.

N. Accessories:

Retain one or more of seven optional accessories below.

1. Vertical discharge louvers.

2. Discharge Nozzle:  Discharge at [25 to 65 degrees (0.44 to 1.13 radians)] [50 to 90 degrees (0.87 to 1.57 radians)] from horizontal.

3. Four-point suspension kit.

4. Summer fan switch.

5. Unit-mounted thermostat bracket.

Retain subparagraph below for power-vented model.

6. Power Venter:  Centrifugal aluminized-steel fan, with stainless-steel shaft; 120-V ac motor.

Retain subparagraph below for separated-combustion model.

7. Concentric, Terminal Vent Assembly:  Combined combustion-air inlet and power-vent outlet with wall or roof caps.  Include adapter assembly for connection to inlet and outlet pipes, and flashing for wall or roof penetration.

If Project has more than one type or configuration of fuel-fired unit heater, delete paragraph and subparagraphs below and schedule unit heaters on Drawings.

O. Capacities and Characteristics:

1. Gas Input:  <Insert Btu/h (kW).>

2. Gas Output:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

3. Minimum Combustion Efficiency:  [80] <Insert value> percent.

4. Minimum Airflow:  <Insert cfm (L/s).>

5. External Static Pressure:  <Insert inches wg (kPa).>

6. Motor Size:  <Insert horsepower.>

7. Motor Speed:  <Insert number> rpm.

8. Electrical Characteristics:

a. Volts:  [120] [208] [230] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.2 OIL-FIRED UNIT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Modine Manufacturing Company.

2. Reznor/Thomas & Betts Corporation.

3. Sterling HVAC Products; Div. of Mestek Technology Inc.

4. <Insert manufacturer's name.>

D. Description:  Factory assembled, piped, and wired, and complying with UL 731.

E. Housing:  Steel, with inserts for suspension mounting rods.

1. External Casings and Cabinets:  [Baked enamel] [Powder coating] over corrosion-resistant-treated surface.

Retain subparagraph and associated subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

2. Suspension Attachments:  Reinforce suspension attachments at connection to fuel-fired unit heaters.

a. Seismic Fabrication Requirements:  Fabricate suspension attachments of fuel-fired unit heaters, accessories mountings, and components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when fuel-fired unit heater is anchored to building structure.

F. Heat Exchanger:  Minimum 0.09-inch (2.2-mm) steel.

G. Burners:  Flame-retention, pressure-atomizing, forced-draft, gun type; with integral fuel pump and electronic spark ignition and flame safety.

1. Safety Device:  Oil-pressure switch.

Retain one of first two paragraphs and associated subparagraphs below or revise to suit selected equipment.  If multiple units are required and some units require propeller fans and some require centrifugal fans, indicate fan type in a schedule on Drawings.  See the sample schedule in the Evaluations.

H. Unit Fan:  Propeller fan with aluminum blades dynamically balanced and resiliently mounted.

1. Steel fan-blade guard.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

2. General requirements for motors are specified in Division 15 Section "Motors."

a. Motors:  Totally enclosed with internal thermal-overload protection and complying with Division 15 Section "Motors."

b. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

c. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

I. Unit Fan:  Steel, centrifugal fan dynamically balanced and resiliently mounted.

1. Belt driven with adjustable-pitch motor sheave.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

2. General requirements for motors are specified in Division 15 Section "Motors."

a. Motors:  Totally enclosed with internal thermal-overload protection and complying with Division 15 Section "Motors."

b. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

c. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

J. Controls:  Factory piped and prewired to electrical junction box mounted on unit, including the following:

1. Control Transformer:  Integrally mounted, 120 to 24 V ac.

2. Cad-cell safety system.

3. Manual reset safety.

4. Thermostat:  Devices and wiring are specified in Division 15 Section "HVAC Instrumentation and Controls."

Retain subparagraph above or one of four subparagraphs below, or revise to suit selected equipment.

5. Thermostat:  Single-stage, 24-V ac, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

6. Thermostat:  2-stage, 24-V ac, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

7. Thermostat:  Single-stage, 24-V ac type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

8. Thermostat:  2-stage, 24-V ac type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

K. Automatic Fan Thermal Switch:  Fan operates with heat-exchanger temperature more than 135 deg F (58 deg C).

L. Discharge Louvers:  Independently adjustable horizontal blades.

M. Accessories:

Retain one or more of seven optional accessories below.

1. Vertical discharge louvers.

2. Discharge Nozzle:  Discharge at [25 to 65 degrees (0.44 to 1.13 radians)] [50 to 90 degrees (0.87 to 1.57 radians)] from horizontal.

3. Summer fan switch.

4. Unit-mounted thermostat bracket.

5. Oil Booster Pump:  [30-gph (108-L/h)] [70-gph (252-L/h)] capacity; motor and 2-stage fuel unit with pressure-regulating valve and strainer.

6. Oil safety valve.

7. Outdoor Combustion-Air Adapter:  Sealed to housing and fitted with quick access cover or door and fitting for terminating outdoor-air duct.

If Project has more than one type or configuration of fuel-fired unit heater, delete paragraph and subparagraphs below and schedule unit heaters on Drawings.

N. Capacities and Characteristics:

1. Oil Input:  <Insert gph (L/s).>

2. Heat Output:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

3. Minimum Combustion Efficiency:  [80] <Insert value> percent.

4. Minimum Airflow:  <Insert cfm (L/s).>

5. External Static Pressure:  <Insert inches wg (kPa).>

6. Motor Size:  <Insert horsepower.>

7. Motor Speed:  <Insert number> rpm.

8. Electrical Characteristics:

a. Volts:  [120] [208] [230] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain paragraph below for gas-fired units.  Retain first option for projects in the U.S.; retain second option for projects in Canada.

A. Install and connect gas-fired unit heaters and associated fuel and vent features and systems according to [NFPA 54] [CAN/CSA B149.1], applicable local codes and regulations, and manufacturer's written installation instructions.

Retain first paragraph below for oil-fired units.  Retain first option for projects in the U.S.; retain second option for projects in Canada.

B. Install and connect oil-fired unit heaters and associated fuel and vent piping according to [NFPA 31] [CAN/CSA B139], applicable local codes and regulations, and manufacturer's written installation instructions.

C. Suspended Units:  Suspend from substrate using threaded rods, spring hangers, and building attachments.  Secure rods to unit hanger attachments.  Adjust hangers so unit is level and plumb.

Delete subparagraph below if Project site is aseismic.

1. Restrain the unit to resist code-required horizontal acceleration.

D. Substrate-Mounted Units:  Provide supports connected to substrate.  Secure units to supports.

1. Spring hangers[ and seismic restraints] are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

Delete subparagraph below if Project site is aseismic.

2. Anchor the unit to resist code-required horizontal acceleration.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to fuel-fired unit heater to allow service and maintenance.

Retain paragraph below for gas-fired units.

C. Gas Piping:  Comply with Division 15 Section "Fuel Gas Piping." Connect gas piping to gas train inlet; provide union with enough clearance for burner removal and service.

Retain first paragraph below for oil-fired units.

D. Fuel Oil Piping:  Comply Division 15 Section "Fuel Oil Piping." Connect to fuel oil supply and return piping with shutoff valve and union at each connection.

E. Vent Connections:  Comply with Division 15 Section "Breechings, Chimneys, and Stacks."

F. Electrical Connections:  Comply with applicable requirements in Division 16 Sections.

1. Install electrical devices furnished with heaters but not specified to be factory mounted.

3.3 FIELD QUALITY CONTROL

Retain one of first two paragraphs below.  Retain first to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed by either entity in two paragraphs above.

C. Tests and Inspections:

1. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

2. Verify bearing lubrication.

3. Verify proper motor rotation.

4. Test Reports:  Prepare a written report to record the following:

a. Test procedures used.

b. Test results that comply with requirements.

c. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

D. Remove and replace malfunctioning units and retest as specified above.

3.4 ADJUSTING

A. Adjust initial temperature set points.

B. Adjust burner and other unit components for optimum heating performance and efficiency.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain fuel-fired unit heaters.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15543END OF SECTION 15543

FUEL-FIRED UNIT HEATERS
15543 - 1

