Copyright 2005 AIA
MASTERSPEC Full Length
06/05 (R 06/06)

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15762 - UNIT HEATERS
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include unit heaters may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Cabinet unit heaters with centrifugal fans and [hot-water] [steam] [electric-resistance heating] coils.

2. Propeller unit heaters with [hot-water] [steam] [electric-resistance heating] coils.

3. Wall and ceiling heaters with propeller fans and electric-resistance heating coils.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. BAS:  Building automation system.

B. CWP:  Cold working pressure.

C. PTFE:  Polytetrafluoroethylene plastic.

D. TFE:  Tetrafluoroethylene plastic.

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each product indicated.

B. LEED Submittal:

1. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

C. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Edit subparagraphs below to suit Project.

1. Plans, elevations, sections, and details.

2. Location and size of each field connection.

3. Details of anchorages and attachments to structure and to supported equipment.

4. Equipment schedules to include rated capacities, operating characteristics, furnished specialties, and accessories.

Retain subparagraph below for hydronic and steam cabinet unit heaters.

5. Location and arrangement of piping valves and specialties.

Retain first subparagraph below for cabinet unit heaters with integral controls; delete if control devices are specified in Division 15 Section "HVAC Instrumentation and Controls."

6. Location and arrangement of integral controls.

7. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Floor plans, reflected ceiling plans, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs and associated subparagraphs below to suit Project.

1. Suspended ceiling components.

2. Structural members to which unit heaters will be attached.

3. Method of attaching hangers to building structure.

4. Size and location of initial access modules for acoustical tile.

5. Items penetrating finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. <Insert item.>

6. Perimeter moldings for exposed or partially exposed cabinets.

E. Samples for Initial Selection:  Finish colors for units with factory-applied color finishes.

Delete paragraph above if colors are preselected and specified or scheduled.  Retain paragraph below with or without above.

F. Samples for Verification:  Finish colors for each type of cabinet unit heater and wall and ceiling heaters indicated with factory-applied color finishes.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

G. Manufacturer Seismic Qualification Certification:  Submit certification that cabinet unit heaters, accessories, and components will withstand seismic forces defined in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

H. Field quality-control test reports.

I. Operation and Maintenance Data:  For cabinet unit heaters to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

B. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1-2004.

C. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.6 EXTRA MATERIALS

Retain this Article for cabinet unit heaters with filters.  Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Cabinet Unit Heater Filters:  Furnish [one] <Insert number> spare filter(s) for each filter installed.

PART 2 -  PRODUCTS

2.1 CABINET UNIT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Airtherm; a Mestek Company.

2. Berko Electric Heating; a division of Marley Engineered Products.

3. Carrier Corporation.

4. Chromalox, Inc.; a division of Emerson Electric Company.

5. Dunham-Bush, Inc.

6. Engineered Air Ltd.

7. Indeeco.

8. International Environmental Corporation.

9. Markel Products; a division of TPI Corporation.

10. Marley Electric Heating; a division of Marley Engineered Products.

11. McQuay International.

12. Ouellet Canada Inc.

13. QMark Electric Heating; a division of Marley Engineered Products.

14. Rosemex Products.

15. Trane.

16. USA Coil & Air.

17. <Insert manufacturer's name.>

D. Description:  A factory-assembled and -tested unit complying with ARI 440.

Retain subparagraph below for electric cabinet unit heaters.

1. Comply with UL 2021.

Retain and edit one "Coil Section Insulation" Paragraph below.  Flexible elastomeric insulation and mineral-fiber insulation with a foil face are available from some manufacturers to reduce the number of glass or mineral fibers circulating through the air-conditioned space.

Retain paragraph and subparagraphs below for duct-liner-type, glass-fiber insulation.

E. Coil Section Insulation:  ASTM C 1071; surfaces exposed to airstream shall be [aluminum-foil facing] [erosion-resistant coating] to prevent erosion of glass fibers.

1. Thickness:  [1/2 inch (13 mm)] [1 inch (25 mm)] [1-1/2 inches (38 mm)].

2. Thermal Conductivity (k-Value):  0.26 Btu x in./h x sq. ft. at 75 deg F (0.037 W/m x K at 24 deg C) mean temperature.

3. Fire-Hazard Classification:  Maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84.

4. Adhesive:  Comply with ASTM C 916 and with NFPA 90A or NFPA 90B.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain paragraph and subparagraphs below for flexible elastomeric insulation.

F. Coil Section Insulation:  Comply with NFPA 90A or NFPA 90B.  Unicellular polyethylene thermal plastic, preformed sheet insulation complying with ASTM C 534, Type II, except for density.

1. Thickness:  [3/8 inch (9 mm)] [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)].

2. Thermal Conductivity (k-Value):  0.24 Btu x in./h x sq. ft. at 75 deg F (0.034 W/m x K at 24 deg C) mean temperature.

3. Fire-Hazard Classification:  Maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM C 411.

4. Adhesive:  As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain paragraph and subparagraphs below for surface, semirecessed, and fully recessed units.  Cabinet is not required for concealed units.  Coordinate custom-color requirements in paragraph below with sample submittal requirements.  Coordinate field painting with Division 9 painting Sections.

G. Cabinet:  Steel with [factory prime coating, ready for field painting] [baked-enamel finish with manufacturer's standard paint, in color selected by Architect] [baked-enamel finish with manufacturer's custom paint, in color selected by Architect].

First option in two subparagraphs below, for thickness of 0.0528 inch (1.35 mm), is the equivalent of 16-gage steel; second option, for 0.0677 inch (1.7 mm), is the equivalent of 14-gage steel.

1. Vertical Unit, Exposed Front Panels:  Minimum [0.0528-inch- (1.35-mm-)] [0.0677-inch- (1.7-mm-)] thick, [galvanized,] sheet steel, removable panels with channel-formed edges secured with tamperproof cam fasteners.

2. Horizontal Unit, Exposed Bottom Panels:  Minimum [0.0528-inch- (1.35-mm-)] [0.0677-inch- (1.7-mm-)] thick, [galvanized,] sheet steel, removable panels secured with tamperproof cam fasteners and safety chain.

Retain first subparagraph below for units that are semirecessed or fully recessed in walls or ceilings.

3. Recessing Flanges:  Steel, finished to match cabinet.

4. Control Access Door:  Key operated.

Retain first subparagraph below for surface, vertical, wall-mounting units.

5. Base:  Minimum 0.0528-inch- (1.35-mm-) thick steel, finished to match cabinet, [4 inches (100 mm)] [6 inches (150 mm)] <Insert dimension> high with leveling bolts.

6. Extended Piping Compartment:  [8-inch- (200-mm-)] <Insert dimension> wide piping end pocket.

Accessories described in two subparagraphs below are furnished for vertical, wall-mounting units only.

7. False Back:  Minimum 0.0428-inch- (1.1-mm-) thick steel, finished to match cabinet.

8. Outdoor-Air Wall Box:  Minimum 0.1265-inch- (3.2-mm-) thick, aluminum, rain-resistant louver and box with integral eliminators and bird screen.  Aluminum louver with [anodized] [baked-enamel] finish in color selected by Architect from manufacturer's [standard] [custom] colors.

Retain subparagraph below only if retaining subparagraph above.  Retain second or third option below if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004 and Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.

a. Outdoor-Air Damper:  Galvanized-steel blades with edge and end seals and nylon bearings; with [manual] [electronic] [pneumatic], two-position actuators.

Verify available filter types with manufacturer.  Indicate filter thickness in "Capacities and Characteristics" Paragraph in this Article or in the Cabinet Unit Heater Schedule on Drawings.

H. Filters:  Minimum arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Retain one or more of three subparagraphs below.  If retaining more than one filter type, indicate type for each unit in the Cabinet Unit Heater Schedule on Drawings.

1. Washable Foam:  70 percent arrestance and 3 MERV.

2. Glass Fiber Treated with Adhesive:  80 percent arrestance and 5 MERV.

3. Pleated:  90 percent arrestance and 7 MERV.

Retain one of first three paragraphs below.

I. Hot-Water Coil:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 200 psig (1378 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C).  Include manual air vent and drain.

J. Steam Coil:  Copper[ distributing] tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 75 psig (517 kPa).

Some manufacturers do not provide electric-resistance heating coils in downflow configuration.

K. Electric-Resistance Heating Coil:  Nickel-chromium heating wire, free from expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with fuses in terminal box for overcurrent protection and limit controls for high-temperature protection.  Terminate elements in stainless-steel machine-staked terminals secured with stainless-steel hardware.

L. Fan and Motor Board:  Removable.

1. Fan:  Forward curved, [high static, ]double width, centrifugal; directly connected to motor.  Thermoplastic or painted-steel wheels, and aluminum, painted-steel, or galvanized-steel fan scrolls.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

2. Motor:  Permanently lubricated, multispeed; resiliently mounted on motor board.  Comply with requirements in Division 15 Section "Common Motor Requirements for HVAC Equipment."

3. Wiring Terminations:  Connect motor to chassis wiring with plug connection.

Retain first paragraph and applicable subparagraphs below to require factory-piping package.

M. Factory, Hot-Water Piping Package:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M Type C)] copper tube with wrought-copper fittings and brazed joints.  Label piping to indicate service, inlet and outlet.

Retain one or more of first four subparagraphs and associated subparagraphs below.

1. [Two] [Three]-way, [two-position] [modulating] control valve.[  Three-way valve packages shall include bypass line with manually adjustable balance device.]

2. Hose Kits:  Minimum 400-psig (2758-kPa) working pressure, and operating temperatures from 33 to 211 deg F (0.5 to 99 deg C).  Tag hose kits to equipment designations.

a. Length:  [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension>.

b. Minimum Diameter:  Equal to cabinet unit heater connection size.

3. Two-Piece, Ball Valves:  Bronze body with full-port, chrome-plated bronze ball; PTFE or TFE seats; and 600-psig (4140-kPa) minimum CWP rating and blowout-proof stem.

4. Calibrated-Orifice Balancing Valves:  Bronze body, ball type, 125-psig (860-kPa) working pressure, 250 deg F (121 deg C) maximum operating temperature; with calibrated orifice or venture, connection for portable differential pressure meter with integral seals, threaded ends, and equipped with a memory stop to retain set position.

5. Automatic Flow-Control Valve:  Brass or ferrous-metal body, 300-psig (2068-kPa) working pressure at 250 deg F (121 deg C), with removable, corrosion-resistant, tamperproof, self-cleaning, piston-spring; factory set to maintain constant indicated flow with plus or minus 10 percent over differential pressure range of 2 to 80 psig (13.8 to 552 kPa).

6. Y-Pattern, Hot-Water Strainers:  Cast-iron body (ASTM A 126, Class B); 125-psig (860-kPa) minimum working pressure; with threaded connections, bolted cover, perforated stainless-steel basket, and bottom drain connection.  Include minimum NPS 1/2 (DN 15) threaded pipe and full-port ball valve in strainer drain connection.

7. Wrought-Copper Unions:  ASME B16.22.

N. Control devices and operational sequences are specified in Division 15 Sections "HVAC Instrumentation and Controls" and "Sequence of Operation."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

O. Basic Unit Controls:

1. Control voltage transformer.

Verify control features with manufacturer.

2. [Wall-mounting] [Unit-mounted] thermostat with the following features.

a. Heat-off switch.

b. Fan on-auto switch.

Retain first subparagraph below if multispeed motors are specified.

c. Manual fan speed switch.

d. Adjustable deadband.

e. [Concealed] [Exposed] set point.

f. [Concealed] [Exposed] indication.

g. Deg F (Deg C) indication.

3. [Wall-mounting] [Unit-mounted] temperature sensor.

4. Unoccupied period override push button.

5. Data entry and access port.

a. Input data includes room temperature, and occupied and unoccupied periods.

b. Output data includes room temperature, supply-air temperature, entering-water temperature, operating mode, and status.

Retain first paragraph and subparagraphs below and coordinate with "Basic Unit Controls" Paragraph and subparagraphs above or with control devices specified in Division 15 Section "HVAC Instrumentation and Controls."

P. [DDC ]Terminal Controller:

1. Scheduled Operation:  Occupied and unoccupied periods on seven-day clock with a minimum of four programmable periods per day.

2. Unoccupied Period Override:  [Two] <Insert number> hours.

3. Unit Supply-Air Fan Operations:

a. Occupied Periods:  Fan runs continuously.

b. Unoccupied Periods:  Fan cycles to maintain setback room temperature.

4. Heating Coil Operations:

a. Occupied Periods:  [Open control valve] [Modulate control valve] [Energize electric-resistance coil] to provide heating if room temperature falls below thermostat set point.

b. Unoccupied Periods:  Start fan and [open control valve] [modulate control valve] [energize electric-resistance coil] if room temperature falls below setback temperature.

Retain first subparagraph and associated subparagraphs below for automatic outdoor-air intake damper.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004 and Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.

5. Outdoor-Air Damper Operation:

a. Occupied Periods:  Open dampers.  Delay damper opening if room temperature is more than three degrees below set point.

b. Unoccupied Periods:  Close damper.

6. Controller shall have volatile-memory backup.

Q. BAS Interface Requirements:

1. Interface relay for scheduled operation.

2. Interface relay to provide indication of fault at central workstation.

3. Interface shall be [BAC-net] [or] [LonWorks] compatible for central BAS workstation and include the following functions:

a. Adjust set points.

b. Cabinet unit heater start, stop, and operating status.

c. Data inquiry, including [outdoor-air damper position, ]supply-air and room-air temperature.

d. Occupied and unoccupied schedules.

R. Electrical Connection:  Factory wire motors and controls for a single field connection.

If Project has more than one type or configuration of heater, delete paragraph and subparagraphs below and schedule cabinet unit heaters on Drawings.

S. Capacities and Characteristics:

1. Cabinet:

a. Vertical, Surface Mounted:  Upflow.

1) Top:  [Flat] [Sloped] [Flat or sloped].

2) Air Inlet:  [Open bottom] [Front, punched louver grille] [Front, extruded-aluminum bar grille].

3) Air Outlet:  [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

b. Vertical, Surface Mounted:  Downflow.

1) Top:  [Flat] [Sloped] [Flat or sloped].

2) Air Inlet:  [Front] [Top] [Front or top], [punched louver] [extruded-aluminum bar grille].

3) Air Outlet:  Front, [quad louver] [punched louver] [extruded-aluminum bar grille].

c. Vertical, Semirecessed:  Upflow.

1) Air Inlet:  [Open bottom] [Front, punched louver grille] [Front, extruded-aluminum bar grille].

2) Air Outlet:  [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

d. Vertical, Semirecessed:  Downflow.

1) Air Inlet:  [Front] [Top] [Front or top], [punched louver] [extruded-aluminum bar grille].

2) Air Outlet:  Front, [quad louver] [punched louver] [extruded-aluminum bar grille].

e. Vertical, Fully Recessed:  [Upflow] [Downflow].

1) Air Inlet and Outlet:  Front, [punched louver] [extruded-aluminum bar grille] inlet and [quad louver] [punched louver] [extruded-aluminum bar grille] outlet.

Retain subparagraph above or first two subparagraphs below.

2) Air Inlet:  [Front] [Duct connection], [punched louver] [extruded-aluminum bar grille].

3) Air Outlet:  [Front] [Duct connection], [quad louver] [punched louver] [extruded-aluminum bar grille].

f. Horizontal, Surface Mounted:

1) Air Inlet:  [Bottom] [Front] [Bottom or front], [punched louver] [extruded-aluminum bar grille].

2) Air Outlet:  [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

g. Horizontal, Semirecessed:

1) Air Inlet:  [Bottom] [Front] [Bottom or front], [punched louver] [extruded-aluminum bar grille].

2) Air Outlet:  [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

h. Horizontal, Fully Recessed:

1) Air Inlet and Outlet:  Front, [punched louver] [extruded-aluminum bar grille] inlet and [quad louver] [punched louver] [extruded-aluminum bar grille] outlet.

Retain subparagraph above or first two subparagraphs below.

2) Air Inlet:  [Front] [Duct connection], [punched louver] [extruded-aluminum bar grille].

3) Air Outlet:  [Front] [Duct connection], [quad louver] [punched louver] [extruded-aluminum bar grille].

2. Fan:

a. Airflow:  <Insert cfm (L/s).>

b. External Static Pressure:  <Insert inches wg (Pa).>

c. Fan Speed:  <Insert rpm.>

d. Motor Horsepower:  <Insert value.>

3. Heating Capacity:

a. Output:  <Insert Btu/h (kW).>

b. Entering-Air Temperature:  <Insert deg F (deg C).>

c. Air-Temperature Rise:  <Insert deg F (deg C).>

4. Hot-Water Heating Coil:

a. Water Flow:  <Insert gpm (L/s).>

b. Water-Side Pressure Loss:  <Insert feet wg (kPa).>

c. Entering-Water Temperature:  <Insert deg F (deg C).>

5. Steam Heating Coil:

a. Inlet Steam Pressure:  <Insert psig (kPa).>

b. Condensing Capacity:  <Insert lb/h (g/s).>

6. Electric-Resistance Heating Coil:

a. Capacity:  <Insert kW.>

b. Number of Steps:  <Insert number.>

7. Filters:

a. Face Area:  <Insert sq. ft. (sq. m).>

b. Thickness:  [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert thickness>.

8. Electrical Characteristics for Single-Point Connection:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.2 PROPELLER UNIT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Airtherm; a Mestek Company.

2. Engineered Air Ltd.

3. McQuay International.

4. Rosemex Products.

5. Ruffneck Heaters; a division of Lexa Corporation.

6. Trane.

7. <Insert manufacturer's name.>

C. Description:  An assembly including casing, coil, fan, and motor in [vertical] [and] [horizontal] discharge configuration with adjustable discharge louvers.

Retain paragraph below for electric unit heaters.

D. Comply with UL 2021.

Retain paragraph below for explosion-proof electric unit heaters.

E. Comply with UL 823.

F. Cabinet:  Removable panels for maintenance access to controls.

G. Cabinet Finish:  Manufacturer's [standard] [custom] baked enamel applied to factory-assembled and -tested propeller unit heater before shipping.

Retain first paragraph below to comply with LEED-NC Prerequisite EQ 1.

H. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

I. Discharge Louver:  Adjustable fin diffuser for horizontal units and conical diffuser for vertical units.

J. General Coil Requirements:  Test and rate [hot-water] [steam] propeller unit heater coils according to ASHRAE 33.

Retain one of first eight paragraphs below.  First paragraph is standard coil construction for hot-water heating systems.  Next four paragraphs are for situations where higher pressure ratings are required or corrosion resistance is required for some fluids inside the coils.

K. Hot-Water Coil:  Copper tube, minimum 0.025-inch (0.635-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 200 psig (1380 kPa) and a maximum entering-water temperature of 325 deg F (163 deg C), with manual air vent.  Test for leaks to 350 psig (2413 kPa) underwater.

L. Hot-Water Coil:  Cupronickel tube, minimum 0.031-inch (0.78-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 400 psig (2760 kPa) and a maximum entering-water temperature of 450 deg F (232 deg C), with manual air vent.  Test for leaks to 600 psig (4137 kPa) underwater.

M. Hot-Water Coil:  Red brass tube, minimum 0.049-inch (1.24-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 260 psig (1793 kPa) and a maximum entering-water temperature of 390 deg F (199 deg C), with manual air vent.  Test for leaks to 390 psig (2689 kPa) underwater.

N. Hot-Water Coil:  Steel tube, minimum 0.049-inch (1.24-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 400 psig (2760 kPa) and a maximum entering-water temperature of 450 deg F (232 deg C), with manual air vent.  Test for leaks to 600 psig (4137 kPa) underwater.

Paragraph below is industrial-quality construction available from a limited number of manufacturers.

O. Hot-Water Coil:  Vertical steel tube, minimum 0.065-inch (1.65-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 400 psig (2760 kPa) and a maximum entering-water temperature of 450 deg F (232 deg C), with steel headers at top and bottom.  Test for leaks to 600 psig (4137 kPa) underwater.

First paragraph below is standard coil construction for steam heating systems.  Next two paragraphs are for situations where higher pressure ratings are required or corrosion resistance is required for some fluids inside the coils.

P. Steam Coil:  Copper tube, minimum 0.025-inch (0.635-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 75 psig (520 kPa).

Q. Steam Coil:  Red brass tube, minimum 0.049-inch (1.24-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 75 psig (520 kPa).

Paragraph below is industrial-quality construction available from a limited number of manufacturers.

R. Steam Coil:  Vertical steel tube, minimum 0.065-inch (1.65-mm) wall thickness, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of [100 psig (690 kPa)] [200 psig (1380 kPa)], with steel headers at top and bottom.

S. Electric-Resistance Heating Elements:  Nickel-chromium heating wire, free from expansion noise and 60-Hz hum, embedded in magnesium oxide refractory and sealed in steel or corrosion-resistant metallic sheath with fins no closer than 0.16 inch (4 mm).  Element ends shall be enclosed in terminal box.  Fin surface temperature shall not exceed 550 deg F (288 deg C) at any point during normal operation.

1. Circuit Protection:  One-time fuses in terminal box for overcurrent protection and limit controls for high-temperature protection of heaters.

2. Wiring Terminations:  Stainless-steel or corrosion-resistant material.

T. Fan:  Propeller type with aluminum wheel directly mounted on motor shaft in the fan venturi.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified inDivision 15 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add paragraphs below to suit Project.

U. Fan Motors:  Comply with requirements in Division 15 Section "Common Motor Requirements for HVAC Equipment."

1. Motor Type:  Permanently lubricated, [explosion proof] [multispeed] [variable speed].

Delete first paragraph below if controls are part of control system specified in Division 15 Section "HVAC Instrumentation and Controls." See Evaluations for discussion on control schemes and energy efficiency.

V. Control Devices:

1. [Unit-mounted] [Wall-mounting], [variable ]fan-speed switch.

2. [Unit-mounted] [Wall-mounting] thermostat.

If Project has more than one type or size, delete paragraph and subparagraphs below and schedule propeller unit heaters on Drawings.

W. Capacities and Characteristics

1. Heating Capacity:

a. Heat Output:  <Insert Btu/h (kW).>

b. Length of Throw:  <Insert feet (m).>

c. Mounting Height:  <Insert feet (m).>

2. Water Coil:

a. Entering-Water Temperature:  <Insert deg F (deg C).>

b. Temperature Difference:  <Insert deg F (deg C).>

c. Water Flow:  <Insert gpm (L/s).>

d. Water-Side Pressure Drop:  <Insert feet (kPa).>

3. Steam Coil:

a. Inlet Pressure:  <Insert psig (kPa).>

b. Condensing Capacity:  <Insert lb/h (g/s).>

4. Electric Coil:

a. Heating Capacity:  <Insert kW.>

b. Number of Steps:  <Insert number.>

5. Supply Air:

a. Airflow:  <Insert cfm (L/s).>

b. Leaving-Air Temperature:  <Insert deg F (deg C).>

c. Entering-Air Temperature:  <Insert deg F (deg C).>

6. Fan Motor:

a. High Speed:  <Insert rpm.>

b. Motor Size:  <Insert hp.>

7. Electrical Characteristics for Single-Point Connection:

a. Volts/Phase/Hertz:  <Insert values.>

b. Full-Load Amperes:  <Insert value.>

c. Minimum Circuit Amperes:  <Insert value.>

d. Maximum Overcurrent Protection:  <Insert value.>

2.3 WALL AND CEILING HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Berko Electric Heating; a division of Marley Engineered Products.

2. Chromalox, Inc.; a division of Emerson Electric Company.

3. Indeeco.

4. Markel Products; a division of TPI Corporation.

5. Marley Electric Heating; a division of Marley Engineered Products.

6. Ouellet Canada Inc.

7. QMark Electric Heating; a division of Marley Engineered Products.

8. Trane.

9. <Insert manufacturer's name.>

D. Description:  An assembly including chassis, electric heating coil, fan, motor, and controls.  Comply with UL 2021.

E. Cabinet:

1. Front Panel:  [Stamped-steel louver] [Extruded-aluminum bar grille], with removable panels fastened with tamperproof fasteners.

2. Finish:  Baked enamel over baked-on primer with manufacturer's [standard] [custom] color selected by Architect, applied to factory-assembled and -tested wall and ceiling heaters before shipping.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

3. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

F. Surface-Mounting Cabinet Enclosure:  Steel with finish to match cabinet.

G. Electric-Resistance Heating Coil:  Nickel-chromium heating wire, free from expansion noise and hum, embedded in magnesium oxide refractory and sealed in corrosion-resistant metallic sheath.  Terminate elements in stainless-steel, machine-staked terminals secured with stainless-steel hardware, and limit controls for high temperature protection.[  Provide integral circuit breaker for overcurrent protection.]

H. Fan:  Aluminum propeller directly connected to motor.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motor:  Permanently lubricated[, multispeed].  Comply with requirements inDivision 15 Section "Common Motor Requirements for HVAC Equipment."

I. Controls:  Unit-mounted thermostat.[  Low-voltage relay with transformer kit.]

J. Electrical Connection:  Factory wire motors and controls for a single field connection[ with disconnect switch].

If Project has more than one type or configuration of heater, delete paragraph and subparagraphs below and schedule wall and ceiling heaters on Drawings.

K. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. Fan Speed:  <Insert rpm.>

3. Heating Coil:  <Insert kW.>

4. Electrical Characteristics for Single-Point Connection:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas to receive unit heaters for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Examine roughing-in for [piping and ]electrical connections to verify actual locations before unit heater installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain first paragraph below for vertical, wall-mounting cabinet unit heaters with wall boxes and outdoor-air intake louvers.

A. Install wall boxes in finished wall assembly; seal and weatherproof.  Joint-sealant materials and applications are specified in Division 7 Section "Joint Sealants."

B. Install cabinet unit heaters to comply with NFPA 90A.

C. Install propeller unit heaters level and plumb.

D. Suspend cabinet unit heaters from structure with elastomeric hangers[ and seismic restraints].  Vibration isolators[ and seismic restraints] are specified in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

E. Suspend propeller unit heaters from structure with all-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop].  Hanger rods and attachments to structure are specified in Division 15 Section "Hangers and Supports for HVAC Piping and Equipment." Vibration hangers are specified in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Retain first paragraph below if controls are provided by unit heater manufacturer.  To comply with requirements of the Americans with Disabilities Act, verify mounting height with authorities having jurisdiction.

F. Install wall-mounting thermostats and switch controls in electrical outlet boxes at heights to match lighting controls.  Verify location of thermostats and other exposed control sensors with Drawings and room details before installation.

G. Install new filters in each fan-coil unit within two weeks of Substantial Completion.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Connect piping to cabinet unit heater's factory, hot-water piping package.  Install the piping package if shipped loose.

Retain paragraph below for concealed cabinet unit heaters.  Coordinate duct installation requirements with Drawings and with requirements specified in Division 15 Sections "Metal Ducts," "Nonmetal Ducts," and "Duct Accessories."

D. Connect supply and return ducts to cabinet unit heaters with flexible duct connectors specified in Division 15 Section "Duct Accessories."

Retain paragraph below for cabinet unit heaters with either hot-water or steam coils.

E. Comply with safety requirements in UL 1995.

Retain paragraph below for hot-water propeller unit heaters and for cabinet unit heaters if factory piping package is not required.

F. Unless otherwise indicated, install union and gate or ball valve on supply-water connection and union and calibrated balancing valve on return-water connection of unit heater.  Hydronic specialties are specified in Division 15 Section "Hydronic Piping."

Retain first paragraph below for steam unit heaters.

G. Unless otherwise indicated, install union and gate or ball valve on steam-supply connection and union, strainer, steam trap, and gate or ball valve on condensate-return connection of unit heater.  Steam specialties are specified in Division 15 Section "Steam and Condensate Piping."

H. Ground equipment according to Division 16 Section "Grounding and Bonding."

I. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Retain first subparagraph below for units that have electric-resistance heating coils.

2. Operate electric heating elements through each stage to verify proper operation and electrical connections.

3. Test and adjust controls and safety devices.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning units and retest as specified above.

3.5 ADJUSTING

Retain this Article if control devices are specified in this Section; delete if they are specified in Division 15 Sections "HVAC Instrumentation and Controls" and "Sequence of Operation."

A. Adjust initial temperature set points.

B. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

3.6 DEMONSTRATION

Delete this Article if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain cabinet unit heaters.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15762

UNIT HEATERS
15762 - 1

