Copyright 2005 AIA
MASTERSPEC
06/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15774 - RADIANT-HEATING ELECTRIC CABLES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes electric heating cables for ceiling or floor radiant heating, snow and ice melting on pavement, and freezer-floor frost-heave prevention with the following electric heating cables:

1. Mineral insulated, series resistance.

2. Plastic insulated, series resistance.

3. Self-regulating, parallel resistance.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Radiant Heating and Cooling Units" for factory-fabricated electric heating panels for ceiling and wall applications.

2. Division 15 Section "Radiant-Heating Electric Panels."

3. Division 15 Section "Heat Tracing for Fire-Suppression Piping."

4. Division 15 Section "Heat Tracing for Plumbing Piping."

5. Division 15 Section "Heat Tracing for HVAC Piping."

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated.

1. Schedule heating capacity, length of cable, spacing, and electrical power requirement for each electric heating cable required.

B. Shop Drawings:  For electric heating cable.  Include plans, sections, details, and attachments to other work.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Ceiling suspension assembly members.

2. Method of attaching hangers to building structure.

3. Items installed in finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. Perimeter moldings.

g. <Insert item.>

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For electric heating cables to include in operation and maintenance manuals.

F. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 COORDINATION

A. Coordinate layout and installation of electric heating cables and system components with other construction.

Retain subparagraph below for snow-melting cable in pavement or for radiant-heating cable in concrete floor.

1. Coordinate concrete, reinforcement, and formwork with requirements specified in Division 3.

Retain subparagraph below for ceiling- or floor-mounting heating cable.

2. Coordinate with [ceiling] [floor] installation requirements.

Retain subparagraph below for roof-mounting heating cable.

3. Coordinate with roofing installer for installation and roof penetrations specified in Division 7 Sections.

Retain subparagraph below for freezer-floor frost-heave prevention.

4. Coordinate with freezer installer for cable placement in subsoil below insulation for freezer specified in Division 11 Section "Foodservice Equipment."

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period.

Verify available warranties for electric heating cable and insert number in subparagraph below.

1. Warranty Period:  [10] [15] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MINERAL-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain this Article for snow melting on pavement.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Chromalox, Inc.; Wiegard Industrial Division; Emerson Electric Company.

2. Delta-Therm Corporation.

3. Easy Heat Inc.

4. Nelson Heat Trace.

5. Pyrotenax; a division of Tyco Thermal Controls.

6. Raychem; a division of Tyco Thermal Controls.

7. Trasor Corp.

8. Watts Radiant Inc.

9. <Insert manufacturer's name.>

D. Heating Element:  Single- or dual-conductor resistor wire.  Terminate with waterproof, factory-assembled nonheating leads with connectors at both ends.

E. Electrical Insulating Mineral:  Magnesium oxide.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover:  Copper/nickel alloy[ and high-density polyethylene outer jacket].

G. Maximum Operating Temperature:  [300 deg F (150 deg C)] <Insert temperature>.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

H. Capacities and Characteristics:

1. Maximum Heat Output:  [6 W/ft. (19.7 W/m)] [7.5 W/ft. (24.6 W/m)] <Insert heat output>.

2. Spacing:  <Insert inches (mm).>

Verify available voltages and heat-output ratings with specified manufacturer.

3. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

4. Phase:  <Insert value.>

5. Hertz:  <Insert value.>

6. Full-Load Amperes:  <Insert value.>

7. Minimum Circuit Ampacity:  <Insert value.>

8. Maximum Overcurrent Protection:  <Insert value.>

2.2 PLASTIC-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain this Article for ceiling and floor radiant heating, freezer-floor frost-heave prevention, and snow and ice melting on pavement.  Some manufacturers limit use of this product to stone, ceramic tile, or concrete floors.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Delta-Therm Corporation.

2. Easy Heat Inc.

3. NUHEAT.

4. Orbit Manufacturing.

5. Pyrotenax; a division of Tyco Thermal Controls.

6. Raychem; a division of Tyco Thermal Controls.

7. WarmlyYours.com Inc.

8. Watts Radiant Inc.

9. <Insert manufacturer's name.>

D. Comply with UL 1673.

E. Heating Element:  Single- or dual-stranded resistor wire.  Terminate with waterproof, factory-assembled nonheating leads with connectors at both ends.

F. Electrical Insulating Jacket:  Minimum 4.0-mil (0.10-mm) Kapton with silicone jacket or Tefzel.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

G. Cable Cover:  Aluminum braid[ and silicone or Hylar outer jacket].

H. Maximum Operating Temperature:  [300 deg F (150 deg C)] <Insert temperature>.

Retain paragraph below for heating cables in factory-fabricated mats.  Indicate length and spacing of cables on Drawings.

I. Heating Cable Mats:  Factory-fabricated cable and fiberglass or plastic mesh with uniform [1-1/2-inch (38-mm)] [3-inch (76-mm)] <Insert dimension> cable spacing, in [18-inch (457-mm)] [36-inch (914-mm)] <Insert dimension> widths.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

J. Capacities and Characteristics:

1. Maximum Heat Output:  [6 W/ft. (19.7 W/m)] [7.5 W/ft. (24.6 W/m)] <Insert heat output>.

Retain subparagraph below for radiant panels.

2. Spacing:  <Insert inches (mm).>

Verify available voltages and heat-output ratings with specified manufacturer.

3. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

4. Phase:  <Insert value.>

5. Hertz:  <Insert value.>

6. Full-Load Amperes:  <Insert value.>

7. Minimum Circuit Ampacity:  <Insert value.>

8. Maximum Overcurrent Protection:  <Insert value.>

2.3 SELF-REGULATING, PARALLEL-RESISTANCE HEATING CABLES

Retain this Article for ceiling and floor radiant heating, freezer-floor frost-heave prevention, and snow and ice melting on pavement.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. BH Thermal Corporation.

2. Chromalox, Inc.; Wiegard Industrial Division; Emerson Electric Company.

3. Delta-Therm Corporation.

4. Easy Heat Inc.

5. Nelson Heat Trace.

6. Pyrotenax; a division of Tyco Thermal Controls.

7. Raychem; a division of Tyco Thermal Controls.

8. Thermon Manufacturing Co.

9. Trasor Corp.

10. <Insert manufacturer's name.>

D. Comply with UL 1673.

E. Heating Element:  Pair of parallel No. [16] [18] AWG, [tinned] [nickel-coated] stranded copper bus wires embedded in crosslinked conductive polymer core, which varies heat output in response to temperature along its length.  Terminate with waterproof, factory-assembled nonheating leads with connectors at one end, and seal the opposite end watertight.  Cable shall be capable of crossing over itself once without overheating.

F. Electrical Insulating Jacket:  Flame-retardant polyolefin.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

G. Cable Cover:  [Tinned-copper] [Stainless-steel] braid[, and polyolefin outer jacket with UV inhibitor].

H. Maximum Operating Temperature (Power On):  [150 deg F (65 deg C)] <Insert temperature>.

Retain first paragraph below for heating cables in factory-fabricated mats.  Indicate length and spacing of cables on Drawings.

I. Heating Cable Mats:  Factory-fabricated cable and fiberglass or plastic mesh with uniform [1-1/2-inch (38-mm)] [3-inch (76-mm)] <Insert dimension> cable spacing, in [18-inch (457-mm)] [36-inch (914-mm)] <Insert dimension> widths.

J. Maximum Operating Temperature:  [300 deg F (150 deg C)] <Insert temperature>.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

K. Capacities and Characteristics:

1. Maximum Heat Output:  [3 W/ft. (9.8 W/m)] [5 W/ft. (16.4 W/m)] [8 W/ft. (26 W/m)] [10 W/ft. (32.8 W/m)] [12 W/ft. (39.4 W/m)] <Insert heat output>.

2. Spacing:  <Insert inches (mm).>

Verify available voltages and heat-output ratings with specified manufacturer.

3. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

4. Phase:  <Insert value.>

5. Hertz:  <Insert value.>

6. Full-Load Amperes:  <Insert value.>

7. Minimum Circuit Ampacity:  <Insert value.>

8. Maximum Overcurrent Protection:  <Insert value.>

2.4 CONTROLS

A. Refer to Division 15 Sections "HVAC Instrumentation and Controls" and "Sequence of Operation."

Retain paragraph above or applicable paragraphs and subparagraphs remaining in this Article for controls provided with electric heating cables.  Revise temperature ranges to suit Project.

Retain paragraph and subparagraphs below for room temperature control of electrical cables in ceilings and floors.

B. Wall-Mounting Thermostats for Ceiling and Floor Heating Cables:

1. Minimum temperature range from [50 to 90 deg F (10 to 32 deg C)] <Insert range>.

2. Manually operated with on-off switch.

Retain paragraph and subparagraphs below to operate electric heating cable for snow melting on pavement.

C. Precipitation and Temperature Sensor for Snow Melting on Pavement:

1. [Microprocessor-based] [Automatic] control with manual on, automatic, and standby/reset switch.

2. Precipitation and temperature sensors shall sense the surface conditions of pavement and shall be programmed to energize the cable as follows:

Retain and edit desired features in first four subparagraphs below.  Verify available features with manufacturer.

a. Temperature Span:  [34 to 44 deg F (1 to 7 deg C)] <Insert range>.

b. Adjustable Delay Off Span:  [30 to 90] <Insert time> minutes.

c. Energize Cables:  Following [two] <Insert time>-minute delay if ambient temperature is below set point and precipitation is detected.

d. De-Energize Cables:  On detection of a dry surface plus time delay.

3. Corrosion-proof and waterproof enclosure suitable for outdoor mounting, for controls and precipitation and temperature sensors.

4. Minimum 30-A contactor to energize cable or close other contactors.

Consider pavement-mounting sensor for snow melting on pavement.

5. Precipitation sensor shall be mounted in pavement.

6. Provide relay with contacts to indicate operational status, on or off, for interface with central HVAC control system workstation.

2.5 ACCESSORIES

A. Cable Installation Accessories:  Fiberglass tape, heat-conductive putty, cable ties, silicone end seals and splice kits, and installation clips all furnished by manufacturer, or as recommended in writing by manufacturer.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine surfaces and substrates to receive electric heating cables for compliance with requirements for installation tolerances and other conditions affecting performance.

1. Ensure surfaces in contact with electric heating cables are free of burrs and sharp protrusions.

2. Ensure surfaces and substrates are level and plumb.

3. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATIONS

Applications in this Article are typical uses for each type of electric heating cable.  Consult manufacturers for other applications and for applications of other electric heating cables.

A. Install the following types of electric heating cable for the applications described:

1. Ceiling Radiant Heating:  [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

2. Floor Radiant Heating:  [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

3. Snow and Ice Melting on Pavement:  [Mineral-insulated, series-resistance] [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

4. Freezer-Floor Frost-Heave Prevention:  [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

3.3 INSTALLATION

A. Install electric heating cable or mats across expansion, construction, and control joints according to manufacturer's written recommendations using cable protection conduit and slack cable to allow movement without damage to cable.

B. Do not energize cables embedded in concrete or plaster until those assemblies are cured.

C. Electric Heating Cable Installation for Ceiling Radiant Heating:  Install heating cable with heat-conductive fill materials such as plaster, to ensure direct contact with finished radiant surfaces.

D. Electric Heating Cable Installation for Floor Radiant Heating:  Install heating cable with heat-conductive fill materials such as concrete, to ensure direct contact with finished radiant surfaces.

E. Electric Heating Cable Installation for Snow and Ice Melting on Pavement:

1. Install heating cable with heat-conductive fill materials such as asphalt or concrete, to ensure direct contact with finished radiant surfaces.

2. Install cables or mats after applying bituminous binder course to lower base; ensure that second bituminous binder course is applied to cables before pouring finish topping.

F. Electric Heating Cable Installation for Freezer-Floor Frost-Heave Prevention:  Install electric heating cable below insulation in subsoil.

G. Set field-adjustable switches and circuit-breaker trip ranges.

H. Protect installed heating cables, including nonheating leads, from damage.

3.4 CONNECTIONS

A. Ground equipment according to Division 16 Section "Grounding and Bonding."

B. Connect wiring according to Division 16 Section "Conductors and Cables."

3.5 FIELD QUALITY CONTROL

A. Testing:  Perform tests after cable installation but before application of coverings such as insulation, wall or ceiling construction, or concrete.

1. Test cables for electrical continuity and insulation integrity before energizing.

2. Test cables to verify rating and power input.  Energize and measure voltage and current simultaneously.

Retain paragraph below for ceiling or floor radiant heating, snow and ice melting on pavement, and freezer-floor frost-heave prevention.

B. Repeat tests for continuity, insulation resistance, and input power after applying finished surface on heating cables.

C. Remove and replace malfunctioning units and retest as specified above.

END OF SECTION 15774

RADIANT-HEATING ELECTRIC CABLES
15774 - 1

