Copyright 2003 AIA
MASTERSPEC
09/03

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15838 - POWER VENTILATORS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Utility set fans.

2. Centrifugal roof ventilators.

3. Axial roof ventilators.

4. Upblast propeller roof exhaust fans.

5. Centrifugal wall ventilators.

6. Ceiling-mounting ventilators.

7. In-line centrifugal fans.

8. Propeller fans.

1.3 PERFORMANCE REQUIREMENTS

Retain one of two paragraphs in this Article.

A. Project Altitude:  Base fan-performance ratings on [actual Project site elevations] [sea level].

B. Operating Limits:  Classify according to AMCA 99.

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, furnished specialties, and accessories for each type of product indicated and include the following:

1. Certified fan performance curves with system operating conditions indicated.

2. Certified fan sound-power ratings.

3. Motor ratings and electrical characteristics, plus motor and electrical accessories.

4. Material thickness and finishes, including color charts.

5. Dampers, including housings, linkages, and operators.

6. Roof curbs.

7. Fan speed controllers.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

2. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

3. Vibration Isolation Base Details:  Detail fabrication, including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails, and base weights.

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plans and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

1. Roof framing and support members relative to duct penetrations.

2. Ceiling suspension assembly members.

3. Size and location of initial access modules for acoustical tile.

4. Ceiling-mounted items including light fixtures, diffusers, grilles, speakers, sprinklers, access panels, and special moldings.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For power ventilators to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

AMCA compliance below is an optional requirement and not necessarily available from all manufacturers.

B. AMCA Compliance:  Products shall comply with performance requirements and shall be licensed to use the AMCA-Certified Ratings Seal.

C. NEMA Compliance:  Motors and electrical accessories shall comply with NEMA standards.

D. UL Standard:  Power ventilators shall comply with UL 705.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver fans as factory-assembled unit, to the extent allowable by shipping limitations, with protective crating and covering.

B. Disassemble and reassemble units, as required for moving to final location, according to manufacturer's written instructions.

C. Lift and support units with manufacturer's designated lifting or supporting points.

1.7 COORDINATION

Edit first paragraph below to delete or add types of construction.

A. Coordinate size and location of structural-steel support members.

B. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Belts:  [One] <Insert number> set(s) for each belt-driven unit.

PART 2 -  PRODUCTS

2.1 UTILITY SET FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Aerovent; a Twin City Fan Company.

2. American Coolair Corp.

3. Ammerman; General Resource Corp.

4. Bayley Fans; a division of Lau Industries, Inc..

5. Breidert Air Products.

6. Carnes Company HVAC.

7. Delhi Industries Inc.

8. Hartzell Fan, Inc.

9. Industrial Air; a division of Lau Industries, Inc.

10. JencoFan; Div. of Breidert Air Products.

11. Loren Cook Company.

12. Madison Manufacturing.

13. New York Blower Company (The).

14. Penn Ventilation.

15. Quietaire Corporation.

16. Trane.

17. <Insert manufacturer's name.>

D. Description:  [Direct] [Belt]-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor and disconnect switch, drive assembly, and accessories.

E. Housing:  Fabricated of[ galvanized] steel with side sheets fastened with a deep lock seam or welded to scroll sheets.

1. Housing Discharge Arrangement:  Adjustable to eight standard positions.

F. Fan Wheels:  Single-width, single inlet; welded to cast-iron or cast-steel hub and spun-steel inlet cone, with hub keyed to shaft.

Retain wheel material and blade style in two subparagraphs below.  Some materials and styles are not available in all sizes.

1. Blade Materials:  [Steel] [Aluminum].

2. Blade Type:  [Backward inclined] [Forward curved] [Airfoil].

Retain subparagraph below for spark-resistant construction and coordinate with materials in first subparagraph above.

3. Spark-Resistant Construction:  AMCA 99, Type [A] [B] [C].

G. Fan Shaft:  Turned, ground, and polished steel; keyed to wheel hub.

H. Shaft Bearings:  Prelubricated and sealed, self-aligning, pillow-block-type ball bearings with ABMA 9, [L50 of 200,000 hours] [L10 of 80,000 hours] <Insert life>.

Delete first paragraph and subparagraphs below if Project includes only direct-driven fans.

I. Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

Retain required service factor in subparagraph below.

1. Service Factor Based on Fan Motor Size:  [1.5] [1.4] [1.3] [1.2].

5-hp limit in first subparagraph below is standard with many manufacturers but is a designer's choice.

2. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert value> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

3. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

4. Belt Guards:  Fabricate of steel for motors mounted on outside of fan cabinet.

J. Accessories:

Retain accessories in subparagraphs below required for Project.

1. Inlet and Outlet:  Flanged.

2. Companion Flanges:  Rolled flanges for duct connections of same material as housing.

3. Backdraft Dampers:  Gravity actuated with counterweight and interlocking aluminum blades with felt edges in steel frame installed on fan discharge.

4. Access Door:  Gasketed door in scroll with latch-type handles.

5. Scroll Dampers:  Single-blade damper installed at fan scroll top with adjustable linkage.

6. Inlet Screens:  Removable wire mesh.

7. Drain Connections:  NPS 3/4 (DN 20) threaded coupling drain connection installed at lowest point of housing.

8. Weather Hoods:  Weather resistant with stamped vents over motor and drive compartment.

9. Discharge Dampers:  Assembly with [parallel] [opposed] blades constructed of two plates formed around and to shaft, channel frame, sealed ball bearings, with blades linked outside of airstream to single control lever of same material as housing.

10. Variable Inlet Vanes:  With blades supported at both ends with two permanently lubricated bearings of same material as housing.  Variable mechanism terminating in single control lever with control shaft for double-width fans.

11. Speed Controller:  Solid-state control to reduce speed from 100 to less than 50 percent.

Retain coatings for special protection applications.  Review manufacturer's data for specific trade names and literature.

K. Coatings:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

If Project has more than one type or configuration of utility set fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

L. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Wheel Type:  [Backward inclined] [Forward curved] [Airfoil].

5. Class:  [I] [II] [III].

6. Drive Arrangement:  <Insert AMCA number.>

7. Brake Horsepower:  <Insert value.>

8. Fan Rpm:  <Insert value.>

9. Outlet Velocity:  <Insert fpm (m/s).>

10. Motor Size:  <Insert value> hp.

11. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

12. Vibration Isolators:

a. Type:  [Spring isolators] [Restrained spring isolators] <Insert type>.

b. Static Deflection:  <Insert inches (mm).>

13. Spark Arrestance Class:  [A] [B] [C].

2.2 CENTRIFUGAL ROOF VENTILATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan Company

3. American Coolair Corp.

4. Ammerman; General Resource Corp.

5. Breidert Air Products.

6. Broan Mfg. Co., Inc.

7. Carnes Company HVAC.

8. Central Blower Co.

9. Dayton Electric Manufacturing Co.; a division of W. W. Grainger, Inc.

10. Delhi Industries Inc.

11. Greenheck.

12. Hartzell Fan, Inc.

13. JencoFan; Div. of Breidert Air Products.

14. Loren Cook Company.

15. NuTone Inc.

16. Penn Ventilation.

17. Quietaire Corporation.

18. <Insert manufacturer's name.>

D. Description:  Direct- or belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor and disconnect switch, drive assembly, curb base, and accessories.

Painted galvanized-steel and fiberglass housings are also available from some manufacturers.

E. Housing:  Removable, [spun-aluminum, dome top and outlet baffle] [extruded-aluminum, rectangular top] [galvanized steel, mushroom-domed top]; square, one-piece, aluminum base with venturi inlet cone.

1. Upblast Units:  Provide spun-aluminum discharge baffle to direct discharge air upward, with rain and snow drains[ and grease collector].

2. Hinged Subbase:  Galvanized-steel hinged arrangement permitting service and maintenance.

F. Fan Wheels:  Aluminum hub and wheel with backward-inclined blades.

G. Belt-Driven Drive Assembly:  Resiliently mounted to housing, with the following features:

1. Fan Shaft:  Turned, ground, and polished steel; keyed to wheel hub.

2. Shaft Bearings:  Permanently lubricated, permanently sealed, self-aligning ball bearings.

3. Pulleys:  Cast-iron, adjustable-pitch motor pulley.

4. Fan and motor isolated from exhaust airstream.

H. Accessories:

Retain accessories in subparagraphs below required for Project.

1. Variable-Speed Controller:  Solid-state control to reduce speed from 100 to less than 50 percent.

2. Disconnect Switch:  Nonfusible type, with thermal-overload protection mounted [inside] [outside] fan housing, factory wired through an internal aluminum conduit.

3. Bird Screens:  Removable, 1/2-inch (13-mm) mesh, aluminum or brass wire.

4. Dampers:  Counterbalanced, parallel-blade, backdraft dampers mounted in curb base; factory set to close when fan stops.

5. Motorized Dampers:  Parallel-blade dampers mounted in curb base with electric actuator; wired to close when fan stops.

Specify roof curbs, if they are site fabricated, in Division 7 Section "Roof Accessories."  Retain paragraph and subparagraphs below to require roof curbs to be provided by fan manufacturer.

I. Roof Curbs:  Galvanized steel; mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid, fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer.  Size as required to suit roof opening and fan base.

In subparagraph below, retain configuration coordinated with roof type specified in Division 7.

1. Configuration:  [Self-flashing without a cant strip, with mounting flange] [Built-in cant and mounting flange] [Built-in raised cant and mounting flange].

Coordinate curb height with roof deck construction and insulation thickness; other heights are available.  16-inch (400-mm) height is for sound curb.

2. Overall Height:  [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Subparagraphs below are optional features.

3. Sound Curb:  Curb with sound-absorbing insulation matrix.

4. Pitch Mounting:  Manufacture curb for roof slope.

5. Metal Liner:  Galvanized steel.

6. Burglar Bars:  [1/2-inch- (13-mm-)] [5/8-inch- (16-mm-)] [3/4-inch- (19-mm-)] thick steel bars welded in place to form 6-inch (150-mm) squares.

7. Mounting Pedestal:  Galvanized steel with removable access panel.

8. Vented Curb:  Unlined with louvered vents in vertical sides.

If Project has more than one type or configuration of centrifugal roof ventilator, delete paragraph and subparagraphs below and schedule ventilators on Drawings.

J. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Hood Material:  <Insert material.>

5. Drive Arrangement:  [Direct] [Belt drive].

6. Brake Horsepower:  <Insert value.>

7. Fan Rpm:  <Insert value.>

8. Tip Speed:  <Insert fpm (m/s).>

9. Sound:  <Insert sone.>

10. Curb Size:  <Insert inches by inches (mm by mm).>

11. Curb Height:  <Insert inches (mm).>

12. Damper:  [Yes] [No].

13. Damper Size:  <Insert inches by inches (mm by mm).>

14. Motor Size:  <Insert value> hp.

15. Motor Fan Rpm:  <Insert value.>

16. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

2.3 AXIAL ROOF VENTILATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan Company.

3. American Coolair Corp.

4. Ammerman; General Resource Corp.

5. Bayley Fans; a division of Lau Industries, Inc.

6. Breidert Air Products.

7. Broan Mfg. Co., Inc.

8. Carnes Company HVAC.

9. FloAire.

10. Greenheck.

11. Hartzell Fan, Inc.

12. Industrial Air;  a division of Lau Industries, Inc.

13. JencoFan; Div. of Breidert Air Products.

14. Loren Cook Company.

15. New York Blower Company (The).

16. Penn Ventilation.

17. Stanley Fans.

18. <Insert manufacturer's name.>

D. Description:  Direct- or belt-driven axial fans consisting of housing, wheel, fan shaft, bearings, motor and disconnect switch, drive assembly, curb base, and accessories.

Characteristics in remaining paragraphs and subparagraphs below are examples of power ventilator specifications.  Galvanized-steel and fiberglass housings are also available from some manufacturers.

E. Housing:  Heavy-gage, removable, spun-aluminum, dome top and outlet baffle; square, one-piece, hinged, aluminum base.

1. Hinged Subbase:  Galvanized-steel hinged arrangement permitting service and maintenance.

F. Fan Wheel:  [Aluminum] [Steel] hub and blades.

G. Belt-Driven Drive Assembly:  Resiliently mounted to housing, with the following features:

1. Fan Shaft:  Turned, ground, and polished steel; keyed to wheel hub.

2. Shaft Bearings:  Permanently lubricated, permanently sealed, self-aligning ball bearings.

3. Pulleys:  Cast-iron, adjustable-pitch motor pulley.

H. Accessories:

Retain accessories in subparagraphs below required for Project.

1. Disconnect Switch:  Nonfusible type, with thermal-overload protection mounted [inside] [outside] fan housing, factory wired through an internal aluminum conduit.

2. Bird Screens:  Removable, 1/2-inch (13-mm) mesh, aluminum or brass wire.

3. Dampers:  Counterbalanced, parallel-blade, backdraft dampers mounted in curb base; factory set to close when fan stops.

4. Motorized Dampers:  Parallel-blade dampers mounted in curb base with electric actuator; wired to close when fan stops.

Specify roof curbs, if they are site fabricated, in Division 7 Section "Roof Accessories."  Retain paragraph and subparagraphs below to require roof curbs to be provided by fan manufacturer.

I. Roof Curbs:  Galvanized steel; mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid, fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer.  Size as required to suit roof opening and fan base.

In subparagraph below, retain configuration coordinated with roof type specified in Division 7.

1. Configuration:  [Self-flashing without a cant strip, with mounting flange] [Built-in cant and mounting flange] [Built-in raised cant and mounting flange].

Coordinate curb height with roof deck construction; other heights are available.  16-inch (400-mm) height is for sound curb.

2. Overall Height:  [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Subparagraphs below are optional features.

3. Sound Curb:  Curb with sound-absorbing insulation matrix.

4. Pitch Mounting:  Manufacture curb for roof slope.

5. Metal Liner:  Galvanized steel.

6. Burglar Bars:  [1/2-inch- (13-mm-)] [5/8-inch- (16-mm-)] [3/4-inch- (19-mm-)] thick steel bars welded in place to form 6-inch (150-mm) squares.

7. Mounting Pedestal:  Galvanized steel with removable access panel.

If Project has more than one type or configuration of axial roof ventilator, delete paragraph and subparagraphs below and schedule ventilators on Drawings.

J. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Hood Material:  <Insert material.>

5. Drive Arrangement:  [Direct] [Belt drive].

6. Brake Horsepower:  <Insert value.>

7. Fan Rpm:  <Insert value.>

8. Tip Speed:  <Insert fpm (m/s).>

9. Sound:  <Insert sone.>

10. Curb Size:  <Insert inches by inches (mm by mm).>

11. Curb Height:  <Insert inches (mm).>

12. Damper:  [Yes] [No].

13. Damper Size:  <Insert inches by inches (mm by mm).>

14. Motor Size:  <Insert value> hp.

15. Motor Fan Rpm:  <Insert value.>

16. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

2.4 UPBLAST PROPELLER ROOF EXHAUST FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan Company.

3. American Coolair Corp.

4. Ammerman; General Resource Corp.

5. Breidert Air Products.

6. Carnes Company HVAC.

7. Cincinnati Fan.

8. Greenheck.

9. Hartzell Fan, Inc.

10. Industrial Air; a division of Lau Industries, Inc.

11. JencoFan; Div. of Breidert Air Products.

12. Loren Cook Company.

13. Madison Manufacturing.

14. New York Blower Company (The).

15. Penn Ventilation.

16. Quietaire Corporation.

17. Stanley Fans.

18. <Insert manufacturer's name.>

D. Description:  Direct- or belt-driven propeller fans consisting of housing, wheel, butterfly-type discharge damper, fan shaft, bearings, motor and disconnect switch, drive assembly, curb base, and accessories.

Wind bands, fan housings, and bases are available in both aluminum and galvanized steel depending on unit size.  Stainless steel is also available for special applications.  Verify materials with manufacturers selected.

E. Wind Band, Fan Housing, and Base:  Reinforced and braced [galvanized steel] [aluminum], containing [galvanized-steel] [aluminum] butterfly dampers and rain trough, motor and drive assembly, and fan wheel.

1. Damper Rods:  Steel with [bronze] [nylon] bearings.

2. Hinged Subbase:  Galvanized-steel hinged arrangement permitting service and maintenance.

Verify wheel-type availability with selected manufacturers.  Aluminum blades below are normally used in large sizes and high-static-pressure applications.

F. Fan Wheel:  Replaceable, [cast] [extruded]-aluminum, airfoil blades fastened to cast-aluminum hub; factory set pitch angle of blades.

Add temperature ratings and other features to drive assembly if these fans are used for smoke exhaust.

G. Belt-Driven Drive Assembly:  Resiliently mounted to housing; weatherproof housing of same material as fan housing with the following features:

1. Fan Shaft:  Turned, ground, and polished steel; keyed to wheel hub.

2. Shaft Bearings:  Prelubricated and sealed, self-aligning, pillow-block-type ball bearings.

3. Pulleys:  Cast-iron, adjustable-pitch motor pulley.

4. Motor Mount:  On outside of fan cabinet, adjustable base for belt tensioning.

Specify roof curbs, if they are site fabricated, in Division 7 Section "Roof Accessories."  Retain paragraph and subparagraphs below to require roof curbs to be provided by fan manufacturer.

H. Roof Curbs:  Galvanized steel; mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid, fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer.  Size as required to suit roof opening and fan base.

In subparagraph below, retain configuration coordinated with roof type specified in Division 7.

1. Configuration:  [Self-flashing without a cant strip, with mounting flange] [Built-in cant and mounting flange] [Built-in raised cant and mounting flange].

Coordinate curb height with roof deck construction; other heights are available.  16-inch (400-mm) height is for sound curb.

2. Overall Height:  [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Subparagraphs below are optional features.

3. Sound Curb:  Curb with sound-absorbing insulation matrix.

4. Pitch Mounting:  Manufacture curb for roof slope.

5. Metal Liner:  Galvanized steel.

6. Burglar Bars:  [1/2-inch- (13-mm-)] [5/8-inch- (16-mm-)] [3/4-inch- (19-mm-)] thick steel bars welded in place to form 6-inch (150-mm) squares.

7. Mounting Pedestal:  Galvanized steel with removable access panel.

If Project has more than one type or configuration of upblast propeller roof exhaust fan, delete paragraph and subparagraphs below and schedule exhaust fans on Drawings.

I. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Drive Arrangement:  [Direct] [Belt drive].

5. Brake Horsepower:  <Insert value.>

6. Fan Rpm:  <Insert value.>

7. Tip Speed:  <Insert fpm (m/s).>

8. Sound:  <Insert sone.>

9. Curb Size:  <Insert inches by inches (mm by mm).>

10. Curb Height:  <Insert inches (mm).>

11. Damper:  [Yes] [No].

12. Damper Size:  <Insert inches by inches (mm by mm).>

13. Motor Size:  <Insert value> hp.

14. Motor Fan Rpm:  <Insert value.>

15. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

2.5 CENTRIFUGAL WALL VENTILATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan Company.

3. American Coolair Corp.

4. Ammerman; General Resource Corp.

5. Breidert Air Products.

6. Broan Mfg. Co., Inc.

7. Carnes Company HVAC.

8. Dayton Electric Manufacturing Co.; a division of W. W. Grainger, Inc.

9. Greenheck.

10. Hartzell Fan, Inc.

11. JencoFan; Div. of Breidert Air Products.

12. Loren Cook Company.

13. NuTone Inc.

14. Penn Ventilation.

15. <Insert manufacturer's name.>

D. Description:  Direct- or belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor and disconnect switch, drive assembly, and accessories.

Galvanized-steel and fiberglass housings are also available from some manufacturers.

E. Housing:  Heavy-gage, removable, spun-aluminum, dome top and outlet baffle; venturi inlet cone.

F. Fan Wheel:  Aluminum hub and wheel with backward-inclined blades.

G. Belt-Driven Drive Assembly:  Resiliently mounted to housing, with the following features:

1. Fan Shaft:  Turned, ground, and polished steel; keyed to wheel hub.

2. Shaft Bearings:  Permanently lubricated, permanently sealed, self-aligning ball bearings.

3. Pulleys:  Cast-iron, adjustable-pitch motor pulley.

4. Fan and motor isolated from exhaust airstream.

H. Accessories:

Retain accessories in subparagraphs below required for Project.

1. Variable-Speed Controller:  Solid-state control to reduce speed from 100 to less than 50 percent.

2. Disconnect Switch:  Nonfusible type, with thermal-overload protection mounted inside fan housing, factory wired through internal aluminum conduit.

3. Bird Screens:  Removable, 1/2-inch (13-mm) mesh, aluminum or brass wire.

4. Wall Grille:  Ring type for flush mounting.

5. Dampers:  Counterbalanced, parallel-blade, backdraft dampers mounted in wall sleeve; factory set to close when fan stops.

6. Motorized Dampers:  Parallel-blade dampers mounted in curb base with electric actuator; wired to close when fan stops.

If Project has more than one type or configuration of centrifugal wall ventilator, delete paragraph and subparagraphs below and schedule ventilators on Drawings.

I. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Drive Arrangement:  [Direct] [Belt drive].

5. Brake Horsepower:  <Insert value.>

6. Fan Rpm:  <Insert value.>

7. Tip Speed:  <Insert fpm (m/s).>

8. Sound:  <Insert sone.>

9. Damper:  [Yes] [No].

10. Damper Size:  <Insert inches by inches (mm by mm).>

11. Motor Size:  <Insert value> hp.

12. Motor Fan Rpm:  <Insert value.>

13. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

2.6 CEILING-MOUNTING VENTILATORS

These units are factory assembled with one or more centrifugal wheels up to 12 inches (300 mm) wide, directly connected to motor, enclosed in housing, with inlet grille and integral backdraft damper; AMCA rated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. American Coolair Corp.

2. Ammerman; General Resource Corp.

3. Breidert Air Products.

4. Broan Mfg. Co., Inc.

5. Carnes Company HVAC.

6. Dayton Electric Manufacturing Co.; a division of W. W. Grainger, Inc.

7. FloAire.

8. Greenheck.

9. JencoFan; Div. of Breidert Air Products.

10. Loren Cook Company.

11. NuTone Inc.

12. Penn Ventilation.

13. <Insert manufacturer's name.>

D. Description:  Centrifugal fans designed for installing in ceiling or wall or for concealed in-line applications.

E. Housing:  Steel, lined with acoustical insulation.

F. Fan Wheel:  Centrifugal wheels directly mounted on motor shaft.  Fan shrouds, motor, and fan wheel shall be removable for service.

Grille designs other than those specified in first paragraph below are available.

G. Grille:  [Plastic] [Stainless steel] [Aluminum] [Painted aluminum], louvered grille with flange on intake and thumbscrew attachment to fan housing.

H. Electrical Requirements:  Junction box for electrical connection on housing and receptacle for motor plug-in.

I. Accessories:

Retain accessories in subparagraphs below required for Project.

1. Variable-Speed Controller:  Solid-state control to reduce speed from 100 to less than 50 percent.

2. Manual Starter Switch:  Single-pole rocker switch assembly with cover and pilot light.

3. Time-Delay Switch:  Assembly with single-pole rocker switch, timer, and cover plate.

4. Motion Sensor:  Motion detector with adjustable shutoff timer.

5. Ceiling Radiation Damper:  Fire-rated assembly with ceramic blanket, stainless-steel springs, and fusible link.

6. Filter:  Washable aluminum to fit between fan and grille.

7. Isolation:  Rubber-in-shear vibration isolators.

8. Manufacturer's standard roof jack or wall cap, and transition fittings.

If Project has more than one type or configuration of ceiling-mounting ventilator, delete paragraph and subparagraphs below and schedule ventilators on Drawings.

J. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Sound:  <Insert sone.>

4. Motor Size:  <Insert value> hp.

5. Motor Rpm:  <Insert value.>

6. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

2.7 IN-LINE CENTRIFUGAL FANS

These fans are both belt and direct driven, usually with spun-aluminum housings, and are used for small ventilation requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. American Coolair Corp.

3. Ammerman; General Resource Corp.

4. Bayley Fans; a division of Lau Industries, Inc.

5. Breidert Air Products.

6. Carnes Company HVAC.

7. FloAire.

8. Greenheck.

9. Hartzell Fan, Inc.

10. JencoFan; Div. of Breidert Air Products.

11. Loren Cook Company.

12. Madison Manufacturing.

13. Penn Ventilation.

14. Quietaire Corporation.

15. <Insert manufacturer's name.>

D. Description:  In-line, [direct] [belt]-driven centrifugal fans consisting of housing, wheel, outlet guide vanes, fan shaft, bearings, motor and disconnect switch, drive assembly, mounting brackets, and accessories.

E. Housing:  Split, spun aluminum with aluminum straightening vanes, inlet and outlet flanges, and support bracket adaptable to floor, side wall, or ceiling mounting.

F. Direct-Driven Units:  Motor mounted in airstream, factory wired to disconnect switch located on outside of fan housing[; with wheel, inlet cone, and motor on swing-out service door].

G. Belt-Driven Units:  Motor mounted on adjustable base, with adjustable sheaves, enclosure around belts within fan housing, and lubricating tubes from fan bearings extended to outside of fan housing.

H. Fan Wheels:  Aluminum, airfoil blades welded to aluminum hub.

I. Accessories:

Retain accessories in subparagraphs below required for Project.

1. Variable-Speed Controller:  Solid-state control to reduce speed from 100 to less than 50 percent.

2. Volume-Control Damper:  Manually operated with quadrant lock, located in fan outlet.

3. Companion Flanges:  For inlet and outlet duct connections.

4. Fan Guards:  1/2- by 1-inch (13- by 25-mm) mesh of galvanized steel in removable frame.  Provide guard for inlet or outlet for units not connected to ductwork.

5. Motor and Drive Cover (Belt Guard):  Epoxy-coated steel.

If Project has more than one type or configuration of in-line centrifugal fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

J. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Wheel Type:  [Backward inclined] [Forward curved] [Airfoil].

5. Class:  [I] [II] [III].

6. Drive Arrangement:  <Insert AMCA number.>

7. Brake Horsepower:  <Insert value.>

8. Fan Rpm:  <Insert value.>

9. Outlet Velocity:  <Insert fpm (m/s).>

10. Motor Size:  <Insert value> hp.

11. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

12. Vibration Isolators:

a. Type:  [Elastomeric hangers] <Insert type>.

b. Static Deflection:  [1 inch (25 mm)] <Insert value>.

13. Spark Arrestance Class:  [A] [B] [C].

2.8 PROPELLER FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan Company.

3. Airmaster Fan Co.

4. American Coolair Corp.

5. Ammerman; General Resource Corp.

6. Bayley Fans; a division of Lau Industries, Inc.

7. Breidert Air Products.

8. Carnes Company HVAC.

9. Chicago Blower Corporation.

10. Cincinnati Fan.

11. Dayton Electric Manufacturing Co.; a division of W. W. Grainger, Inc.

12. Hartzell Fan, Inc.

13. Howden Buffalo Inc.

14. Industrial Air; a division of Lau Industries, Inc.

15. JencoFan; Div. of Breidert Air Products.

16. King Co. (The); King Air Systems.

17. Loren Cook Company.

18. Madison Manufacturing.

19. Moffitt Corporation, Inc.

20. New York Blower Company (The).

21. NuTone Inc.

22. Penn Ventilation.

23. Quietaire Corporation.

24. Stanley Fans.

25. <Insert manufacturer's name.>

D. Description:  Direct- or belt-driven propeller fans consisting of fan blades, hub, housing, orifice ring, motor, drive assembly, and accessories.

E. Housing:  Galvanized-steel sheet with flanged edges and integral orifice ring with baked-enamel finish coat applied after assembly.

F. Steel Fan Wheels:  Formed-steel blades riveted to heavy-gage steel spider bolted to cast-iron hub.

Retain paragraph above or first paragraph below.  Aluminum blades below are normally used in large sizes and in high-static-pressure applications.

G. Fan Wheel:  Replaceable, [cast] [extruded]-aluminum, airfoil blades fastened to cast-aluminum hub; factory set pitch angle of blades.

H. Belt-Driven Drive Assembly:  Resiliently mounted to housing, statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  1.4.

2. Fan Shaft:  Turned, ground, and polished steel; keyed to wheel hub.

3. Shaft Bearings:  Permanently lubricated, permanently sealed, self-aligning ball bearings.

a. Ball-Bearing Rating Life:  ABMA 9, [L10 of 100,000 hours] <Insert life>.

4. Pulleys:  Cast iron with split, tapered bushing; dynamically balanced at factory.

5. Motor Pulleys:  Adjustable pitch for use with motors through [5] <insert value> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

6. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

7. Belt Guards:  Fabricate of steel for motors mounted on outside of fan cabinet.

I. Accessories:

Retain accessories in subparagraphs below required for Project.

1. Gravity Shutters:  Aluminum blades in aluminum frame; interlocked blades with nylon bearings.

2. Motor-Side Back Guard:  Galvanized steel, complying with OSHA specifications, removable for maintenance.

3. Wall Sleeve:  Galvanized steel to match fan and accessory size.

4. Weathershield Hood:  Galvanized steel to match fan and accessory size.

5. Weathershield Front Guard:  Galvanized steel with expanded metal screen.

6. Variable-Speed Controller:  Solid-state control to reduce speed from 100 to less than 50 percent.

7. Disconnect Switch:  Nonfusible type, with thermal-overload protection mounted inside fan housing, factory wired through an internal aluminum conduit.

If Project has more than one type or configuration of propeller fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

J. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Wheel Type:  [Backward inclined] [Forward curved] [Airfoil].

5. Class:  [I] [II] [III].

6. Drive Arrangement:  <Insert AMCA number.>

7. Brake Horsepower:  <Insert value.>

8. Fan Rpm:  <Insert value.>

9. Outlet Velocity:  <Insert fpm (m/s).>

10. Motor Size:  <Insert value> hp.

11. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

12. Vibration Isolators:

a. Type:  [Elastomeric hangers] [Spring isolators] [Restrained spring isolators] <Insert type>.

b. Static Deflection:  [1 inch (25 mm)] <Insert value>.

13. Spark Arrestance Class:  [A] [B] [C].

2.9 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add paragraphs below to suit Project.

A. Comply with requirements in Division 15 Section "Motors."

Retain paragraph below if enclosure type must be other than "open dripproof."

B. Enclosure Type:  Totally enclosed, fan cooled.

2.10 SOURCE QUALITY CONTROL

Sound-power rating information may only be available from manufacturers on request.  Refer to discussion on sound and vibration control in the Evaluations.

A. Sound-Power Level Ratings:  Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data."  Factory test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans."  Label fans with the AMCA-Certified Ratings Seal.

B. Fan Performance Ratings:  Establish flow rate, pressure, power, air density, speed of rotation, and efficiency by factory tests and ratings according to AMCA 210, "Laboratory Methods of Testing Fans for Rating."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install power ventilators level and plumb.

Retain and edit first three paragraphs and associated subparagraph below for floor-mounting units; delete if vibration and seismic controls are specified in Part 2 "Capacities and Characteristics" paragraphs or are indicated on Drawings.  If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Division 15 Section "Mechanical Vibration and Seismic Controls" and identify its required static deflection.

B. Support units using [elastomeric mounts] [restrained elastomeric mounts] [spring isolators] [restrained spring isolators] <Insert device> having a static deflection of [1 inch (25 mm)] <Insert deflection>.  Vibration- and seismic-control devices are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

1. Secure vibration and seismic controls to concrete bases using anchor bolts cast in concrete base.

C. Install floor-mounting units on concrete bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Section "Cast-in-Place Concrete."

Retain paragraph above for projects not in seismic areas; retain first paragraph below for projects in seismic areas.

D. Install floor-mounting units on concrete bases designed to withstand, without damage to equipment, the seismic force required by code.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Section "Cast-in-Place Concrete."

E. Secure roof-mounting fans to roof curbs with cadmium-plated hardware.  Refer to Division 7 Section "Roof Accessories" for installation of roof curbs.

F. Ceiling Units:  Suspend units from structure; use steel wire or metal straps.

Retain and edit first paragraph below for suspended units; delete if vibration and seismic controls are specified in Part 2 "Capacities and Characteristics" paragraphs or are indicated on Drawings.  If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Division 15 Section "Mechanical Vibration and Seismic Controls" and identify its required static deflection.

G. Support suspended units from structure using threaded steel rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stops] <Insert device> having a static deflection of [1 inch (25 mm)] <Insert deflection>.  Vibration-control devices are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

H. Install units with clearances for service and maintenance.

I. Label units according to requirements specified in Division 15 Section "Mechanical Identification."

3.2 CONNECTIONS

Coordinate duct installation and specialty arrangements with schematics on Drawings and with requirements specified in duct systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Duct installation and connection requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of ducts and duct accessories.  Make final duct connections with flexible connectors.  Flexible connectors are specified in Division 15 Section "Duct Accessories."

B. Install ducts adjacent to power ventilators to allow service and maintenance.

C. Ground equipment according to Division 16 Section "Grounding and Bonding."

D. Connect wiring according to Division 16 Section "Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. Verify that shipping, blocking, and bracing are removed.

2. Verify that unit is secure on mountings and supporting devices and that connections to ducts and electrical components are complete.  Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

3. Verify that cleaning and adjusting are complete.

4. Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation.  Reconnect fan drive system, align and adjust belts, and install belt guards.

5. Adjust belt tension.

6. Adjust damper linkages for proper damper operation.

7. Verify lubrication for bearings and other moving parts.

8. Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

9. Disable automatic temperature-control operators, energize motor and adjust fan to indicated rpm, and measure and record motor voltage and amperage.

10. Shut unit down and reconnect automatic temperature-control operators.

11. Remove and replace malfunctioning units and retest as specified above.

B. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3.4 ADJUSTING

A. Adjust damper linkages for proper damper operation.

B. Adjust belt tension.

C. Refer to Division 15 Section "Testing, Adjusting, and Balancing" for testing, adjusting, and balancing procedures.

D. Replace fan and motor pulleys as required to achieve design airflow.

E. Lubricate bearings.

END OF SECTION 15838

POWER VENTILATORS
15838 - 1

