Copyright 2002 AIA
MASTERSPEC
09/02

Copyright 2002, The American Institute of Architects (AIA)

SECTION 15861 - AIR FILTERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes factory-fabricated air-filter devices and media used to remove particulate matter from air for HVAC applications.

1.3 DEFINITIONS

Retain acronyms that remain after this Section has been edited.

A. DOP:  Dioctyl phthalate or bis-(2-ethylhexyl) phthalate.

B. HEPA:  High-efficiency particulate air.

C. ULPA:  Ultra low penetration air.

1.4 SUBMITTALS

A. Product Data:  Include dimensions; operating characteristics; required clearances and access; rated flow capacity, including initial and final pressure drop at rated airflow; efficiency and test method; fire classification; furnished specialties; and accessories for each model indicated.

B. Shop Drawings:  Include plans, elevations, sections, and details to illustrate component assemblies and attachments.

1. Show filter rack assembly, dimensions, materials, and methods of assembly of components.

2. Include setting drawings, templates, and requirements for installing anchor bolts and anchorages.

Retain subparagraph below if equipment includes wiring.

3. Wiring Diagrams:  Power, signal, and control wiring.

C. Operation and Maintenance Data:  For each type of filter and rack to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

Retain first paragraph below to allow Drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of air filters and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Verify use of ARI 850.  ARI 850 does not apply to HEPA filters but includes ozone-concentration testing for electronic air cleaners.

C. Comply with ARI 850.

D. Comply with [ASHRAE 52.1] [and] [ASHRAE 52.2] for method of testing and rating air-filter units.

E. Comply with NFPA 70 for installing electrical components.

F. Comply with NFPA 90A and NFPA 90B.

1.6 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Provide one complete set of filters for each filter bank.  If system includes prefilters, provide only prefilters.

2. Provide one container of red oil for inclined manometer filter gage.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Air Filters, Electrostatic Air Cleaners, and Filter-Holding Systems:

a. AAF International.

b. Filtration Group.

c. Airguard Industries, Inc.

d. Barnebey & Sutcliffe Corp.

e. Columbus Industries, Inc.

f. CRS Industries, Inc.; CosaTron Div.

g. D Mark Inc.

h. Farr Co.

i. Flame Gard, Inc.

j. Flanders/CSC Corp.

k. Flanders Filters, Inc.

l. General Filters Inc.

m. International Air Filtration Corporation.

n. Koch Filter Corporation.

o. LakeAir International, Inc.

p. NiCon Filter Corp.; Continental Air Filter Div.

q. Purafil, Inc.

r. Research Products Corp.

s. <Insert manufacturer's name.>

2. Filter Gages:

a. Airguard Industries, Inc.

b. Dwyer Instruments, Inc.

c. <Insert manufacturer's name.>

2.2 DISPOSABLE PANEL FILTERS

A. Description:  Factory-fabricated, viscous-coated, flat-panel-type, disposable air filters with holding frames.

B. Media:  Interlaced glass fibers sprayed with nonflammable adhesive[ and anti-microbial agent].

C. Frame:  [Cardboard frame with perforated metal retainer] [Galvanized steel with metal grid on outlet side, steel rod grid on inlet side, hinged, and with pull and retaining handles].

D. Duct-Mounting Frames:  Welded, galvanized steel with gaskets and fasteners and suitable for bolting together into built-up filter banks.

2.3 EXTENDED-SURFACE, DISPOSABLE PANEL FILTERS

A. Description:  Factory-fabricated, dry, extended-surface filters with holding frames.

B. Media:  Fibrous material formed into deep-V-shaped pleats[ with anti-microbial agent] and held by self-supporting wire grid.

C. Media and Media-Grid Frame:  [Nonflammable cardboard] [Galvanized steel] [Fire-retardant, 3/4-inch (19-mm) particleboard with gaskets].

D. Duct-Mounting Frames:  Welded, galvanized steel with gaskets and fasteners, and suitable for bolting together into built-up filter banks.

2.4 EXTENDED-SURFACE, NONSUPPORTED-MEDIA FILTERS

A. Description:  Factory-fabricated, dry, extended-surface, self-supporting filters with holding frames.

B. Media:  Fibrous material constructed so individual pleats are maintained in tapered form by flexible internal supports under rated-airflow conditions[ and anti-microbial agent].

C. Filter-Media Frame:  [Galvanized steel] [Hard polyurethane foam].

D. Duct-Mounting Frames:  Welded galvanized steel with gaskets and fasteners, and suitable for bolting together into built-up filter banks.

2.5 AUTOMATIC ROLL FILTERS

A. Description:  Factory-fabricated, automatic, motor-driven, roll-type filter with holding casing.

1. Arrangement:  [Horizontal] [Vertical].

B. Media:  Compressed and rolled, fibrous-glass material viscous-coated[, and with anti-microbial agent].

C. Holding Frame:  Galvanized steel with enclosed, clean media roll arranged to allow upstream replacement of filter media.

1. Auxiliary Frame:  Locate on downstream side of unit with [downstream] [side] access.

2. Final Filter:  Extended-surface, [retained-media] [nonsupported-media] [HEPA] filters.

D. Control and Drive:  Electric, gear-reducer, motor-driven, feed-control mechanism equipped with manual media advance and runout switches for stopping media movement of filter bank and operating remote warning signal lights.

1. Manual Control:  Manual switch to advance media and wired to override automatic controls.

2. Automatic Control:  Prewired control package to advance media [when filter resistance exceeds preselected high limit] [after preselected operating time].

2.6 ACTIVATED-CARBON PANEL FILTERS

A. Description:  Factory-fabricated unit with activated-carbon media.

Retain one of first two paragraphs below.

B. Media:  Flat-panel, multilayer filter with inlet layer of polyester fibers, layer of activated-carbon granules bonded to fibers, layer of polyurethane foam, and housed in cardboard frame.

C. Media:  Pleated, multilayer filter with inlet layer of cotton and synthetic fibers and layer of activated-carbon granules bonded to synthetic fibers, formed into deep-V-shaped pleats and held by self-wire grid, and housed in nonflammable cardboard frame.

D. Duct-Mounting Frames:  Welded galvanized steel with polyurethane gaskets and fasteners, capable of holding media and media frame in place and suitable for bolting together into built-up filter banks.

2.7 ACTIVATED-CARBON FILTERS

A. Description:  Factory-fabricated unit with activated-carbon trays in deep-V arrangement with disposable panel prefilter.

B. Media:  Activated carbon and mounted in removable carbon-cell trays of epoxy-coated steel.

1. Activated-Carbon Capacity:  [12 lb (5.4 kg) of activated carbon per 500 cfm (236 L/s)] [8.8 lb (4.0 kg) of activated carbon per 2000 cfm (944 L/s)] of airflow.

C. Housing:  0.064-inch- (1.6-mm-) thick, galvanized steel, for side servicing through gasketed access doors on both sides.  Equip housings with metal slide channel tracks to hold activated-carbon trays.

2.8 HIGH-EFFICIENCY FILTERS

A. Description:  Factory-fabricated [95 percent DOP] [HEPA] [ULPA] filters with holding casing.

B. Media:  UL 586, fibrous glass, constructed of continuous sheets with closely spaced pleats with [aluminum separators] [vinyl-coated aluminum separators] [separators of ribbons of filter media].

C. Frame Material:  [3/4-inch- (19-mm-) thick, fire-retardant plywood] [3/4-inch- (19-mm-) thick, fire-retardant particleboard] [3/4-inch- (19-mm-) thick plywood] [3/4-inch- (19-mm-) thick particleboard] [Galvanized steel] [Aluminized steel] [Cadmium-plated steel] [Stainless steel] [Aluminum].

D. Media to Frame Side Bond:  [Polyurethane foam] [Silicone] [Neoprene adhesive] [Fiberglass-mat packing] [Thermosetting sealant] [Knife-edge in fluid-filled channel].

E. Face Gasket:  [Neoprene expanded rubber] [Ceramic fiber] [Silicone].

F. Duct-Mounting Frames:  Construct downstream corners of holding device with cushion pads to protect media.  Provide bolted filter-sealing mechanism to mount and continuously seal each individual filter.

2.9 ELECTRONIC AIR CLEANERS

A. Description:  Galvanized-steel assembly containing electronic agglomerator and prefilters.

B. Media:  Independently supported and nested aluminum collection cells.

1. Ionizing Section:  Alternately spaced grounded struts and charged ionizing wires.

2. Collecting Section:  Alternately grounded and charged plates, with insulators located out of airstream.

C. Power Pack:  Self-contained, prewired rectifying unit to convert 120-V, single-phase, 60-Hz ac power to approximately 12,000-V dc for ionizer and 6000-V dc for collector; include overload protection, on-off switch, and pilot light showing operating status.

D. Safety Accessories:  Manual-reset safety switches and warning lights for filter plenum access doors, signal lights and safety switching upstream and downstream from unit within duct, and enameled high-voltage warning signs.

2.10 FRONT- AND REAR-ACCESS FILTER FRAMES

This Article is an example of filter-holding frames for front and rear loading.  Edit to suit Project or add other types.

A. Framing System:  Aluminum framing members with access for either upstream (front) or downstream (rear) filter servicing, cut to size and prepunched for assembly into modules.  Vertically support filters prevent deflection of horizontal members without interfering with either filter installation or operation.

B. Prefilters:  Incorporate a separate track, removable from front or back.

C. Sealing:  Factory-installed, positive-sealing device for each row of filters to ensure seal between gasketed filter elements to prevent bypass of unfiltered air.

2.11 SIDE-SERVICE HOUSINGS

This Article is an example of filter-holding frames for side loading.  Edit to suit Project or add other types.

A. Description:  Factory-assembled, side-service housings, constructed of galvanized steel, with flanges to connect to duct system.

B. Prefilters:  Integral tracks to accommodate 2-inch (50-mm) disposable or washable filters.

C. Access Doors:  Continuous gaskets on perimeter and positive-locking devices.  Arrange so filter cartridges can be loaded from either access door.[  Provide ribbed bagging rim behind access door and PVC bags, for bag-in, bag-out arrangement.]

D. Sealing:  Incorporate positive-sealing gasket material on channels to seal top and bottom of filter cartridge frames to prevent bypass of unfiltered air.

2.12 FILTER GAGES

A. Description:  Diaphragm type with dial and pointer in metal case, vent valves, black figures on white background, and front recalibration adjustment.

1. Diameter:  [4-1/2 inches (115 mm)] [2 inches (50 mm)].

2. Range:  [0- to 0.5-inch wg (0 to 125 Pa)] [0- to 1.0-inch wg (0 to 250 Pa)] [0- to 2.0-inch wg (0 to 500 Pa)] [0- to 3.0-inch wg (0 to 750 Pa)] [0- to 4.0-inch wg (0 to 1000 Pa)].

B. Manometer-Type Filter Gage:  Molded plastic with epoxy-coated aluminum scale, logarithmic-curve tube gage with integral leveling gage, graduated to read from 0- to 3.0-inch wg (0 to 750 Pa), and accurate within 3 percent of full scale range.

C. Accessories:  Static-pressure tips, tubing, gage connections, and mounting bracket.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install filter frames according to manufacturer's written instructions.

B. Position each filter unit with clearance for normal service and maintenance.  Anchor filter holding frames to substrate.

C. Install filters in position to prevent passage of unfiltered air.

D. Install filter gage for each filter bank.

E. Install filter gage static-pressure tips upstream and downstream from filters to measure pressure drop through filter.  Mount filter gages on outside of filter housing or filter plenum in an accessible position.  Adjust and level inclined gages.

F. Coordinate filter installations with duct and air-handling unit installations.

G. Electrical wiring and connections are specified in Division 16 Sections.

H. Ground equipment according to Division 16 Section "Grounding and Bonding."

3.2 FIELD QUALITY CONTROL

Retain paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components, filter and filter-frame installation, and electrical wiring[, and to assist in field testing].  Report results in writing.

B. Operate automatic roll filters to demonstrate compliance with requirements.  Test for leakage of unfiltered air while system is operating.  Correct malfunctioning units, then retest to demonstrate compliance.  Remove and replace units that cannot be corrected with new units and retest.

C. HEPA Filters:  Pressurize housing to a minimum of 3.0-inch wg (750 Pa) or to designed operating pressure, whichever is higher; and test housing joints, door seals, and sealing edges of filter with soapy water to check for air leaks.

Retain paragraph below in critical applications, per ASME N510.

D. HEPA Filters:  Pressurize housing to a minimum of 3.0-inch wg (750 Pa) or to designed operating pressure, whichever is higher; and test housing joints, door seals, and sealing edges of filter for air leaks according to ASME N510 pressure-decay method.

3.3 CLEANING

A. After completing system installation and testing, adjusting, and balancing air-handling and air-distribution systems, clean filter housings and install new filter media.

END OF SECTION 15861

AIR FILTERS
15861 - 8

