Copyright 2003 AIA
MASTERSPEC
12/03

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16231 - PACKAGED ENGINE GENERATOR
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged engine-generator sets for [emergency] [standby] power supply with the following features:

Adjust list below to suit Project.

1. [Gas] [Diesel] engine.

2. [Unit-mounted] [Remote-mounting] cooling system.

3. [Unit-mounted] [Remote-mounting] control and monitoring.

4. Performance requirements for sensitive loads.

5. Load banks.

6. Outdoor enclosure.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 16 Section "Transfer Switches" for transfer switches including sensors and relays to initiate automatic-starting and -stopping signals for engine-generator sets.

1.3 DEFINITIONS

Retain abbreviation and terms that remain after this Section has been edited.

A. Operational Bandwidth:  The total variation from the lowest to highest value of a parameter over the range of conditions indicated, expressed as a percentage of the nominal value of the parameter.

B. LP:  Liquid petroleum.

1.4 SUBMITTALS

A. Product Data:  For each type of packaged engine generator indicated.  Include rated capacities, operating characteristics, and furnished specialties and accessories.  In addition, include the following:

1. Thermal damage curve for generator.

2. Time-current characteristic curves for generator protective device.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Dimensioned outline plan and elevation drawings of engine-generator set and other components specified.

2. Design Calculations:  Signed and sealed by a qualified professional engineer.  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

3. Vibration Isolation Base Details:  Signed and sealed by a qualified professional engineer.  Detail fabrication, including anchorages and attachments to structure and to supported equipment.  Include base weights.

4. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Electrical Supports and Seismic Restraints."

Retain option below for diesel-engine generators with day tank.

C. Manufacturer Seismic Qualification Certification:  Submit certification that [day tank, ]engine-generator set, batteries, battery racks, accessories, and components will withstand seismic forces defined in Division 16 Section "Electrical Supports and Seismic Restraints."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For [installer] [manufacturer] [and] [testing agency].

Coordinate paragraph below with Part 2 "Source Quality Control" Article.

E. Source quality-control test reports.

See Editing Instruction No. 3 in the Evaluations for discussion about prototype-unit testing.

1. Certified summary of prototype-unit test report.

2. Certified Test Reports:  For components and accessories that are equivalent, but not identical, to those tested on prototype unit.

Retain first subparagraph below for generator sets specified to meet performance requirements and for generator sets serving sensitive loads.

3. Certified Summary of Performance Tests:  Certify compliance with specified requirement to meet performance criteria for sensitive loads.

4. Report of factory test on units to be shipped for this Project, showing evidence of compliance with specified requirements.

5. Report of sound generation.

Retain first subparagraph below if required by authorities having jurisdiction.  See "Application Considerations" Article in the Evaluations for more information.

6. Report of exhaust emissions showing compliance with applicable regulations.

7. Certified Torsional Vibration Compatibility:  Comply with NFPA 110.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For packaged engine generators to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1 Section "Operation and Maintenance Data," include the following:

1. List of tools and replacement items recommended to be stored at Project for ready access.  Include part and drawing numbers, current unit prices, and source of supply.

H. Warranty:  Special warranty specified in this Section.

1.5 QUALITY ASSURANCE

A. Installer Qualifications:  Manufacturer's authorized representative who is trained and approved for installation of units required for this Project.

Revise subparagraph below to suit Project location.

1. Maintenance Proximity:  Not more than [four] <Insert number> hours' normal travel time from Installer's place of business to Project site.

Retain subparagraph below if Contractor is required to assume responsibility for engineering.

2. Engineering Responsibility:  Preparation of data for vibration isolators and seismic restraints of engine skid mounts, including Shop Drawings, based on testing and engineering analysis of manufacturer's standard units in assemblies similar to those indicated for this Project.

B. Manufacturer Qualifications:  A qualified manufacturer.  Maintain, within [200 miles (321 km)] <Insert number of miles (kilometers)> of Project site, a service center capable of providing training, parts, and emergency maintenance repairs.

Retain first paragraph below if Contractor selects testing agency or Contractor is required to provide services of an independent testing agency in Part 3 "Field Quality Control" Article.  Qualification requirements supplement those specified in Division 1 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

C. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL), and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

D. Source Limitations:  Obtain packaged generator sets and auxiliary components through one source from a single manufacturer.

E. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

F. Comply with ASME B15.1.

G. Comply with NFPA 37.

H. Comply with NFPA 70.

Retain paragraph below for healthcare facilities.

I. Comply with NFPA 99.

Retain first paragraph below if generator is automatically started.  See Editing Instruction No. 4 in the Evaluations.

J. Comply with NFPA 110 requirements for Level [1] [2] emergency power supply system.

K. Comply with UL 2200.

Retain paragraph below for state or local compliance.

L. Engine Exhaust Emissions:  Comply with applicable state and local government requirements.

Retain paragraph below for installations with critical noise-abatement requirements, particularly outdoor generator sets.  Coordinate with noise-reduction features in the design, including those relating to cooling-air intake and discharge arrangement and muffler specification and its location and orientation as shown on Drawings.

M. Noise Emission:  Comply with [applicable state and local government requirements] <Insert Project criteria> for maximum noise level at [adjacent property boundaries] <Insert critical locations> due to sound emitted by generator set including engine, engine exhaust, engine cooling-air intake and discharge, and other components of installation.

1.6 PROJECT CONDITIONS

Delete first paragraph and subparagraphs below if no interruption of existing electrical service is required.

A. Interruption of Existing Electrical Service:  Do not interrupt electrical service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electrical service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of electrical service.

2. Do not proceed with interruption of electrical service without [Architect's] [Construction Manager's] [Owner's] written permission.

B. Environmental Conditions:  Engine-generator system shall withstand the following environmental conditions without mechanical or electrical damage or degradation of performance capability:

Retain first option in subparagraph below if generator-set start time must be within NFPA 110 limits.  This temperature range usually implies installation indoors in heated space.  Coordinate with Drawings.

1. Ambient Temperature:  [5 to 40 deg C] [Minus 15 to plus 40 deg C].

Delete first subparagraph below for outdoor units.

2. Relative Humidity:  0 to 95 percent.

3. Altitude:  Sea level to [1000 feet (300 m)] <Insert altitude>.

If unusual service conditions for equipment exist and cannot be eliminated, specify them in paragraph below.  See Editing Instruction No. 5 in the Evaluations.

C. Unusual Service Conditions:  Engine-generator equipment and installation are required to operate under the following conditions:

Subparagraph below is an example only.  Revise to list unusual conditions.

1. [High salt-dust content in the air due to sea-spray evaporation] <Insert unusual condition>.

1.7 COORDINATION

A. Coordinate size and location of concrete bases for package engine generators[ and remote radiators mounted on grade].  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

Retain paragraph below for remote radiators located on roof.

B. Coordinate size and location of roof curbs, equipment supports, and roof penetrations for remote radiators.  These items are specified in Division 7 Section "Roof Accessories."

1.8 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of packaged engine generators and associated auxiliary components that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period:  <Insert number> years from date of Substantial Completion.

1.9 MAINTENANCE SERVICE

Retain this Article for critical installations and consider including a provision for submitting a continuing maintenance agreement proposal.  Revise starting date if required.  Obtain a copy of maintenance agreement before retaining or editing below.  Maintenance contracts may not be allowed for publicly funded projects.

A. Initial Maintenance Service:  Beginning at Substantial Completion, provide [12] <Insert number> months' full maintenance by skilled employees of manufacturer's designated service organization.  Include quarterly exercising to check for proper starting, load transfer, and running under load.  Include routine preventive maintenance as recommended by manufacturer and adjusting as required for proper operation.  Provide parts and supplies same as those used in the manufacture and installation of original equipment.

1.10 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Quantities below are examples only.

1. Fuses:  One for every 10 of each type and rating, but no fewer than one of each.

2. Indicator Lamps:  Two for every six of each type used, but no fewer than two of each.

3. Filters:  One set each of lubricating oil, fuel, and combustion-air filters.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers in this Article.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Caterpillar; Engine Div.

2. Generac Power Systems, Inc.

3. Kohler Co.; Generator Division.

4. Magnetek, Inc.

5. Onan/Cummins Power Generation; Industrial Business Group.

6. Spectrum Detroit Diesel.

7. <Insert manufacturer's name.>

2.2 ENGINE-GENERATOR SET

A. Factory-assembled and -tested, engine-generator set.

B. Mounting Frame:  Maintain alignment of mounted components without depending on concrete foundation; and have lifting attachments.

Retain subparagraph below if rigging is required.

1. Rigging Diagram:  Inscribed on metal plate permanently attached to mounting frame to indicate location and lifting capacity of each lifting attachment and generator-set center of gravity.

Coordinate paragraph and subparagraphs below with prototype test requirements in Part 1 "Submittals" Article and in Part 2 "Source Quality Control" Article.

C. Capacities and Characteristics:

1. Power Output Ratings:  Nominal ratings as indicated[, with capacity as required to operate as a unit as evidenced by records of prototype testing].

2. Output Connections:  Three-phase, [three] [four] wire.

3. Nameplates:  For each major system component to identify manufacturer's name and address, and model and serial number of component.

Retain paragraph and subparagraphs below for loads involving little or no sensitive electronic equipment, adjustable frequency drives, or uninterruptible power supply systems.  See Evaluations.

D. Generator-Set Performance:

1. Steady-State Voltage Operational Bandwidth:  3 percent of rated output voltage from no load to full load.

2. Transient Voltage Performance:  Not more than 20 percent variation for 50 percent step-load increase or decrease.  Voltage shall recover and remain within the steady-state operating band within three seconds.

3. Steady-State Frequency Operational Bandwidth:  0.5 percent of rated frequency from no load to full load.

4. Steady-State Frequency Stability:  When system is operating at any constant load within the rated load, there shall be no random speed variations outside the steady-state operational band and no hunting or surging of speed.

5. Transient Frequency Performance:  Less than 5 percent variation for 50 percent step-load increase or decrease.  Frequency shall recover and remain within the steady-state operating band within five seconds.

6. Output Waveform:  At no load, harmonic content measured line to line or line to neutral shall not exceed 5 percent total and 3 percent for single harmonics.  Telephone influence factor, determined according to NEMA MG 1, shall not exceed 50 percent.

7. Sustained Short-Circuit Current:  For a 3-phase, bolted short circuit at system output terminals, system shall supply a minimum of 250 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to generator system components.

Below requires 10-second maximum start time under specific conditions and includes startup only, not load assumption.

8. Start Time:  Comply with NFPA 110, Type 10, system requirements.

Retain paragraph and subparagraphs below for loads involving sensitive electronic equipment, significant nonlinear load elements, or uninterruptible power supply systems.  Coordinate with "Governor" Paragraph in "Engine" Article and with "Generator, Exciter, and Voltage Regulator" Article.  See Evaluations.

E. Generator-Set Performance for Sensitive Loads:

1. Oversizing generator compared with the rated power output of the engine is permissible to meet specified performance.

a. Nameplate Data for Oversized Generator:  Show ratings required by the Contract Documents rather than ratings that would normally be applied to generator size installed.

2. Steady-State Voltage Operational Bandwidth:  1 percent of rated output voltage from no load to full load.

Some manufacturers may be required to provide an oversized engine-generator set in order to meet parameters in first subparagraph below.  This could impact space, noise, ventilation, cooling, and other parameters.  Verify performance of products if specific manufacturers are listed at the beginning of Part 2.  Edit requirements below to suit actual Project load characteristics.

3. Transient Voltage Performance:  Not more than 10 percent variation for 50 percent step-load increase or decrease.  Voltage shall recover and remain within the steady-state operating band within 0.5 second.

4. Steady-State Frequency Operational Bandwidth:  Plus or minus 0.25 percent of rated frequency from no load to full load.

5. Steady-State Frequency Stability:  When system is operating at any constant load within the rated load, there shall be no random speed variations outside the steady-state operational band and no hunting or surging of speed.

6. Transient Frequency Performance:  Less than 2-Hz variation for 50 percent step-load increase or decrease.  Frequency shall recover and remain within the steady-state operating band within three seconds.

7. Output Waveform:  At no load, harmonic content measured line to neutral shall not exceed 2 percent total with no slot ripple.  Telephone influence factor, determined according to NEMA MG 1, shall not exceed 50 percent.

8. Sustained Short-Circuit Current:  For a 3-phase, bolted short circuit at system output terminals, system shall supply a minimum of 300 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to winding insulation or other generator system components.

9. Excitation System:  Performance shall be unaffected by voltage distortion caused by nonlinear load.

Permanent magnet excitation in subparagraph below is a standard feature of some manufacturers' engine-generator sets larger than 200 kW.

a. Provide permanent magnet excitation for power source to voltage regulator.

Retain subparagraph below if required start time is 10 seconds or less.

10. Start Time:  Comply with NFPA 110, Type 10, system requirements.

2.3 ENGINE

Depending on NFPA 110 class and local codes, LP-gas standby may not be required for natural gas-fueled systems.  Verify requirements with authorities having jurisdiction.

A. Fuel:  [Fuel oil, Grade DF-2] [Natural gas with automatic LP-gas standby] [Natural gas].

1. <Insert specific fuel grade requirements.>

B. Rated Engine Speed:  1800 rpm.

C. Maximum Piston Speed for Four-Cycle Engines:  2250 fpm (11.4 m/s).

D. Lubrication System:  The following items are mounted on engine or skid:

1. Filter and Strainer:  Rated to remove 90 percent of particles 5 micrometers and smaller while passing full flow.

2. Thermostatic Control Valve:  Control flow in system to maintain optimum oil temperature.  Unit shall be capable of full flow and is designed to be fail-safe.

3. Crankcase Drain:  Arranged for complete gravity drainage to an easily removable container with no disassembly and without use of pumps, siphons, special tools, or appliances.

E. Engine Fuel System:

Retain first two subparagraphs below for diesel-fueled engine; retain third subparagraph and associated subparagraphs for natural-gas- and LP-gas-fueled engine.

1. Main Fuel Pump:  Mounted on engine.  Pump ensures adequate primary fuel flow under starting and load conditions.

2. Relief-Bypass Valve:  Automatically regulates pressure in fuel line and returns excess fuel to source.

3. Dual Natural Gas with LP-Gas Backup (Vapor-Withdrawal) System:

a. Carburetor.

b. Secondary Gas Regulators:  One for each fuel type.

c. Fuel-Shutoff Solenoid Valves:  One for each fuel source.

d. Flexible Fuel Connectors:  One for each fuel source.

Retain paragraph below where required by NFPA 110, which prescribes engine water-jacket temperature requirements.  Coordinate with Drawings for electrical supply.

F. Coolant Jacket Heater:  Electric-immersion type, factory installed in coolant jacket system.  Comply with NFPA 110 requirements for Level 1 equipment for heater capacity.

Retain option in paragraph below that is consistent with steady-state tolerances and transient frequency tolerances of loads supplied.  Retain second option for systems with sensitive loads.  Coordinate with "Engine-Generator Set" Article.

G. Governor:  [Mechanical] [Adjustable isochronous, with speed sensing].

Retain one of two paragraphs and associated subparagraphs below.  Coordinate with Drawings.  See Editing Instruction No. 6 in the Evaluations.

H. Cooling System:  Closed loop, liquid cooled, with radiator factory mounted on engine-generator-set mounting frame and integral engine-driven coolant pump.

1. Coolant:  Solution of 50 percent ethylene-glycol-based antifreeze and 50 percent water, with anticorrosion additives as recommended by engine manufacturer.

Retain one of first two subparagraphs below.  Retain second if containment of coolant expansion by radiator is marginal or inadequate.  Coordinate with Drawings.

2. Size of Radiator:  Adequate to contain expansion of total system coolant from cold start to 110 percent load condition.

3. Expansion Tank:  Constructed of welded steel plate and rated to withstand maximum closed-loop coolant system pressure for engine used.  Equip with gage glass and petcock.

4. Temperature Control:  Self-contained, thermostatic-control valve modulates coolant flow automatically to maintain optimum constant coolant temperature as recommended by engine manufacturer.

5. Coolant Hose:  Flexible assembly with inside surface of nonporous rubber and outer covering of aging-, ultraviolet-, and abrasion-resistant fabric.

a. Rating:  50-psig (345-kPa) maximum working pressure with coolant at 180 deg F (82 deg C), and noncollapsible under vacuum.

b. End Fittings:  Flanges or steel pipe nipples with clamps to suit piping and equipment connections.

I. Cooling System:  Closed loop, liquid cooled, with remote radiator and integral engine-driven coolant pump.

1. Configuration:  [Vertical] [Horizontal] air discharge.

2. Radiator Core Tubes:  [Aluminum] [Nonferrous-metal construction other than aluminum].

Retain one of first two subparagraphs below.  Retain second if containment of coolant expansion by radiator is marginal or inadequate.  Coordinate with Drawings.

3. Size of Radiator:  Adequate to contain expansion of total system coolant from cold start to 110 percent load condition.

4. Expansion Tank:  Constructed of welded steel plate and rated to withstand maximum closed-loop coolant system pressure for engine used.  Equip with gage glass and petcock.

5. Fan:  Driven by [multiple belts from engine shaft] [totally enclosed electric motor with sealed bearings].

6. Coolant:  Solution of 50 percent ethylene-glycol-based antifreeze and 50 percent water, with anticorrosion additives as recommended by engine manufacturer.

7. Temperature Control:  Self-contained, thermostatic-control valve modulates coolant flow automatically to maintain optimum constant coolant temperature as recommended by engine manufacturer.

Retain one of three "Muffler/Silencer" paragraphs below.  Modify dBA requirement in second subparagraph to accommodate environment in which engine-generator set is operating.  If unit is specified with an enclosure, consider specifying sound level requirements at specified distance from enclosure on each of four sides.

J. Muffler/Silencer:  Critical type, sized as recommended by engine manufacturer and selected with exhaust piping system to not exceed engine manufacturer's engine backpressure requirements.

1. Minimum sound attenuation of 25 dB at 500 Hz.

2. Sound level measured at a distance of 10 feet (3 m) from exhaust discharge after installation is complete shall be [85] <Insert number> dBA or less.

K. Muffler/Silencer:  Residential type, sized as recommended by engine manufacturer and selected with exhaust piping system to not exceed engine manufacturer's engine backpressure requirements.

1. Minimum sound attenuation of 18 dB at 500 Hz.

2. Sound level measured at a distance of 10 feet (3 m) from exhaust discharge after installation is complete shall be [95] <Insert number> dBA or less.

L. Muffler/Silencer:  Industrial type, sized as recommended by engine manufacturer and selected with exhaust piping system to not exceed engine manufacturer's engine backpressure requirements.

1. Minimum sound attenuation of 12 dB at 500 Hz.

2. Sound level measured at a distance of 25 feet (8 m) from exhaust discharge after installation is complete shall be [87] <Insert number> dBA or less.

Retain second option in paragraph below if filters may not be serviced as often as recommended.  If air contaminant level is excessive, consult manufacturers to determine if special filtration of combustion air is needed.

M. Air-Intake Filter:  [Standard] [Heavy]-duty, engine-mounted air cleaner with replaceable dry-filter element and "blocked filter" indicator.

Select first option in paragraph below for smaller engine-generator sets.  Retain second option for units 175 kW and larger.

N. Starting System:  [12] [24]-V electric, with negative ground.

1. Components:  Sized so they will not be damaged during a full engine-cranking cycle with ambient temperature at maximum specified in Part 1 "Project Conditions" Article.

2. Cranking Motor:  Heavy-duty unit that automatically engages and releases from engine flywheel without binding.

Retain first option in subparagraph below if system description in Part 1 "Quality Assurance" Article specifies NFPA 110, Level 1 or 2; otherwise, retain second.  See Editing Instruction No. 7 in the Evaluations.

3. Cranking Cycle: [As required by NFPA 110 for system level specified] [60 seconds].

First option in subparagraph below complies with NFPA 110 requirements.  Second is a more conservative rule used for some industrial applications.

4. Battery:  Adequate capacity within ambient temperature range specified in Part 1 "Project Conditions" Article to provide specified cranking cycle at least [twice] [three times] without recharging.

Coordinate subparagraph below with Drawings.

5. Battery Cable:  Size as recommended by engine manufacturer for cable length indicated.  Include required interconnecting conductors and connection accessories.

Retain first subparagraph below if compartment is required.

6. Battery Compartment:  Factory fabricated of metal with acid-resistant finish and thermal insulation.  Thermostatically controlled heater shall be arranged to maintain battery above 10 deg C regardless of external ambient temperature within range specified in Part 1 "Project Conditions" Article.  Include accessories required to support and fasten batteries in place.

7. Battery-Charging Alternator:  Factory mounted on engine with solid-state voltage regulation and 35-A minimum continuous rating.

Coordinate first subparagraph below with Division 16 Section "Transfer Switches."  Retain if battery charger is not specified to be integral with transfer switch.

8. Battery Charger:  Current-limiting, automatic-equalizing and float-charging type.  Unit shall comply with UL 1236 and include the following features:

a. Operation:  Equalizing-charging rate of 10 A shall be initiated automatically after battery has lost charge until an adjustable equalizing voltage is achieved at battery terminals.  Unit shall then be automatically switched to a lower float-charging mode and shall continue to operate in that mode until battery is discharged again.

b. Automatic Temperature Compensation:  Adjust float and equalize voltages for variations in ambient temperature from minus 40 deg C to plus 60 deg C to prevent overcharging at high temperatures and undercharging at low temperatures.

c. Automatic Voltage Regulation:  Maintain constant output voltage regardless of input voltage variations up to plus or minus 10 percent.

d. Ammeter and Voltmeter:  Flush mounted in door.  Meters shall indicate charging rates.

First subparagraph below covers sensing for safety indications on control and monitoring panel.  NFPA 110 requires sensing for Level 1 systems and makes sensing optional for Level 2 systems.  See Editing Instruction No. 4 in the Evaluations.

e. Safety Functions:  Sense abnormally low battery voltage and close contacts providing low battery voltage indication on control and monitoring panel.  Sense high battery voltage and loss of ac input or dc output of battery charger.  Either condition shall close contacts that provide a battery-charger malfunction indication at system control and monitoring panel.

f. Enclosure and Mounting:  NEMA 250, Type 1, wall-mounted cabinet.

2.4 FUEL OIL STORAGE

Retain this Article for diesel-engine units.

A. Comply with NFPA 30.

B. Day Tank:  Comply with UL 142, freestanding, factory-fabricated fuel tank assembly, with integral, float-controlled transfer pump and the following features:

1. Containment:  Integral rupture basin with a capacity of 150 percent of nominal capacity of day tank.

a. Leak Detector:  Locate in rupture basin and connect to provide audible and visual alarm in the event of day-tank leak.

Revise hours in first subparagraph below or delete subparagraph and indicate capacity on Drawings.  Coordinate with Drawings and NFPA 110 requirements.

2. Tank Capacity:  [As recommended by engine manufacturer for an uninterrupted period of 4 hours' operation at 100 percent of rated power output of engine-generator system without being refilled] <Insert gallons (liters)>.

3. Pump Capacity:  Exceeds maximum flow of fuel drawn by engine-mounted fuel supply pump at 110 percent of rated capacity, including fuel returned from engine.

4. Low-Level Alarm Sensor:  Liquid-level device operates alarm contacts at 25 percent of normal fuel level.

Revise first subparagraph below or delete if not required.  Coordinate with Part 2 "Control and Monitoring" Article.

5. High-Level Alarm Sensor:  Liquid-level device operates alarm and redundant fuel shutoff contacts at midpoint between overflow level and 100 percent of normal fuel level.

6. Piping Connections:  Factory-installed fuel supply and return lines from tank to engine; local fuel fill, vent line, overflow line; and tank drain line with shutoff valve.

Subparagraph below is not in NFPA 110 minimum requirements.

7. Redundant High-Level Fuel Shutoff:  Actuated by high-level alarm sensor in day tank to operate a separate motor device that disconnects day-tank pump motor.  Sensor shall signal solenoid valve, located in fuel suction line between fuel storage tank and day tank, to close.  Both actions shall remain in shutoff state until manually reset.  Shutoff action shall initiate an alarm signal to control panel but shall not shut down engine-generator set.

C. Base-Mounted Fuel Oil Tank:  Factory installed and piped, complying with UL 142 fuel oil tank.  Features include the following:

1. Tank level indicator.

Consult tank manufacturers about capacities available for size of set in Project.

2. Capacity:  Fuel for [eight] <Insert number> hours' continuous operation at 100 percent rated power output.

3. Vandal-resistant fill cap.

Determine applicable codes and regulations, and coordinate subparagraph below with Drawings.

4. Containment Provisions:  Comply with requirements of authorities having jurisdiction.

2.5 CONTROL AND MONITORING

This Article specifies the subsystem that monitors, protects, and controls the engine generator.  See Editing Instruction No. 8 in the Evaluations.

Retain first paragraph below for automatically starting systems; retain second paragraph for manually starting systems.

A. Automatic Starting System Sequence of Operation:  When mode-selector switch on the control and monitoring panel is in the automatic position, remote-control contacts in one or more separate automatic transfer switches initiate starting and stopping of generator set.  When mode-selector switch is switched to the on position, generator set starts.  The off position of same switch initiates generator-set shutdown.  When generator set is running, specified system or equipment failures or derangements automatically shut down generator set and initiate alarms.  Operation of a remote emergency-stop switch also shuts down generator set.

B. Manual Starting System Sequence of Operation:  Switching on-off switch on the generator control panel to the on position starts generator set.  The off position of same switch initiates generator-set shutdown.  When generator set is running, specified system or equipment failures or derangements automatically shut down generator set and initiate alarms.  Operation of a remote emergency-stop switch also shuts down generator set.

Retain one of three paragraphs below to describe control and monitoring unit configuration.  Coordinate retained paragraph with Drawings.  Retain first paragraph unless special requirements justify significant extra cost of one of the other two configurations.  See Evaluations.

C. Configuration:  Operating and safety indications, protective devices, basic system controls, and engine gages shall be grouped in a common control and monitoring panel mounted on the generator set.  Mounting method shall isolate the control panel from generator-set vibration.

D. Configuration:  Operating and safety indications, protective devices, basic system controls, and engine gages shall be grouped in a common wall-mounted control and monitoring panel.

E. Configuration:  Operating and safety indications, protective devices, basic system controls, engine gages, instrument transformers, generator disconnect switch or circuit breaker, and other indicated components shall be grouped in a combination control and power panel.  Control and monitoring section of panel shall be isolated from power sections by steel barriers.  Panel features shall include the following:

Retain one of first two subparagraphs below to further define control and power panel in last paragraph above.

1. Wall-Mounting Cabinet Construction:  Rigid, self-supporting steel unit complying with NEMA ICS 6.  Power bus shall be copper.  Bus, bus supports, control wiring, and temperature rise shall comply with UL 891.

2. Switchboard Construction:  Freestanding unit complying with Division 16 Section "Switchboards."

3. Switchgear Construction:  Freestanding unit complying with Division 16 Section "Switchgear."

4. Current and Potential Transformers:  Instrument accuracy class.

Retain one of first two paragraphs and associated subparagraphs below to specify minimum control and monitoring panel features.  First is for standardized panels for automatically starting units.  Second is for a typical manually operated generator system.  Coordinate with Drawings.  See Editing Instruction No. 9 in the Evaluations.

F. Indicating and Protective Devices and Controls:  As required by NFPA 110 for Level [1] [2] system, and the following:

1. AC voltmeter.

2. AC ammeter.

3. AC frequency meter.

4. DC voltmeter (alternator battery charging).

5. Engine-coolant temperature gage.

6. Engine lubricating-oil pressure gage.

7. Running-time meter.

8. Ammeter-voltmeter, phase-selector switch(es).

9. Generator-voltage adjusting rheostat.

Two subparagraphs below are optional devices.

10. Fuel tank derangement alarm.

11. Fuel tank high-level shutdown of fuel supply alarm.

Retain subparagraph below for units with "generator-protector" feature.

12. Generator overload.

G. Indicating and Protective Devices and Controls:

1. AC voltmeter.

2. AC ammeter.

3. AC frequency meter.

4. DC voltmeter (alternator battery charging).

5. Engine-coolant temperature gage.

6. Engine lubricating-oil pressure gage.

7. Running-time meter.

8. Ammeter-voltmeter, phase-selector switch(es).

9. Generator-voltage adjusting rheostat.

Coordinate five subparagraphs below with Drawings.  See Evaluations for typical local and remote alarm indications and shutdowns.

10. Start-stop switch.

11. Overspeed shutdown device.

12. Coolant high-temperature shutdown device.

13. Coolant low-level shutdown device.

14. Oil low-pressure shutdown device.

Two subparagraphs below are optional devices.

15. Fuel tank derangement alarm.

16. Fuel tank high-level shutdown of fuel supply alarm.

Retain subparagraph below for units with "generator-protector" feature.

17. Generator overload.

H. Supporting Items:  Include sensors, transducers, terminals, relays, and other devices and include wiring required to support specified items.  Locate sensors and other supporting items on engine or generator, unless otherwise indicated.

Feature in paragraph below facilitates connection to building automation system or building control and monitoring system.  Coordinate with Drawings and Section covering data transmission and data terminals.

I. Connection to Data Link:  A separate terminal block, factory wired to Form C dry contacts, for each alarm and status indication is reserved for connections for data-link transmission of indications to remote data terminals.  Data system connections to terminals are covered in Division 16 Section "Electrical Power Monitoring and Control."

Retain one of first two paragraphs and associated subparagraphs below or delete all.  The Evaluations discuss what will be obtained by selecting first paragraph and subparagraphs.  Coordinate with Drawings.

J. Common Remote Audible Alarm:  Comply with NFPA 110 requirements for Level 1 systems.  Include necessary contacts and terminals in control and monitoring panel.

1. Overcrank shutdown.

2. Coolant low-temperature alarm.

3. Control switch not in auto position.

4. Battery-charger malfunction alarm.

5. Battery low-voltage alarm.

Retain paragraph and subparagraphs below and coordinate with Drawings for manually starting systems or for automatically starting systems not specified to comply with NFPA 110, Level 1, but where some remote alarm functions are needed.

K. Common Remote Audible Alarm:  Signal the occurrence of any events listed below without differentiating between event types.  Connect so that after an alarm is silenced, clearing of initiating condition will reactivate alarm until silencing switch is reset.

1. Engine high-temperature shutdown.

2. Lube-oil, low-pressure shutdown.

3. Overspeed shutdown.

4. Remote emergency-stop shutdown.

5. Engine high-temperature prealarm.

6. Lube-oil, low-pressure prealarm.

7. Fuel tank, low-fuel level.

8. Low coolant level.

Retain paragraph below and coordinate with Drawings for systems required to comply with NFPA 99 or where otherwise needed.  Revise if all indications required by NFPA 99 are not needed.

L. Remote Alarm Annunciator:  Comply with NFPA 99.  An LED labeled with proper alarm conditions shall identify each alarm event and a common audible signal shall sound for each alarm condition.  Silencing switch in face of panel shall silence signal without altering visual indication.  Connect so that after an alarm is silenced, clearing of initiating condition will reactivate alarm until silencing switch is reset.  Cabinet and faceplate are surface- or flush-mounting type to suit mounting conditions indicated.

Coordinate paragraph below with Drawings.

M. Remote Emergency-Stop Switch:  Flush; wall mounted, unless otherwise indicated; and labeled.  Push button shall be protected from accidental operation.

2.6 GENERATOR OVERCURRENT AND FAULT PROTECTION

Retain one or more paragraphs in this Article to specify disconnect switch(es) and protective devices for the generator (alternator) component of generator set.  Revise as required to accommodate multiple output devices.  See Editing Instruction No. 10 in the Evaluations.

Retain one of first four paragraphs and associated subparagraphs below.  Retain first for units smaller than 200 kW where initial cost is a concern.  Device provides little or no generator protection and no selectivity with downstream circuit protective devices.

A. Generator Circuit Breaker:  Molded-case, thermal-magnetic type; 100 percent rated; complying with NEMA AB 1 and UL 489.

1. Tripping Characteristic:  Designed specifically for generator protection.

2. Trip Rating:  Matched to generator rating.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

B. Generator Circuit Breaker:  Molded-case, electronic-trip type; 100 percent rated; complying with UL 489.

1. Tripping Characteristics:  Adjustable long-time and short-time delay and instantaneous.

2. Trip Settings:  Selected to coordinate with generator thermal damage curve.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

C. Generator Circuit Breaker:  Insulated-case, electronic-trip type; 100 percent rated; complying with UL 489.

1. Tripping Characteristics:  Adjustable long-time and short-time delay and instantaneous.

2. Trip Settings:  Selected to coordinate with generator thermal damage curve.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

Retain paragraph and subparagraphs below if generator is protected by "generator-protector" feature.

D. Generator Disconnect Switch:  Molded-case type, 100 percent rated.

1. Rating:  Matched to generator output rating.

2. Shunt Trip:  Connected to trip switch when signaled by generator protector or by other protective devices.

Protection scheme specified in paragraph and subparagraphs below may be proprietary.  Consult manufacturers.

E. Generator Protector:  Microprocessor-based unit shall continuously monitor current level in each phase of generator output, integrate generator heating effect over time, and predict when thermal damage of alternator will occur.  When signaled by generator protector or other generator-set protective devices, a shunt-trip device in the generator disconnect switch shall open the switch to disconnect the generator from load circuits.  Protector shall perform the following functions:

1. Initiates a generator overload alarm when generator has operated at an overload equivalent to 110 percent of full-rated load for 60 seconds.  Indication for this alarm is integrated with other generator-set malfunction alarms.

2. Under single or three-phase fault conditions, regulates generator to 300 percent of rated full-load current for up to 10 seconds.

3. As overcurrent heating effect on the generator approaches the thermal damage point of the unit, protector switches the excitation system off, opens the generator disconnect device, and shuts down the generator set.

4. Senses clearing of a fault by other overcurrent devices and controls recovery of rated voltage to avoid overshoot.

Retain paragraph below and coordinate with Drawings for legally required emergency generator sets rated 1000 A and more at 277/480 V.

F. Ground-Fault Indication:  Comply with NFPA 70, "Emergency System" signals for ground-fault.  Integrate ground-fault alarm indication with other generator-set alarm indications.

2.7 GENERATOR, EXCITER, AND VOLTAGE REGULATOR

A. Comply with NEMA MG 1.

B. Drive:  Generator shaft shall be directly connected to engine shaft.  Exciter shall be rotated integrally with generator rotor.

C. Electrical Insulation:  Class H or Class F.

D. Stator-Winding Leads:  Brought out to terminal box to permit future reconnection for other voltages if required.

E. Construction shall prevent mechanical, electrical, and thermal damage due to vibration, overspeed up to 125 percent of rating, and heat during operation at 110 percent of rated capacity.

F. Enclosure:  Dripproof.

Delete first paragraph below if instrument transformers are housed in control and power panel.

G. Instrument Transformers:  Mounted within generator enclosure.

H. Voltage Regulator:  Solid-state type, separate from exciter, providing performance as specified.

1. Adjusting rheostat on control and monitoring panel shall provide plus or minus 5 percent adjustment of output-voltage operating band.

Retain paragraph below for high-humidity environments to limit condensation in alternator windings.

I. Strip Heater:  Thermostatically controlled unit arranged to maintain stator windings above dew point.

Retain both paragraphs below for units specified for "critical" performance.  Coordinate with generator-set performance Paragraph selected in "Engine-Generator Set" Article.  See "Specifying Considerations" Article in the Evaluations for discussions on sensitive electronic equipment and nonlinear generator loads and on supplying significant harmonic currents.

J. Windings:  Two-thirds pitch stator winding and fully linked amortisseur winding.

K. Subtransient Reactance:  [12] <Insert number> percent, maximum.

2.8 LOAD BANK

Retain this Article and revise for resistive load elements only or for another type of load bank.  See Editing Instruction No. 11 in the Evaluations.  Coordinate with Drawings.

A. Description:  Permanent, outdoor, weatherproof, remote-controlled, forced-air-cooled, [resistive] [resistive and reactive] unit capable of providing a balanced 3-phase, delta-connected load to generator set at [100] <Insert number> percent rated-system capacity, at [80] <Insert number> percent power factor, lagging.  Unit may be composed of separate resistive and reactive load banks controlled by a common control panel.  Unit shall be capable of selective control of load in 25 percent steps and with minimum step changes of approximately 5 and 10 percent available.

B. Resistive Load Elements:  Corrosion-resistant chromium alloy with ceramic and steel supports.  Elements shall be double insulated and designed for repetitive on-off cycling.  Elements shall be mounted in removable aluminized-steel heater cases.

C. Reactive Load Elements:  Epoxy-encapsulated reactor coils.

D. Load-Bank Heat Dissipation:  Integral fan with totally enclosed motor shall provide uniform cooling airflow through load elements.  Airflow and coil operating current shall be such that, at maximum load, with ambient temperature at the upper end of specified range, load-bank elements operate at not more than 50 percent of maximum continuous temperature rating of resistance elements.

E. Load Element Switching:  Remote-controlled contactors switch groups of load elements.  Contactor coils are rated 120 V.  Contactors shall be located in a separate NEMA 250, Type 3R enclosure within load-bank enclosure, accessible from exterior through hinged doors with tumbler locks.

F. Contactor Enclosures:  Heated by thermostatically controlled strip heaters to prevent condensation.

G. Load-Bank Enclosures:  NEMA 250, Type 3R, complying with NEMA ICS 6.  Louvers at cooling-air intake and discharge openings shall prevent entry of rain and snow.  Openings for airflow shall be screened with 1/2-inch- (13-mm-) square, galvanized-steel mesh.  Reactive load bank shall include automatic shutters at air intake and discharge.

H. Protective Devices:  Power input circuits to load banks shall be fused, and fuses shall be selected to coordinate with generator circuit breaker.  Fuse blocks shall be located in contactor enclosure.  Cooling airflow and overtemperature sensors shall automatically shut down and lock out load bank until manually reset.  Safety interlocks on access panels and doors shall disconnect load power, control, and heater circuits.  Fan motor shall be separately protected by overload and short-circuit devices.  Short-circuit devices shall be noninterchangeable fuses with 200,000-A interrupting capacity.

Coordinate two paragraphs below with Drawings.

I. Remote-Control Panel:  Separate from load bank in NEMA 250, Type 1 enclosure with a control power switch and pilot light, and switches controlling groups of load elements.

Retain paragraph below if load bank is used in automatic exercising of generator.  Coordinate with Section covering remote-controlled switch, contactor, or electrically operated circuit breaker used to switch load bank to generator output.  Switching device is typically not part of equipment specified in this Section.

J. Control Sequence:  Control panel may be preset for adjustable single-step loading of generator during automatic exercising.

2.9 OUTDOOR GENERATOR-SET ENCLOSURE

Retain one of first two paragraphs and associated subparagraphs below and coordinate with Drawings to define basic outdoor-enclosure type.  Edit to specify enclosure features required.

A. Description:  Vandal-resistant, weatherproof steel housing, wind resistant up to 100 mph (160 km/h).  Multiple panels shall be lockable and provide adequate access to components requiring maintenance.  Panels shall be removable by one person without tools.  Instruments and control shall be mounted within enclosure.

Coordinate first paragraph and subparagraphs below with Drawings showing features, construction details, and equipment arrangement.

B. Description:  Prefabricated or preengineered walk-in enclosure with the following features:

1. Construction:  Galvanized-steel, metal-clad, integral structural-steel-framed building erected on concrete foundation.

Revise wind speed in first subparagraph below to suit local conditions.

2. Structural Design and Anchorage:  Comply with ASCE 7 for wind loads.

3. Space Heater:  Thermostatically controlled and sized to prevent condensation.

4. Louvers:  Equipped with bird screen and filter arranged to permit air circulation when engine is not running while excluding exterior dust, birds, and rodents.

5. Hinged Doors:  With padlocking provisions.

Revise first subparagraph below if forced ventilation rather than convection ventilation is required.

6. Ventilation:  Louvers equipped with bird screen and filter arranged to permit air circulation while excluding exterior dust, birds, and rodents.

7. Thermal Insulation:  Manufacturer's standard materials and thickness selected in coordination with space heater to maintain winter interior temperature within operating limits required by engine-generator-set components.

8. Muffler Location:  [Within] [External to] enclosure.

C. Engine Cooling Airflow through Enclosure:  Maintain temperature rise of system components within required limits when unit operates at 110 percent of rated load for 2 hours with ambient temperature at top of range specified in system service conditions.

1. Louvers:  Fixed-engine, cooling-air inlet and discharge.  Storm-proof and drainable louvers prevent entry of rain and snow.

2. Automatic Dampers:  At engine cooling-air inlet and discharge.  Dampers shall be closed to reduce enclosure heat loss in cold weather when unit is not operating.

Coordinate two paragraphs and associated subparagraphs below with Drawings for lighting types and location, and supply circuits.

D. Interior Lights with Switch:  Factory-wired, vaporproof-type fixtures within housing; arranged to illuminate controls and accessible interior.  Arrange for external electrical connection.

1. AC lighting system and connection point for operation when remote source is available.

2. DC lighting system for operation when remote source and generator are both unavailable.

E. Convenience Outlets:  Factory wired[, GFCI].  Arrange for external electrical connection.

2.10 MOTORS

Retain this Article for generator sets with remote radiators.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, insert additional requirements below.

A. General requirements for motors are specified in Division 15 Section "Motors."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

2.11 VIBRATION ISOLATION DEVICES

A. Elastomeric Isolator Pads:  Oil- and water-resistant elastomer or natural rubber, arranged in single or multiple layers, molded with a nonslip pattern and galvanized-steel baseplates of sufficient stiffness for uniform loading over pad area, and factory cut to sizes that match requirements of supported equipment.

See the Evaluations in Division 15 Section "Mechanical Vibration and Seismic Controls" for a discussion on vibration and seismic-control devices.  Pads in subparagraph below come in standard neoprene, natural rubber, and bridge-bearing neoprene.  Verify availability of various materials with manufacturers.  Costs range from least to most expensive in the order presented below.

1. Material:  [Standard neoprene] [Natural rubber] [Bridge-bearing neoprene, complying with AASHTO M 251].

Durometer values range from 30 to 70 and are measures of hardness or, indirectly, deflection.  Lower durometer values indicate softer material with more deflection.

2. Durometer Rating:  [30] [40] [45] [50] [60] [65] [70] <Insert number>.

Use multiple layers, separated by steel shims, depending on supported equipment load.  See manufacturer's data for load capacities.

3. Number of Layers:  [One] [Two] [Three] [Four] <Insert number>.

Coordinate paragraph and subparagraphs below with Drawings and with Division 16 Section "Electrical Supports and Seismic Restraints."

B. Restrained Spring Isolators:  Freestanding, steel, open-spring isolators with seismic restraint.

1. Housing:  Steel with resilient vertical-limit stops to prevent spring extension due to wind loads or if weight is removed; factory-drilled baseplate bonded to 1/4-inch- (6-mm-) thick, elastomeric isolator pad attached to baseplate underside; and adjustable equipment mounting and leveling bolt that acts as blocking during installation.

2. Outside Spring Diameter:  Not less than 80 percent of compressed height of the spring at rated load.

3. Minimum Additional Travel:  50 percent of required deflection at rated load.

4. Lateral Stiffness:  More than 80 percent of rated vertical stiffness.

5. Overload Capacity:  Support 200 percent of rated load, fully compressed, without deformation or failure.

2.12 FINISHES

A. Indoor and Outdoor Enclosures and Components:  Manufacturer's standard finish over corrosion-resistant pretreatment and compatible primer.

2.13 SOURCE QUALITY CONTROL

A. Prototype Testing:  Factory test engine-generator set using same engine model, constructed of identical or equivalent components and equipped with identical or equivalent accessories.

Consider requiring Level 1 compliance in subparagraph below for other than Level 1 installations to obtain benefits of specific standard requirements.

1. Tests:  Comply with NFPA 110, Level 1 Energy Converters and with IEEE 115.

B. Project-Specific Equipment Tests:  Before shipment, factory test engine-generator set and other system components and accessories manufactured specifically for this Project.  Perform tests at rated load and power factor.  Include the following tests:

1. Test components and accessories furnished with installed unit that are not identical to those on tested prototype to demonstrate compatibility and reliability.

2. Full load run.

3. Maximum power.

4. Voltage regulation.

5. Transient and steady-state governing.

6. Single-step load pickup.

7. Safety shutdown.

Retain subparagraph below if factory tests will be witnessed by Owner's representative.

8. Provide 14 days' advance notice of tests and opportunity for observation of tests by Owner's representative.

Coordinate subparagraph below with Part 1 "Submittals" Article.

9. Report factory test results within 10 days of completion of test.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas, equipment bases, and conditions, with Installer present, for compliance with requirements for installation and other conditions affecting packaged engine-generator performance.

B. Examine roughing-in of piping systems and electrical connections.  Verify actual locations of connections before packaged engine-generator installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Comply with packaged engine-generator manufacturers' written installation and alignment instructions and with NFPA 110.

B. Install packaged engine generator to provide access, without removing connections or accessories, for periodic maintenance.

C. Install packaged engine generator with [elastomeric isolator pads] [restrained spring isolators] having a minimum deflection of [1 inch (25 mm)] <Insert static deflection> on 4-inch- (100-mm-) high concrete base.  Secure sets to anchor bolts installed in concrete bases.  Concrete base construction is specified in Division 16 Section "Electrical Supports and Seismic Restraints."

D. Install remote radiator with [elastomeric isolator pads] [restrained spring isolators] having a minimum deflection of [1 inch (25 mm)] <Insert static deflection> on [concrete base on grade] [roof equipment supports on roof].

Delete first paragraph below if radiator is engine mounted.

E. Install Schedule 40, black steel piping with welded joints for cooling water piping between engine-generator set and [heat exchanger] [remote radiator].  Piping materials and installation requirements are specified in Division 15 Section "Hydronic Piping."

F. Install Schedule 40, black steel piping with welded joints and connect to engine muffler.  Install thimble at wall.  Piping shall be same diameter as muffler outlet.  Flexible connectors and steel piping materials and installation requirements are specified in Division 15 Section "Hydronic Piping."

Coordinate subparagraph below with Drawings.

1. Install condensate drain piping to muffler drain outlet full size of drain connection with a shutoff valve, stainless-steel flexible connector, and Schedule 40, black steel pipe with welded joints.  Flexible connectors and piping materials and installation requirements are specified in Division 15 Section "Hydronic Piping."

G. Electrical Wiring:  Install electrical devices furnished by equipment manufacturers but not specified to be factory mounted.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in Division 15 Sections.  Drawings indicate general arrangement of piping and specialties.

B. Connect fuel, cooling-system, and exhaust-system piping adjacent to packaged engine generator to allow service and maintenance.

Coordinate first paragraph below with Division 15 Section "Hydronic Piping."

C. Connect cooling-system water piping to engine-generator set and [remote radiator] [heat exchanger] with flexible connectors.

D. Connect engine exhaust pipe to engine with flexible connector.

E. Connect fuel piping to engines with a gate valve and union and flexible connector.

1. Diesel storage tanks, tank accessories, piping, valves, and specialties for fuel systems outside the building are specified in Division 2 Section "Fuel Oil Distribution."

2. Diesel fuel piping, valves, and specialties inside the building are specified in Division 15 Section "Fuel Oil Piping."

3. Natural- and LP-gas piping, valves, and specialties for gas distribution outside the building are specified in Division 2 Section "Natural Gas Distribution."

4. Natural- and LP-gas piping, valves, and specialties for gas piping inside the building are specified in Division 15 Section "Fuel Gas Piping."

F. Ground equipment according to Division 16 Section "Grounding and Bonding."

G. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 IDENTIFICATION

A. Identify system components according to Division 15 Section "Mechanical Identification" and Division 16 Section "Electrical Identification."

3.5 FIELD QUALITY CONTROL

Retain one of first three paragraphs below, which identify who shall perform tests and inspections.  If retaining second option in first paragraph below, or if retaining second or third paragraphs, retain requirement for field quality-control test reports in Part 1 "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections and prepare test reports.

Retain paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

C. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed by any of the entities in three paragraphs above.

D. Tests and Inspections:

NETA and other testing requirements indicated in subparagraphs below may be in excess of those required for Project.  Review NETA and other tests listed and revise subparagraphs below to retain only those tests deemed necessary.

1. Perform tests recommended by manufacturer and each electrical test and visual and mechanical inspection[ (except those indicated to be optional)] for "AC Generators and for Emergency Systems" specified in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

2. NFPA 110 Acceptance Tests:  Perform tests required by NFPA 110 that are additional to those specified here including, but not limited to, single-step full-load pickup test.

3. Battery Tests:  Equalize charging of battery cells according to manufacturer's written instructions.  Record individual cell voltages.

a. Measure charging voltage and voltages between available battery terminals for full-charging and float-charging conditions.  Check electrolyte level and specific gravity under both conditions.

b. Test for contact integrity of all connectors.  Perform an integrity load test and a capacity load test for the battery.

c. Verify acceptance of charge for each element of the battery after discharge.

d. Verify that measurements are within manufacturer's specifications.

4. Battery-Charger Tests:  Verify specified rates of charge for both equalizing and float-charging conditions.

5. System Integrity Tests:  Methodically verify proper installation, connection, and integrity of each element of engine-generator system before and during system operation.  Check for air, exhaust, and fluid leaks.

Retain subparagraph below for long, restricted exhaust systems.

6. Exhaust-System Back-Pressure Test:  Use a manometer with a scale exceeding 40-inch wg (120 kPa).  Connect to exhaust line close to engine exhaust manifold.  Verify that back pressure at full-rated load is within manufacturer's written allowable limits for the engine.

Verify local requirements and delete first subparagraph below for most projects.  Few jurisdictions require this test for emergency or standby generator sets.

7. Exhaust Emissions Test:  Comply with applicable government test criteria.

8. Voltage and Frequency Transient Stability Tests:  Use recording oscilloscope to measure voltage and frequency transients for 50 and 100 percent step-load increases and decreases, and verify that performance is as specified.

9. Harmonic-Content Tests:  Measure harmonic content of output voltage under 25 percent and at 100 percent of rated linear load.  Verify that harmonic content is within specified limits.

Retain subparagraph below for projects subject to unwanted or illegal generator-set noise intrusion into adjacent properties or activities.  Coordinate with Drawings and with requirements in Part 1 "Submittals" and "Quality Assurance" articles and in Part 2 "Engine" Article.

10. Noise Level Tests:  Measure A-weighted level of noise emanating from generator-set installation, including engine exhaust and cooling-air intake and discharge, at [four] <Insert number> locations [on the property line] <Insert location for measurement>, and compare measured levels with required values.

E. Coordinate tests with tests for transfer switches and run them concurrently.

F. Test instruments shall have been calibrated within the last 12 months, traceable to standards of NIST, and adequate for making positive observation of test results.  Make calibration records available for examination on request.

G. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

H. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

I. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

J. Remove and replace malfunctioning units and [retest] [reinspect] as specified above.

K. Retest:  Correct deficiencies identified by tests and observations and retest until specified requirements are met.

L. Report results of tests and inspections in writing.  Record adjustable relay settings and measured insulation resistances, time delays, and other values and observations.  Attach a label or tag to each tested component indicating satisfactory completion of tests.

M. Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each power wiring termination and each bus connection.  Remove all access panels so terminations and connections are accessible to portable scanner.

1. Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan 11 months after date of Substantial Completion.

2. Instrument:  Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

3. Record of Infrared Scanning:  Prepare a certified report that identifies terminations and connections checked and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain packaged engine generators.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 16231

PACKAGED ENGINE GENERATOR
16231 - 1

