Copyright 2006 AIA
MASTERSPEC Full Length
03/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16410 - ENCLOSED SWITCHES AND CIRCUIT BREAKERS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Fusible switches.

2. Nonfusible switches.

3. Receptacle switches.

4. Shunt trip switches.

5. Molded-case circuit breakers (MCCBs).

6. Molded-case switches.

7. Enclosures.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. NC:  Normally closed.

B. NO:  Normally open.

C. SPDT:  Single pole, double throw.

1.4 PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

A. Seismic Performance:  Enclosed switches and circuit breakers shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.5 SUBMITTALS

First two paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of enclosed switch, circuit breaker, accessory, and component indicated.  Include dimensioned elevations, sections, weights, and manufacturers' technical data on features, performance, electrical characteristics, ratings, accessories, and finishes.

1. Enclosure types and details for types other than NEMA 250, Type 1.

2. Current and voltage ratings.

3. Short-circuit current ratings (interrupting and withstand, as appropriate).

Retain first subparagraph below if using series rating of overcurrent protective devices.

4. Include evidence of NRTL listing for series rating of installed devices.

5. Detail features, characteristics, ratings, and factory settings of individual overcurrent protective devices, accessories, and auxiliary components.

Retain subparagraph below if final system short-circuit and coordination studies will be performed by the designer or will be assigned to an independent consultant.  These curves are also beneficial to Owner for future additions or reevaluations of settings of overcurrent protective devices.  Although some manufacturers no longer offer curves on translucent graph paper, curves can normally be downloaded from manufacturers' Web sites or be obtained, in electronic form, from various coordination software vendors as part of a subscription service.  Retain option in subparagraph below only if manufacturers selected offer curves on graph paper.

6. Include time-current coordination curves (average melt) for each type and rating of overcurrent protective device; include selectable ranges for each type of overcurrent protective device.[  Submit on translucent log-log graph paper.]

B. Shop Drawings:  For enclosed switches and circuit breakers.  Include plans, elevations, sections, details, and attachments to other work.

1. Wiring Diagrams:  For power, signal, and control wiring.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For qualified testing agency.

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Vibration and Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

D. Seismic Qualification Certificates:  For enclosed switches and circuit breakers, accessories, and components, from manufacturer.

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

E. Field quality-control reports.

1. Test procedures used.

2. Test results that comply with requirements.

3. Results of failed tests and corrective action taken to achieve test results that comply with requirements.

Retain first paragraph below if retaining "Manufacturer's Field Service" Paragraph in "Field Quality Control" Article.  Consider manufacturer's field services especially when retaining zone-selective interlocking because setting it to operate properly requires factory-trained expertise.

F. Manufacturer's field service report.

G. Operation and Maintenance Data:  For enclosed switches and circuit breakers to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1 Section "Operation and Maintenance Data," include the following:

1. Manufacturer's written instructions for testing and adjusting enclosed switches and circuit breakers.

Retain option in subparagraph below only if manufacturers selected offer curves on graph paper.

2. Time-current coordination curves (average melt) for each type and rating of overcurrent protective device; include selectable ranges for each type of overcurrent protective device.[  Submit on translucent log-log graph paper.]

1.6 QUALITY ASSURANCE

Retain first paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Division 1 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

A. Testing Agency Qualifications:  Member company of NETA or an NRTL.

1. Testing Agency's Field Supervisor:  Currently certified by NETA to supervise on-site testing.

B. Source Limitations:  Obtain enclosed switches and circuit breakers, overcurrent protective devices, components, and accessories, within same product category, from single source from single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

C. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for enclosed switches and circuit breakers, including clearances between enclosures, and adjacent surfaces and other items.  Comply with indicated maximum dimensions.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

E. Comply with NFPA 70.

1.7 PROJECT CONDITIONS

Specify unusual environmental or service conditions in first paragraph below.  For equipment installed outdoors, indicate maximum and minimum ambient temperature and expected humidity range.  For additional ambient compensation requirements for fuses, see Editing Instruction No. 5 in the Evaluations.

A. Environmental Limitations:  Rate equipment for continuous operation under the following conditions unless otherwise indicated:

1. Ambient Temperature:  Not less than minus 22 deg F (minus 30 deg C) and not exceeding 104 deg F (40 deg C).

2. Altitude:  Not exceeding 6600 feet (2010 m).

Retain paragraph below if interruption of existing electric service is required.

B. Interruption of Existing Electric Service:  Do not interrupt electric service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electric service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [seven] <Insert number> days in advance of proposed interruption of electric service.

2. Indicate method of providing temporary electric service.

3. Do not proceed with interruption of electric service without [Architect's] [Construction Manager's] [Owner's] written permission.

4. Comply with NFPA 70E.

1.8 COORDINATION

Revise this article to delete or insert types of construction and encumbrances that affect switch and circuit-breaker installation.

A. Coordinate layout and installation of switches, circuit breakers, and components with equipment served and adjacent surfaces.  Maintain required workspace clearances and required clearances for equipment access doors and panels.

1.9 EXTRA MATERIALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Coordinate first subparagraph below with Division 16 Section "Fuses" for quantities of spare fuses and spare-fuse cabinet to be provided.

1. Fuses:  Equal to [10] <Insert number> percent of quantity installed for each size and type, but no fewer than [three] <Insert number> of each size and type.

2. Fuse Pullers:  [Two] <Insert number> for each size and type.

3. <Insert extra materials>.

PART 2 -  PRODUCTS

2.1 FUSIBLE SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Show pole quantities and voltage and ampere ratings of switches on Drawings.  In first two paragraphs below, Type GD is for switches for light-commercial applications, 240-V ac, 30 to 600 A; Type HD is for all other single-throw switch uses.  See Editing Instruction No. 2 in the Evaluations.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Division 16 Section "Fuses." Show fuse ampere ratings on Drawings.  General-duty switches are available with plug fuse interiors.

C. Type GD, General Duty, Single Throw, 240-V ac, 800 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with [cartridge] [plug] fuse interiors to accommodate [specified] [indicated] fuses, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Division 16 Section "Fuses." Show fuse ampere ratings on Drawings.

D. Type HD, Heavy Duty, Single Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

Some listed manufacturers offer the six-pole switch in amperage ratings higher than those in first paragraph below.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Division 16 Section "Fuses." Show fuse ampere ratings on Drawings.

E. Type HD, Heavy Duty, Six Pole, Single Throw, [240] [600]-V ac, 200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Division 16 Section "Fuses." Show fuse ampere ratings on Drawings.

F. Type HD, Heavy Duty, Double Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

G. Accessories:

Retain subparagraphs below with applicable switch paragraphs above.  Verify that accessories specified are available and applicable to switch types and ratings in this article.

1. Equipment Ground Kit:  Internally mounted and labeled for copper and aluminum ground conductors.

2. Neutral Kit:  Internally mounted; insulated, capable of being grounded and bonded; labeled for copper and aluminum neutral conductors.

3. Isolated Ground Kit:  Internally mounted; insulated, capable of being grounded and bonded; labeled for copper and aluminum neutral conductors.

4. Class R Fuse Kit:  Provides rejection of other fuse types when Class R fuses are specified.

5. Auxiliary Contact Kit:  [One] [Two] NO/NC (Form "C") auxiliary contact(s), arranged to activate before switch blades open.

6. Hookstick Handle:  Allows use of a hookstick to operate the handle.

See Editing Instruction No. 7 in the Evaluations for guidance on using mechanical versus compression lugs.  Some size lugs (and lugs in other than NEMA 250, Type 1 and NEMA 250, Type 3R enclosures) are frequently available only for copper conductors; coordinate with manufacturers' literature.

7. Lugs:  [Mechanical] [Compression] type, suitable for number, size, and conductor material.

8. Service-Rated Switches:  Labeled for use as service equipment.

Retain subparagraph below if retaining "Auxiliary Contact Kit" Subparagraph above and if remote-control power for remote indication is not specified in other Sections.  See "Control Power Options" Article in the Evaluations for various sources available for control power.  Although other voltages are available, the Section Text includes only those that are most frequently encountered and listed in manufacturers' literature.  Integrally mounted control power is not available in safety switches.

9. Accessory Control Power Voltage:  Remote mounted and powered; [24-V ac] [120-V ac] [208-V ac] [240-V ac] [6-V dc] [12-V dc] [24-V dc].

2.2 NONFUSIBLE SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Show pole quantities and voltage and ampere ratings of switches on Drawings.  In first two paragraphs below, Type GD is for switches for light-commercial applications, 240-V ac, 30 to 600 A; Type HD is for all other single-throw switch uses.  See Editing Instruction No. 2 in the Evaluations.

C. Type GD, General Duty, Single Throw, 600 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

D. Type HD, Heavy Duty, Single Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

Some listed manufacturers offer the six-pole switch in amperage ratings higher than those in first paragraph below.

E. Type HD, Heavy Duty, Six Pole, Single Throw, [240] [600]-V ac, 200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

F. Type HD, Heavy Duty, Double Throw, [240] [600]-V ac, 1200 A and Smaller:  UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

G. Accessories:

Retain subparagraphs below with applicable switch paragraphs above.  Verify that accessories specified are available and applicable to switch types and ratings in this article.

1. Equipment Ground Kit:  Internally mounted and labeled for copper and aluminum ground conductors.

2. Neutral Kit:  Internally mounted; insulated, capable of being grounded and bonded; labeled for copper and aluminum neutral conductors.

3. Isolated Ground Kit:  Internally mounted; insulated, capable of being grounded and bonded; labeled for copper and aluminum neutral conductors.

4. Auxiliary Contact Kit:  [One] [Two] NO/NC (Form "C") auxiliary contact(s), arranged to activate before switch blades open.

5. Hookstick Handle:  Allows use of a hookstick to operate the handle.

See Editing Instruction No. 7 in the Evaluations for guidance on using mechanical versus compression lugs.  Some size lugs (and lugs in other than NEMA 250, Type 1 and NEMA 250, Type 3R enclosures) are frequently available only for copper conductors; coordinate with manufacturers' literature.

6. Lugs:  [Mechanical] [Compression] type, suitable for number, size, and conductor material.

Retain subparagraph below if retaining "Auxiliary Contact Kit" Subparagraph above and if remote-control power for remote indication is not specified in other Sections.  See "Control Power Options" Article in the Evaluations for various sources available for control power.  Although other voltages are available, the Section Text includes only those that are most frequently encountered and listed in manufacturers' literature.  Integrally mounted control power is not available in safety switches.

7. Accessory Control Power Voltage:  Remote mounted and powered; [24-V ac] [120-V ac] [208-V ac] [240-V ac] [6-V dc] [12-V dc] [24-V dc].

2.3 RECEPTACLE SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Listed manufacturers offer similar but different options for voltage and ampere ratings and the make and model of receptacles available for factory installation on their switches.  See Editing Instruction No. 3 in the Evaluations.  Not all listed voltage and ampere ratings and enclosure types listed in "Enclosures" Article are available from all listed manufacturers.

Show pole quantities and voltage and ampere ratings of switches on Drawings.  Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Division 16 Section "Fuses." Show fuse ampere ratings on Drawings.

C. Type HD, Heavy-Duty, Single-Throw Fusible Switch:  [240] [600]-V ac, [30] [60] [100] A; UL 98 and NEMA KS 1; horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses; lockable handle with capability to accept three padlocks; interlocked with cover in closed position.

D. Type HD, Heavy-Duty, Single-Throw Nonfusible Switch:  [240] [600]-V ac, [30] [60] [100] A; UL 98 and NEMA KS 1; horsepower rated, lockable handle with capability to accept three padlocks; interlocked with cover in closed position.

E. Interlocking Linkage:  Provided between the receptacle and switch mechanism to prevent inserting or removing plug while switch is in the on position, inserting any plug other than specified, and turning switch on if an incorrect plug is inserted or correct plug has not been fully inserted into the receptacle.

F. Receptacle:  Polarized, three-phase, four-wire receptacle (fourth wire connected to enclosure ground lug).

If more than one type or rating of receptacle-switch combination is required, consider showing location of each on Drawings and deleting subparagraph below; otherwise, insert required information.

1. Receptacle Manufacturer and Catalog Number:  <Insert manufacturer and catalog number>.

2.4 SHUNT TRIP SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cooper Bussmann, Inc.

2. Ferraz Shawmut, Inc.

3. Littelfuse, Inc.

4. <Insert manufacturer's name>.

Show voltage and ampere ratings of shunt trip switches and fuses on Drawings.  See Editing Instruction No. 4 and "Shunt Trip Switches" Article in the Evaluations for guidance on using shunt trip switches.

Retain option in first paragraph below if shunt trip switches are used as elevator shunt trip disconnects per ASME A17.1 and NFPA 70.

C. General Requirements:  Comply with[ ASME A17.1,] UL 50, and UL 98, with 200-kA interrupting and short-circuit current rating when fitted with Class J fuses.

D. Switches:  Three-pole, horsepower rated, with integral shunt trip mechanism and Class J fuse block; lockable handle with capability to accept three padlocks; interlocked with cover in closed position.

E. Control Circuit:  120-V ac; obtained from [integral control power transformer, with primary and secondary fuses,] <Insert source of control power> with a control power [transformer] [source] of enough capacity to operate shunt trip, connected pilot, and indicating and control devices.

F. Accessories:

Not all accessories listed in subparagraphs below are available from every listed manufacturer.  Verify availability and unique characteristics with manufacturers selected.

1. Oiltight key switch for key-to-test function.

2. Oiltight [red] [green] [white] [yellow] ON pilot light.

3. Isolated neutral lug; [100] [200] percent rating.

Retain first subparagraph below if using switch for hydraulic elevators with automatic recall.  Show required interface wiring on Drawings.

4. Mechanically interlocked auxiliary contacts that change state when switch is opened and closed.

5. Form C alarm contacts that change state when switch is tripped.

Retain two subparagraphs below when interfacing elevators with the facility fire-alarm system is required.  In first subparagraph, if retaining 24-V dc coil option, a separate 24-V dc source and an initiating contact must be provided by the facility fire-alarm system.

6. Three-pole, double-throw, fire-safety and alarm relay; [120-V ac] [24-V dc] coil voltage.

7. Three-pole, double-throw, fire-alarm voltage monitoring relay complying with NFPA 72.

2.5 MOLDED-CASE CIRCUIT BREAKERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Show pole quantities and voltage and ampere ratings of MCCBs and switches on Drawings.  See Editing Instruction No. 6 in the Evaluations.

C. General Requirements:  Comply with UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents.

D. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

E. Adjustable, Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

F. Electronic Trip Circuit Breakers:  Field-replaceable rating plug, rms sensing, with the following field-adjustable settings:

Retain one or more of four subparagraphs below and coordinate required adjustable settings with Division 16 Section "Overcurrent Protective Device Coordination."

1. Instantaneous trip.

2. Long- and short-time pickup levels.

3. Long- and short-time time adjustments.

4. Ground-fault pickup level, time delay, and I2t response.

G. Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller, and let-through ratings less than NEMA FU 1, RK-5.

H. Integrally Fused Circuit Breakers:  Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker and trip activation on fuse opening or on opening of fuse compartment door.

Retain first paragraph below for GFCI circuit breakers for personnel ground-fault protection as required by NFPA 70; retain second paragraph for equipment ground-fault protection (e.g., for self-limiting heat trace cables) as required by NFPA 70.  GFCI and GFEP circuit breakers are only available fully rated up to interrupting ratings of 22 kA.

I. Ground-Fault, Circuit-Interrupter (GFCI) Circuit Breakers:  Single- and two-pole configurations with Class A ground-fault protection (6-mA trip).

J. Ground-Fault, Equipment-Protection (GFEP) Circuit Breakers:  With Class B ground-fault protection (30-mA trip).

K. Features and Accessories:

Not all features, accessories, and options in subparagraphs below are available for every rating and from every listed manufacturer.  Verify availability and unique characteristics with manufacturers selected.

1. Standard frame sizes, trip ratings, and number of poles.

See Editing Instruction No. 7 in the Evaluations for guidance on using mechanical versus compression lugs.

2. Lugs:  [Mechanical] [Compression] type, suitable for number, size, trip ratings, and conductor material.

3. Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge lighting circuits.

Retain first option in first subparagraph below for solid-state trip units; retain second option for thermal-magnetic trip units.

4. Ground-Fault Protection:  Comply with UL 1053; [integrally mounted, self-powered] [remote-mounted and powered] type with mechanical ground-fault indicator; relay with adjustable pickup and time-delay settings, push-to-test feature, internal memory, and shunt trip unit; and three-phase, zero-sequence current transformer/sensor.

5. Communication Capability:  [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system, specified in Division 16 Section "Electrical Power Monitoring and Control."

6. Shunt Trip:  Trip coil energized from separate circuit, with coil-clearing contact.

An optional time-delay unit, which allows an adjustable time delay in release of the trip coil for overriding momentary fluctuations, is available for the undervoltage trip unit in first subparagraph below.

7. Undervoltage Trip:  Set to operate at 35 to 75 percent of rated voltage without intentional time delay.

8. Auxiliary Contacts:  [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.

9. Alarm Switch:  One [NO] [NC] contact that operates only when circuit breaker has tripped.

10. Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

Retain first option in first subparagraph below for solid-state trip units; retain second option for thermal-magnetic trip units.

11. Zone-Selective Interlocking:  Integral with [electronic] [ground-fault] trip unit; for interlocking ground-fault protection function.

12. Electrical Operator:  Provide remote control for on, off, and reset operations.

Retain subparagraph below if retaining options requiring integral or remote-control power in subparagraphs above and if control power for remote indication or operation is not specified in other Sections.  See "Control Power Options" Article in the Evaluations for various sources available for control power.  Although other voltages are available, the Section Text includes only those that are most frequently encountered and listed in manufacturers' literature.  First option below may not be available in all voltages; coordinate with manufacturers' literature.

13. Accessory Control Power Voltage:  [Integrally mounted, self-powered] [Remote mounted and powered]; [24-V ac] [120-V ac] [208-V ac] [240-V ac] [6-V dc] [12-V dc] [24-V dc].

2.6 MOLDED-CASE SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

C. General Requirements:  MCCB with fixed, high-set instantaneous trip only, and short-circuit withstand rating equal to equivalent breaker frame size interrupting rating.

D. Features and Accessories:

Not all features, accessories, and options listed in subparagraphs below are available for every rating and from every listed manufacturer.  Verify availability and unique characteristics with manufacturers selected.

1. Standard frame sizes and number of poles.

See Editing Instruction No. 7 in the Evaluations for guidance on using mechanical versus compression lugs.

2. Lugs:  [Mechanical] [Compression] type, suitable for number, size, trip ratings, and conductor material.

3. Ground-Fault Protection:  Comply with UL 1053; remote-mounted and powered type with mechanical ground-fault indicator; relay with adjustable pickup and time-delay settings, push-to-test feature, internal memory, and shunt trip unit; and three-phase, zero-sequence current transformer/sensor.

4. Shunt Trip:  Trip coil energized from separate circuit, with coil-clearing contact.

An optional time-delay unit, which allows an adjustable time delay in release of the trip coil for overriding momentary fluctuations, is available for the undervoltage trip unit in first subparagraph below.

5. Undervoltage Trip:  Set to operate at 35 to 75 percent of rated voltage without intentional time delay.

6. Auxiliary Contacts:  [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic switch contacts, "b" contacts operate in reverse of switch contacts.

7. Alarm Switch:  One [NO] [NC] contact that operates only when switch has tripped.

8. Key Interlock Kit:  Externally mounted to prohibit switch operation; key shall be removable only when switch is in off position.

9. Zone-Selective Interlocking:  Integral with ground-fault shunt trip unit; for interlocking ground-fault protection function.

10. Electrical Operator:  Provide remote control for on, off, and reset operations.

Retain subparagraph below if retaining options requiring integral or remote-control power in subparagraphs above and if control power for remote indication or operation is not specified in other Sections.  See "Control Power Options" Article in the Evaluations for various sources available for control power.  Although other voltages are available, the Section Text includes only those that are most frequently encountered and listed in manufacturers' literature.  First option below may not be available in all voltages; coordinate with manufacturers' literature.

11. Accessory Control Power Voltage:  [Integrally mounted, self-powered] [Remote mounted and powered]; [24-V ac] [120-V ac] [208-V ac] [240-V ac] [6-V dc] [12-V dc] [24-V dc].

2.7 ENCLOSURES

A. Enclosed Switches and Circuit Breakers:  NEMA AB 1, NEMA KS 1, NEMA 250, and UL 50, to comply with environmental conditions at installed location.

See "Enclosures" Article in the Evaluations for discussion of enclosure types.  Coordinate subparagraphs below with Drawings by identifying the designated areas on plans or by including the required enclosure types.  Availability of some enclosure types is limited by type of switch or circuit breaker; consult manufacturers for availability of, and limitations on, other than NEMA 250, Type 1 enclosures.  General-duty switches are generally only available in NEMA 250, Type 1 or NEMA 250, Type 3R enclosures.

1. Indoor, Dry and Clean Locations:  NEMA 250, [Type 1] <Insert type>.

2. Outdoor Locations:  NEMA 250, [Type 3R] <Insert type>.

3. [Kitchen] [Wash-Down] Areas:  NEMA 250, [Type 4X] <Insert type>, [stainless steel] <Insert material>.

4. Other Wet or Damp, Indoor Locations:  NEMA 250, [Type 4] <Insert type>.

5. Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids:  NEMA 250, Type 12.

Retain one of two options in subparagraph below to comply with the division and group listing of the environment.  Frequently, one enclosure type will accommodate more than one hazardous environment rating.  Consult manufacturers for availability of, and limitations on, hazardous environment enclosures.  These enclosures do not apply to shunt trip or receptacle switches as specified in the Section Text.

6. Hazardous Areas Indicated on Drawings:  NEMA 250, [Type 7] [Type 9] <Insert type>.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine elements and surfaces to receive enclosed switches and circuit breakers for compliance with installation tolerances and other conditions affecting performance of the Work.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install individual wall-mounted switches and circuit breakers with tops at uniform height unless otherwise indicated.

Retain first paragraph below if seismic controls are required for Project.  Coordinate with Drawings.

B. Comply with mounting and anchoring requirements specified in Division 16 Section "Vibration and Seismic Controls for Electrical Systems."

C. Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

D. Install fuses in fusible devices.

E. Comply with NECA 1.

3.3 IDENTIFICATION

A. Comply with requirements in Division 16 Section "Electrical Identification."

1. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs.

2. Label each enclosure with engraved metal or laminated-plastic nameplate.

3.4 FIELD QUALITY CONTROL

Retain one of first three paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second or third paragraph, retain "Field quality-control reports" Paragraph in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

C. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first two paragraphs below to describe tests and inspections to be performed.

D. Acceptance Testing Preparation:

1. Test insulation resistance for each enclosed switch and circuit breaker, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

E. Tests and Inspections:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

3. Perform the following infrared scan tests and inspections and prepare reports:

a. Initial Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each enclosed switch and circuit breaker.  Remove front panels so joints and connections are accessible to portable scanner.

b. Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan of each enclosed switch and circuit breaker 11 months after date of Substantial Completion.

c. Instruments and Equipment:  Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

4. Test and adjust controls, remote monitoring, and safeties.  Replace damaged and malfunctioning controls and equipment.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

F. Enclosed switches and circuit breakers will be considered defective if they do not pass tests and inspections.

Retain paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

G. Prepare test and inspection reports, including a certified report that identifies enclosed switches and circuit breakers and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.5 ADJUSTING

A. Adjust moving parts and operable components to function smoothly, and lubricate as recommended by manufacturer.

Retain option in paragraph below if the indicated Section is included in the Contract Documents.

B. Set field-adjustable circuit-breaker trip ranges[ as specified in Division 16 Section "Overcurrent Protective Device Coordination"].

END OF SECTION 16410

ENCLOSED SWITCHES AND CIRCUIT BREAKERS
16410 - 1

