Copyright 2003 AIA
MASTERSPEC Full Length
06/03 (R 06/06)

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16511 - INTERIOR LIGHTING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.  ASHRAE/IESNA 90.1-2004, Section 9, "Lighting," sets minimum interior and exterior lighting power densities and minimum requirements for lighting controls.  The selection of the lamp and ballast as a system is an important design decision to optimize energy efficiency of the lighting system.

A reduction in lighting energy usage can be combined with other energy-conserving measures to meet the requirements of LEED-NC Credit EA 1.

LEED-NC Credit SS 8 requires that the angle of the maximum candela of any of the interior light fixtures not spill through any of the building's transparent and translucent surfaces to the exterior areas, and that all interior, nonemergency lights be automatically turned off after-hours with manual override capabilities for after-hours use.  Credit SS 8 also sets requirements for exterior lighting.  See Division 16 Section "Exterior Lighting."

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Interior lighting fixtures, lamps, and ballasts.

2. Emergency lighting units.

3. Exit signs.

4. Lighting fixture supports.

5. Retrofit kits for fluorescent lighting fixtures.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 13 Section "Lighting Controls" for manual or programmable control systems with low-voltage control wiring or data communication circuits.

2. Division 16 Section "Wiring Devices" for manual wall-box dimmers for incandescent lamps.

3. Division 16 Section "Lighting Control Devices" for automatic control of lighting, including time switches, photoelectric relays, occupancy sensors, and multipole lighting relays and contactors.

4. Division 16 Section "Stage Lighting" for theatrical lighting fixtures and their controls.

5. Division 16 Section "Dimming Controls" for architectural dimming systems.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. BF:  Ballast factor.

B. CRI:  Color-rendering index.

C. CU:  Coefficient of utilization.

D. HID:  High-intensity discharge.

E. LER:  Luminaire efficacy rating.

F. Luminaire:  Complete lighting fixture, including ballast housing if provided.

G. RCR:  Room cavity ratio.

1.4 SUBMITTALS

A. Product Data:  For each type of lighting fixture, arranged in order of fixture designation.  Include data on features, accessories, finishes, and the following:

1. Physical description of lighting fixture including dimensions.

2. Emergency lighting units including battery and charger.

3. Ballast.

4. Energy-efficiency data.

Retain first two subparagraphs below for projects with air-handling lighting fixtures.

5. Air and Thermal Performance Data:  For air-handling lighting fixtures.  Furnish data required in "Submittals" Article in Division 15 Section "Diffusers, Registers, and Grilles."

6. Sound Performance Data:  For air-handling lighting fixtures.  Indicate sound power level and sound transmission class in test reports certified according to standards specified in Division 15 Section "Diffusers, Registers, and Grilles."

7. Life, output, and energy-efficiency data for lamps.

8. Photometric data, in IESNA format, based on laboratory tests of each lighting fixture type, outfitted with lamps, ballasts, and accessories identical to those indicated for the lighting fixture as applied in this Project.

Retain one of two subparagraphs below.  Retain first subparagraph if photometric data for one or more lighting fixtures are to be based on independent laboratory tests; coordinate with Interior Lighting Fixture Schedule on Drawings or with Part 2 "Requirements for Individual Lighting Fixtures" Article to indicate which units are required to meet this requirement.  Retain second subparagraph if photometric data based on testing by accredited manufacturers' laboratories are considered adequate for all interior fixtures in this Project.  See Evaluations.

a. For indicated fixtures, photometric data shall be certified by a qualified independent testing agency.  Photometric data for remaining fixtures shall be certified by the manufacturer.

b. Photometric data shall be certified by a manufacturer's laboratory with a current accreditation under the National Voluntary Laboratory Accreditation Program (NVLAP) for Energy Efficient Lighting Products.

Retain paragraph and subparagraph below for custom lighting fixtures.

B. Shop Drawings:  Show details of nonstandard or custom lighting fixtures.  Indicate dimensions, weights, methods of field assembly, components, features, and accessories.

1. Wiring Diagrams:  Power[ and control] wiring.

Retain paragraph and subparagraphs below if Drawings do not include comprehensive reflected ceiling plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plan(s) and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Revise subparagraphs and associated subparagraphs below to suit Project.

1. Lighting fixtures.

2. Suspended ceiling components.

3. Structural members to which suspension systems for lighting fixtures will be attached.

4. Other items in finished ceiling including the following:

a. Air outlets and inlets.

b. Speakers.

c. Sprinklers.

d. Smoke and fire detectors.

e. Occupancy sensors.

f. Access panels.

g. <Insert item.>

5. Perimeter moldings.

Retain first paragraph and subparagraphs below if Samples of interior lighting fixtures are required for verification purposes.  Revise if sample requirements are indicated in other than Interior Lighting Fixture Schedule.  As an alternative, add a list of fixture types for sample submission.

D. Samples for Verification:  Interior lighting fixtures designated for sample submission in Interior Lighting Fixture Schedule.  Each sample shall include the following:

1. Lamps:  Specified units installed.

2. Accessories:  Cords and plugs.

E. Product Certificates:  For each type of ballast for bi-level and dimmer-controlled fixtures, signed by product manufacturer.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

F. Qualification Data:  For agencies providing photometric data for lighting fixtures.

G. Field quality-control test reports.

H. Operation and Maintenance Data:  For lighting equipment and fixtures to include in emergency, operation, and maintenance manuals.

I. Warranties:  Special warranties specified in this Section.

1.5 QUALITY ASSURANCE

Retain one or both of first two paragraphs below to specify qualifications for laboratories providing photometric data to be submitted for lighting fixtures.

A. Luminaire Photometric Data Testing Laboratory Qualifications:  Provided by manufacturers' laboratories that are accredited under the National Volunteer Laboratory Accreditation Program for Energy Efficient Lighting Products.

B. Luminaire Photometric Data Testing Laboratory Qualifications:  Provided by an independent agency, with the experience and capability to conduct the testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

D. Comply with NFPA 70.

Retain paragraph below if FMG compliance is required.  Coordinate with Drawings.

E. FMG Compliance:  Lighting fixtures for hazardous locations shall be listed and labeled for indicated class and division of hazard by FMG.

Mockup lighting fixtures are often part of a typical room or module mockup used to evaluate and demonstrate an overall interior concept, not just lighting.  Delete paragraph and subparagraphs below if not required.  If retaining, indicate location, type, and other details of mockups on Drawings.  Revise wording if only one mockup is required.

F. Mockups:  Provide interior lighting fixtures for room or module mockups, complete with power and control connections.

1. Obtain Architect's approval of fixtures for mockups before starting installations.

2. Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

Retain subparagraph below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 1 Section "Quality Requirements" for demolishing and removing mockups when directed, unless otherwise indicated.

3. Approved fixtures in mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

1.6 COORDINATION

Retain this Article if Coordination Drawings are required.

A. Coordinate layout and installation of lighting fixtures and suspension system with other construction that penetrates ceilings or is supported by them, including HVAC equipment, fire-suppression system, and partition assemblies.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

Retain paragraph and subparagraphs below for rechargeable batteries for emergency lighting equipment.

A. Special Warranty for Emergency Lighting Batteries:  Manufacturer's standard form in which manufacturer of battery-powered emergency lighting unit agrees to repair or replace components of rechargeable batteries that fail in materials or workmanship within specified warranty period.

Subparagraphs below are examples only.  Verify available warranties for units and components and insert number below.  Coordinate with Part 2 article that specifies emergency lighting units.

1. Warranty Period for Emergency Lighting Unit Batteries:  [10] <Insert number> years from date of Substantial Completion.  Full warranty shall apply for first year, and prorated warranty for the remaining nine years.

2. Warranty Period for Emergency Fluorescent Ballast[ and] [Self-Powered Exit Sign] Batteries:  [Seven] <Insert number> years from date of Substantial Completion.  Full warranty shall apply for first year, and prorated warranty for the remaining six years.

Retain paragraph and subparagraphs below for fluorescent ballasts.  Warranty below is an example only.  See Editing Instruction No. 4 in the Evaluations for discussion of ballast and lamp warranties.

B. Special Warranty for Ballasts:  Manufacturer's standard form in which ballast manufacturer agrees to repair or replace ballasts that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period for Electronic Ballasts:  [Five] <Insert number> years from date of Substantial Completion.

Retain subparagraph below if electromagnetic ballasts are specified.

2. Warranty Period for Electromagnetic Ballasts:  [Three] <Insert number> years from date of Substantial Completion.

Retain paragraph and subparagraph below for special warranty for T8 fluorescent lamps.

C. Special Warranty for [T5] [T8] [T5 and T8] Fluorescent Lamps:  Manufacturer's standard form, made out to Owner and signed by lamp manufacturer agreeing to replace lamps that fail in materials or workmanship, f.o.b. the nearest shipping point to Project site, within specified warranty period indicated below.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period:  [One] [Two] <Insert number> year(s) from date of Substantial Completion.

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.  Quantities indicated are examples only.

1. Lamps:  [10 for every 100] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

2. Plastic Diffusers and Lenses:  [1 for every 100] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

3. Battery and Charger Data:  [One] <Insert number> for each emergency lighting unit.

4. Ballasts:  [1 for every 100] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

5. Globes and Guards:  [1 for every 20] <Insert quantity> of each type and rating installed.  Furnish at least one of each type.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

Edit this Article with other Part 2 articles or with Interior Lighting Fixture Schedule on Drawings in which manufacturers and products are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers," "Manufacturers," and "Basis-of-Design Product" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

Retain paragraph above if lighting fixtures are described in this Section; retain paragraph below if lighting fixtures are scheduled on Drawings.  See sample schedule in the Evaluations.

B. In Interior Lighting Fixture Schedule where titles below are column or row headings that introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

3. Basis-of-Design Product:  The design for each lighting fixture is based on the product named.  Subject to compliance with requirements, provide either the named product or a comparable product by one of the other manufacturers specified.

2.2 LIGHTING FIXTURES AND COMPONENTS, GENERAL REQUIREMENTS

A. Recessed Fixtures:  Comply with NEMA LE 4 for ceiling compatibility for recessed fixtures.

B. Incandescent Fixtures:  Comply with UL 1598.  Where LER is specified, test according to NEMA LE 5A.

C. Fluorescent Fixtures:  Comply with UL 1598.  Where LER is specified, test according to NEMA LE 5 and NEMA LE 5A as applicable.

D. HID Fixtures:  Comply with UL 1598.  Where LER is specified, test according to NEMA LE 5B.

E. Metal Parts:  Free of burrs and sharp corners and edges.

F. Sheet Metal Components:  Steel, unless otherwise indicated.  Form and support to prevent warping and sagging.

G. Doors, Frames, and Other Internal Access:  Smooth operating, free of light leakage under operating conditions, and designed to permit relamping without use of tools.  Designed to prevent doors, frames, lenses, diffusers, and other components from falling accidentally during relamping and when secured in operating position.

H. Reflecting surfaces shall have minimum reflectance as follows, unless otherwise indicated:

1. White Surfaces:  85 percent.

2. Specular Surfaces:  83 percent.

3. Diffusing Specular Surfaces:  75 percent.

4. Laminated Silver Metallized Film:  90 percent.

I. Plastic Diffusers, Covers, and Globes:

1. Acrylic Lighting Diffusers:  100 percent virgin acrylic plastic.  High resistance to yellowing and other changes due to aging, exposure to heat, and UV radiation.

For K12 pattern acrylic lenses, thickness of 0.125 inch (3.175 mm) is most common for specification grade fixtures.  Thicknesses of 0.100 and 0.125 inch (2.54 and 3.175 mm) are commonly available.

a. Lens Thickness:  At least [0.125 inch (3.175 mm)] <Insert thickness> minimum unless different thickness is indicated.

b. UV stabilized.

2. Glass:  Annealed crystal glass, unless otherwise indicated.

Retain first paragraph below for special applications where freedom from conducted electromagnetic interference is critical.  Coordinate with Interior Lighting Fixture Schedule on Drawings or with "Requirements for Individual Lighting Fixtures" Article.

J. Electromagnetic-Interference Filters:  Factory installed to suppress conducted electromagnetic-interference as required by MIL-STD-461E.  Fabricate lighting fixtures with one filter on each ballast indicated to require a filter.

K. Air-Handling Fluorescent Fixtures:  For use with plenum ceiling for air return and heat extraction and for attaching an air-diffuser-boot assembly specified in Division 15 Section "Diffusers, Registers, and Grilles."

1. Air Supply Units:  Slots in one or both side trims join with air-diffuser-boot assemblies.

2. Heat Removal Units:  Air path leads through lamp cavity.

3. Combination Heat Removal and Air Supply Unit:  Heat is removed through lamp cavity at both ends of the fixture door with air supply same as for air supply units.

4. Dampers:  Operable from outside fixture for control of return-air volume.

5. Static Fixture:  Air supply slots are blanked off, and fixture appearance matches active units.

2.3 BALLASTS FOR LINEAR FLUORESCENT LAMPS

Select ballast type in first paragraph below to specify the default ballast type for linear fluorescent lamps.  Note that most projects will have some applications for linear fixtures requiring ballasts other than the default type selected below.  For such fixtures, indicate the ballast type in Interior Lighting Fixture Schedule on Drawings or in "Requirements for Individual Lighting Fixtures" Article.  See Editing Instruction No. 9 in the Evaluations for discussion of instant-, rapid-, and programmed-start ballasts.

A. Electronic Ballasts:  Comply with ANSI C82.11; [instant] [programmed]-start type, unless otherwise indicated, and designed for type and quantity of lamps served.  Ballasts shall be designed for full light output unless dimmer or bi-level control is indicated.

1. Sound Rating:  [A] [A, except B for T12/HO and T12/Slimline lamp ballasts].

See Evaluations for discussion of harmonic considerations.

2. Total Harmonic Distortion Rating:  Less than [10] [20] percent.

3. Transient Voltage Protection:  IEEE C62.41, Category A or better.

Consider specifying the higher frequency in subparagraph below if fixtures with default ballasts are used in proximity to infrared sensors.

4. Operating Frequency:  [20] [42] <Insert value> kHz or higher.

See Editing Instruction No. 6 in the Evaluations for discussion of lamp current crest factor.

5. Lamp Current Crest Factor:  [1.7] <Insert value> or less.

6. BF:  0.85 or higher.

7. Power Factor:  [0.95] [0.98] or higher.

Delete subparagraph below if instant start is selected as the default ballast type, since parallel lamp operation is standard with that ballast type.  Retain if default ballast is program start and it is important for surviving lamps to operate when one lamp served by a ballast has failed.  There may be a cost premium for this little-used option for program-start ballasts.

8. Parallel Lamp Circuits:  Multiple lamp ballasts shall comply with ANSI C 82.11 and shall be connected to maintain full light output on surviving lamps if one or more lamps fail.

B. Electronic Programmed-Start Ballasts for [T5] [T5HO] [T5 and T5HO] Lamps:  Comply with ANSI C82.11 and the following:

1. Lamp end-of-life detection and shutdown circuit for T5 diameter lamps.

2. Automatic lamp starting after lamp replacement.

3. Sound Rating:  A.

4. Total Harmonic Distortion Rating:  Less than 20 percent.

5. Transient Voltage Protection:  IEEE C62.41, Category A or better.

6. Operating Frequency:  20 kHz or higher.

7. Lamp Current Crest Factor:  1.7 or less.

8. BF:  0.95 or higher, unless otherwise indicated.

9. Power Factor:  [0.95] [0.98] or higher.

C. Electromagnetic Ballasts:  Comply with ANSI C82.1; energy saving, high-power factor, Class P, and having automatic-reset thermal protection.

1. Ballast Manufacturer Certification:  Indicated by label.

Retain first paragraph below if design requires ballasts in some fixtures to serve lamps in other fixtures.  Indicate fixture types to which this requirement applies in Interior Lighting Fixture Schedule on Drawings or in "Requirements for Individual Lighting Fixtures" Article, and indicate connections on lighting plans.

D. Single Ballasts for Multiple Lighting Fixtures:  Factory-wired with ballast arrangements and bundled extension wiring to suit final installation conditions without modification or rewiring in the field.

E. Ballasts for Low-Temperature Environments:

Consider retaining electromagnetic ballasts in first subparagraph below if lamp starting and operating temperature near 0 deg F (minus 17 deg C) is a critical requirement.  Verify with manufacturers the compatibility of ballasts with indicated lamps for low-temperature operation.

1. Temperatures 0 Deg F (Minus 17 Deg C) and Higher:  [Electronic] [Electromagnetic] [Electronic or electromagnetic] type rated for 0 deg F (minus 17 deg C) starting and operating temperature with indicated lamp types.

2. Temperatures Minus 20 Deg F (Minus 29 Deg C) and Higher:  Electromagnetic type designed for use with indicated lamp types.

Consider retaining paragraph below if some environments in Project have higher than normal sensitivity to electromagnetic interference.  Coordinate with Drawings.  Products for consumer use (usually household) must satisfy more stringent electromagnetic interference limitations than those for nonconsumer environments.  See "Product Selection and Application Considerations" Article in the Evaluations for more information.

F. Ballasts for Low Electromagnetic-Interference Environments:  Comply with 47 CFR, Chapter 1, Part 18, Subpart C, for limitations on electromagnetic and radio-frequency interference for consumer equipment.

Coordinate two paragraphs and associated subparagraphs below with submittal requirements for certificates.

G. Ballasts for Dimmer-Controlled Lighting Fixtures:  Electronic type.

1. Dimming Range:  100 to [5] <Insert value> percent of rated lamp lumens.

2. Ballast Input Watts:  Can be reduced to [20] <Insert value> percent of normal.

3. Compatibility:  Certified by manufacturer for use with specific dimming control system and lamp type indicated.

H. Ballasts for Bi-Level Controlled Lighting Fixtures:  Electronic type.

1. Operating Modes:  Ballast circuit and leads provide for remote control of the light output of the associated lamp between high- and low-level and off.

a. High-Level Operation:  100 percent of rated lamp lumens.

b. Low-Level Operation:  [30] [50] percent of rated lamp lumens.

2. Ballast shall provide equal current to each lamp in each operating mode.

3. Compatibility:  Certified by manufacturer for use with specific bi-level control system and lamp type indicated.

2.4 BALLASTS FOR COMPACT FLUORESCENT LAMPS

A. Description:  Electronic programmed rapid-start type, complying with ANSI C 82.11, designed for type and quantity of lamps indicated. Ballast shall be designed for full light output unless dimmer or bi-level control is indicated:

1. Lamp end-of-life detection and shutdown circuit.

2. Automatic lamp starting after lamp replacement.

3. Sound Rating:  A.

4. Total Harmonic Distortion Rating:  Less than 20 percent.

5. Transient Voltage Protection:  IEEE C62.41, Category A or better.

6. Operating Frequency:  20 kHz or higher.

7. Lamp Current Crest Factor:  1.7 or less.

8. BF:  0.95 or higher, unless otherwise indicated.

9. Power Factor:  [0.95] [0.98] or higher.

See Evaluations for discussion of CFR compliance required in first subparagraph below.

10. Interference:  Comply with 47 CFR, Chapter 1, Part 18, Subpart C, for limitations on electromagnetic and radio-frequency interference for nonconsumer equipment.

11. Ballast Case Temperature:  75 deg C, maximum.

Coordinate paragraph and subparagraphs below with submittal requirements for certificates.

B. Ballasts for Dimmer-Controlled Lighting Fixtures:  Electronic type.

1. Dimming Range:  100 to [5] <Insert value> percent of rated lamp lumens.

2. Ballast Input Watts:  Can be reduced to [20] <Insert value> percent of normal.

3. Compatibility:  Certified by manufacturer for use with specific dimming control system and lamp type indicated.

2.5 EMERGENCY FLUORESCENT POWER UNIT

Retain one or both paragraphs and subparagraphs below to specify emergency battery operation of either linear or compact fluorescent fixtures for code-required egress lighting.  Indicate fixture types to be equipped with these devices in Interior Lighting Fixture Schedule on Drawings or in "Requirements for Individual Lighting Fixtures" Article, and indicate connections on lighting plans.

A. Internal Type:  Self-contained, modular, battery-inverter unit, factory mounted within lighting fixture body and compatible with ballast.  Comply with UL 924.

1. Emergency Connection:  Operate [1] <Insert number> fluorescent lamp(s) continuously at an output of [1100] <Insert value> lumens each.  Connect unswitched circuit to battery-inverter unit and switched circuit to fixture ballast.

Retain first subparagraph below if night-light connections are used.  If used, differentiate two connection modes on Drawings or in Interior Lighting Fixture Schedule on Drawings.

2. Night-Light Connection:  Operate one fluorescent lamp continuously.

3. Test Push Button and Indicator Light:  Visible and accessible without opening fixture or entering ceiling space.

a. Push Button:  Push-to-test type, in unit housing, simulates loss of normal power and demonstrates unit operability.

b. Indicator Light:  LED indicates normal power on.  Normal glow indicates trickle charge; bright glow indicates charging at end of discharge cycle.

4. Battery:  Sealed, maintenance-free, nickel-cadmium type.

5. Charger:  Fully automatic, solid-state, constant-current type with sealed power transfer relay.

Retain subparagraph below to permit periodic test required by codes for emergency equipment to be performed using a hand-held remote device to trigger simulation of loss of normal power in the tested unit.

6. Remote Test:  Switch in hand-held remote device aimed in direction of tested unit initiates coded infrared signal.  Signal reception by factory-installed infrared receiver in tested unit triggers simulation of loss of its normal power supply, providing visual confirmation of either proper or failed emergency response.

Retain subparagraph below to eliminate necessity to manually perform periodic test required by codes for emergency equipment.  Verify requirements of authorities having jurisdiction.

7. Integral Self-Test:  Factory-installed electronic device automatically initiates code-required test of unit emergency operation at required intervals.  Test failure is annunciated by an integral audible alarm and flashing red LED.

B. External Type:  Self-contained, modular, battery-inverter unit, suitable for powering one or more fluorescent lamps, remote mounted from lighting fixture.  Comply with UL 924.

1. Emergency Connection:  Operate one fluorescent lamp continuously.  Connect unswitched circuit to battery-inverter unit and switched circuit to fixture ballast.

Retain first subparagraph below if night-light connections are used.  If used, differentiate two connection modes on Drawings or in Interior Lighting Fixture Schedule on Drawings.

2. Night-Light Connection:  Operate one fluorescent lamp in a remote fixture continuously.

3. Battery:  Sealed, maintenance-free, nickel-cadmium type.

4. Charger:  Fully automatic, solid-state, constant-current type.

5. Housing:  NEMA 250, Type 1 enclosure.

6. Test Push Button:  Push-to-test type, in unit housing, simulates loss of normal power and demonstrates unit operability.

7. LED Indicator Light:  Indicates normal power on.  Normal glow indicates trickle charge; bright glow indicates charging at end of discharge cycle.

Retain subparagraph below to permit periodic test required by codes for emergency equipment to be performed using a hand-held remote device to trigger simulation of loss of normal power in the tested unit.

8. Remote Test:  Switch in hand-held remote device aimed in direction of tested unit initiates coded infrared signal.  Signal reception by factory-installed infrared receiver in tested unit triggers simulation of loss of its normal power supply, providing visual confirmation of either proper or failed emergency response.

Retain subparagraph below to eliminate necessity to manually perform periodic test required by codes for emergency equipment.  Verify requirements of authorities having jurisdiction.

9. Integral Self-Test:  Factory-installed electronic device automatically initiates code-required test of unit emergency operation at required intervals.  Test failure is annunciated by an integral audible alarm and flashing red LED.

2.6 BALLASTS FOR HID LAMPS

First two paragraphs and associated subparagraphs below specify the default ballast type for metal-halide lighting fixtures.  If Project has applications for both electromagnetic and electronic ballasts, indicate the ballast type in Interior Lighting Fixture Schedule on Drawings or in "Requirements for Individual Lighting Fixtures" Article.  See Evaluations.

A. Electromagnetic Ballast for Metal-Halide Lamps:  Comply with ANSI C82.4 and UL 1029.  Include the following features, unless otherwise indicated:

1. Ballast Circuit:  Constant-wattage autotransformer or regulating high-power-factor type.

2. Minimum Starting Temperature:  Minus 22 deg F (Minus 30 deg C) for single-lamp ballasts.

3. Normal Ambient Operating Temperature:  104 deg F (40 deg C).

4. Open-circuit operation that will not reduce average life.

Retain subparagraph below if ballast hum is audible above ambient sound levels and exceeds recommended noise-criterion rating for particular room or area.  Coordinate with Interior Lighting Fixture Schedule on Drawings or with "Requirements for Individual Lighting Fixtures" Article.  See Editing Instruction No. 3 in the Evaluations.

5. Low-Noise Ballasts:  Manufacturers' standard epoxy-encapsulated models designed to minimize audible fixture noise.

Retain first paragraph and subparagraphs below if Project includes pulse-start, metal-halide fixtures with electronic ballasts.  See Evaluations for discussion.

B. Electronic Ballast for Metal-Halide Lamps:  Include the following features unless otherwise indicated:

1. Lamp end-of-life detection and shutdown circuit.

2. Sound Rating:  A.

3. Total Harmonic Distortion Rating:  Less than 15 percent.

4. Transient Voltage Protection:  IEEE C62.41, Category A or better.

5. Lamp Current Crest Factor:  1.5 or less.

6. Power Factor:  .90 or higher.

See Evaluations for discussion of CFR compliance required in first subparagraph below.

7. Interference:  Comply with 47 CFR, Chapter 1, Part 18, Subpart C, for limitations on electromagnetic and radio-frequency interference for nonconsumer equipment.

8. Protection:  Class P thermal cutout.

9. Retain subparagraph and associated subparagraphs below for bi-level ballasts.

10. Bi-Level Dimming Ballast:  Ballast circuit and leads provide for remote control of the light output of the associated fixture between high- and low-level and off.

a. High-Level Operation:  100 percent of rated lamp lumens.

b. Low-Level Operation:  [35] [50] percent of rated lamp lumens.

c. Compatibility:  Certified by ballast manufacturer for use with specific bi-level control system and lamp type indicated.  Certified by lamp manufacturer that ballast operating modes are free from negative effect on lamp life and color-rendering capability.

Retain subparagraph and associated subparagraphs below for ballast with continuous dimming capability.

11. Continuous Dimming Ballast:  Dimming range shall be from 100 to [35] <Insert value> percent of rated lamp lumens without flicker.

a. Ballast Input Watts:  Reduced to a maximum of [50] <Insert value> percent of normal at lowest dimming setting.

b. Compatibility:  Certified by manufacturer for use with specific dimming control system and lamp type indicated.  Certified by lamp manufacturer that ballast operating modes are free from negative effect on lamp life and color-rendering capability.

C. Auxiliary Instant-On Quartz System:  Factory-installed feature automatically switches quartz lamp on when fixture is initially energized and when power outages occur.  System automatically turns quartz lamp off when HID lamp reaches approximately 60 percent light output.

D. High-Pressure Sodium Ballasts:  Electromagnetic type, with solid-state igniter/starter.  Igniter-starter shall have an average life in pulsing mode of 10,000 hours at an igniter/starter-case temperature of 90 deg C.

If unacceptable for safety, security, or other reasons for high-pressure sodium lamps to be extinguished for a lengthy restrike period by momentary power interruptions, specify dual-arc tube lamps in "High-Pressure Sodium Lamps" Paragraph in "HID Lamps" Article or, for lamps up to 150 W, retain first subparagraph and associated subparagraphs below.

1. Instant-Restrike Device:  Integral with ballast, or solid-state potted module, factory installed within fixture and compatible with lamps, ballasts, and mogul sockets up to 150 W.

a. Restrike Range:  105- to 130-V ac.

b. Maximum Voltage:  250-V peak or 150-V ac RMS.

2. Minimum Starting Temperature:  Minus 40 deg F (Minus 40 deg C).

3. Open-circuit operation shall not reduce average lamp life.

2.7 EXIT SIGNS

A. Description:  Comply with UL 924; for sign colors, visibility, luminance, and lettering size, comply with authorities having jurisdiction.

B. Internally Lighted Signs:

Retain one of two subparagraphs below.  See Evaluations for discussion of energy considerations.

1. Lamps for AC Operation:  Fluorescent, 2 for each fixture, 20,000 hours of rated lamp life.

2. Lamps for AC Operation:  LEDs, 70,000 hours minimum rated lamp life.

Coordinate subparagraph and associated subparagraphs below with Part 1 "Warranty" Article.

3. Self-Powered Exit Signs (Battery Type):  Integral automatic charger in a self-contained power pack.

Revise first subparagraph below to specify different battery.  See Evaluations for discussion of battery types.  Verify that battery selection is available as UL-listed unit and coordinate with Part 1 "Warranty" Article.

a. Battery:  Sealed, maintenance-free, nickel-cadmium type.

b. Charger:  Fully automatic, solid-state type with sealed transfer relay.

c. Operation:  Relay automatically energizes lamp from battery when circuit voltage drops to 80 percent of nominal voltage or below.  When normal voltage is restored, relay disconnects lamps from battery, and battery is automatically recharged and floated on charger.

d. Test Push Button:  Push-to-test type, in unit housing, simulates loss of normal power and demonstrates unit operability.

e. LED Indicator Light:  Indicates normal power on.  Normal glow indicates trickle charge; bright glow indicates charging at end of discharge cycle.

Retain subparagraph below to permit periodic test required by codes for emergency equipment to be performed using a hand-held remote device to trigger simulation of loss of normal power in the tested unit.

f. Remote Test:  Switch in hand-held remote device aimed in direction of tested unit initiates coded infrared signal.  Signal reception by factory-installed infrared receiver in tested unit triggers simulation of loss of its normal power supply, providing visual confirmation of either proper or failed emergency response.

Retain subparagraph below to eliminate necessity to manually perform periodic test required by codes for emergency equipment.  Verify requirements of authorities having jurisdiction.

g. Integral Self-Test:  Factory-installed electronic device automatically initiates code-required test of unit emergency operation at required intervals.  Test failure is annunciated by an integral audible alarm and flashing red LED.

Retain subparagraph and associated subparagraphs below if master/remote sign configurations are required to suit code locations both above and at floor adjacent to exit door.  Coordinate with Drawings.

4. Master/Remote Sign Configurations:

a. Master Unit:  Comply with requirements above for self-powered exit signs, and provide additional capacity in [LED power supply] [ballast] for power connection to remote unit.

b. Remote Unit:  Comply with requirements above for self-powered exit signs, except omit power supply, battery and test features.  Arrange to receive full power requirements from master unit.  Connect for testing concurrently with master unit as a unified system.

2.8 EMERGENCY LIGHTING UNITS

A. Description:  Self-contained units complying with UL 924.

Supplement subparagraphs below with data on Drawings in Interior Lighting Fixture Schedule or details.

Revise first subparagraph below to specify different battery.  See Evaluations for discussion of battery types.  Verify that battery selection is available as UL-listed unit and coordinate with Part 1 "Warranty" Article.

1. Battery:  Sealed, maintenance-free, lead-acid type.

2. Charger:  Fully automatic, solid-state type with sealed transfer relay.

3. Operation:  Relay automatically turns lamp on when power supply circuit voltage drops to 80 percent of nominal voltage or below.  Lamp automatically disconnects from battery when voltage approaches deep-discharge level.  When normal voltage is restored, relay disconnects lamps from battery, and battery is automatically recharged and floated on charger.

4. Test Push Button:  Push-to-test type, in unit housing, simulates loss of normal power and demonstrates unit operability.

5. LED Indicator Light:  Indicates normal power on.  Normal glow indicates trickle charge; bright glow indicates charging at end of discharge cycle.

Feature in subparagraph below is optional.  Coordinate with Drawings.

6. Wire Guard:  Heavy-chrome-plated wire guard protects lamp heads or fixtures.

Retain subparagraph below for time-delay option if units are indicated for areas normally lighted by HID fixtures that will not relight for a period after power is restored due to lengthy arc restrike delays.

7. Integral Time-Delay Relay:  Holds unit on for fixed interval of [15] <Insert period> minutes when power is restored after an outage.

Retain subparagraph below to permit periodic test required by codes for emergency equipment to be performed using a hand-held remote device to trigger simulation of loss of normal power in the tested unit.

8. Remote Test:  Switch in hand-held remote device aimed in direction of tested unit initiates coded infrared signal.  Signal reception by factory-installed infrared receiver in tested unit triggers simulation of loss of its normal power supply, providing visual confirmation of either proper or failed emergency response.

Retain subparagraph below to eliminate necessity to manually perform periodic test required by codes for emergency equipment.  Verify requirements of authorities having jurisdiction.

9. Integral Self-Test:  Factory-installed electronic device automatically initiates code-required test of unit emergency operation at required intervals.  Test failure is annunciated by an integral audible alarm and flashing red LED.

2.9 FLUORESCENT LAMPS

Coordinate this Article with Drawings.  Where color rendition or color uniformity is important and several types of fluorescent lamps are used, provide consistent manufacturer designations or ANSI lamp designations to define requirements.  Specifying low-mercury lamps may change the color temperature. Low-mercury versions may not be available in all lamp categories.  Consult manufacturers.

A. Low-Mercury Lamps:  Comply with EPA's toxicity characteristic leaching procedure test; shall yield less than 0.2 mg of mercury per liter when tested according to NEMA LL 1.

Paragraphs and subparagraphs below are sample specifications for typical lamps, which are a few of the thousands of types and ratings available for building illumination.  Indicate here or in Interior Lighting Fixture Schedule the standard designations of the lamps that meet lumen output, energy rating, CRI, color temperature, lamp life, and other requirements for specific Project applications.  See Editing Instruction No. 10 in the Evaluations.

B. T8 rapid-start[ low-mercury] lamps, rated 32 W maximum, nominal length of 48 inches (1220 mm), 2800 initial lumens (minimum), CRI 75 (minimum), color temperature [3500] <Insert value> K, and average rated life 20,000 hours, unless otherwise indicated.

C. T8 rapid-start[ low-mercury] lamps, rated 17 W maximum, nominal length of 24 inches (610 mm), 1300 initial lumens (minimum), CRI 75 (minimum), color temperature [3500] <Insert value> K, and average rated life of 20,000 hours, unless otherwise indicated.

D. T5 rapid-start[ low-mercury] lamps, rated 28 W maximum, nominal length of 45.2 inches (1150 mm), 2900 initial lumens (minimum), CRI 85 (minimum), color temperature [3000] <Insert value> K, and average rated life of 20,000 hours, unless otherwise indicated.

E. T5HO rapid-start, high-output[ low-mercury] lamps, rated 54 W maximum, nominal length of 45.2 inches (1150 mm), 5000 initial lumens (minimum), CRI 85 (minimum), color temperature [4100] <Insert value> K, and average rated life of 20,000 hours, unless otherwise indicated.

F. Compact Fluorescent Lamps:  4-Pin, [low mercury, ]CRI 80 (minimum), color temperature [3500] <Insert value> K, average rated life of 10,000 hours at 3 hours operation per start, [and suitable for use with dimming ballasts, ]unless otherwise indicated.

1. 13 W:  T4, double or triple tube, rated 900 initial lumens (minimum).

2. 18 W:  T4, double or triple tube, rated 1200 initial lumens (minimum).

3. 26 W:  T4, double or triple tube, rated 1800 initial lumens (minimum).

Low-mercury products may not be available in higher-wattage products in three subparagraphs below.  Consult manufacturers.

4. 32 W:  T4, triple tube, rated 2400 initial lumens (minimum).

5. 42 W:  T4, triple tube, rated 3200 initial lumens (minimum).

6. 55 W:  T4, triple tube, rated 4300 initial lumens (minimum).

2.10 HID LAMPS

Coordinate this Article with Drawings.  Where color rendition or color uniformity is important and several types of HID lamps are used, provide consistent manufacturer designations or ANSI designations to define lamp types.

A. High-Pressure Sodium Lamps:  ANSI C78.42, CRI 21 (minimum), color temperature [1900] <Insert value> K, and average rated life of 24,000 hours, minimum.

Consider retaining subparagraph below if extinguishing of high-pressure sodium lamps caused by momentary power interruptions is unacceptable for safety, security, or other reasons.  Instant-restrike feature specified in "Ballasts for HID Lamps" Article may also be considered.  Verify availability of individual ratings with manufacturers before scheduling or specifying.

1. Dual-Arc Tube Lamps:  Arranged so only one of two arc tubes is lighted at one time and, when power is restored after an outage, the cooler arc tube, with lower internal pressure, lights instantly, providing an immediate 8 to 15 percent of normal light output.

ANSI has a separate standard for each conventional metal-halide lamp, unlike standards for low- and high-pressure sodium lamps.  Consider including the standard number in Interior Lighting Fixture Schedule on Drawings.  Wattage and mean lumen output ratings for each lamp may be included in Interior Lighting Fixture Schedule on Drawings or in "Requirements for Individual Lighting Fixture" Article.

B. Metal-Halide Lamps:  ANSI C78.1372, with a minimum CRI [65] <Insert value>, and color temperature [4000] <Insert value> K.

Pulse-start, metal-halide lamps in paragraph below are available in ratings from 30 to 1000 W and provide higher lumen maintenance and reduced color-shift throughout the life of the lamp, compared with basic metal-halide lamps.  This may permit the use of lower-wattage lamps to provide the same maintained illumination level provided by an equal number of conventional metal-halide lamps.  Consult manufacturers to verify compatibility of lamps with ballasts and fixtures.

C. Pulse-Start, Metal-Halide Lamps:  Minimum CRI 65, and color temperature [4000] <Insert value> K.

Ceramic, pulse-start, metal-halide lamps in paragraph below are available in ratings from about 40 to 250 W.  In addition to advantages inherent in pulse-start technology, these lamps have an improved CRI, between 80 and 94, with higher initial and maintained lumen output.

D. Ceramic, Pulse-Start, Metal-Halide Lamps:  Minimum CRI [80] <Insert value>, and color temperature [4000] <Insert value> K.

2.11 LIGHTING FIXTURE SUPPORT COMPONENTS

Coordinate this Article with Drawings.  See Editing Instruction No. 2 in the Evaluations for discussion of seismic considerations.

A. Comply with Division 16 Section "Electrical Supports and Seismic Restraints" for channel- and angle-iron supports and nonmetallic channel and angle supports.

B. Single-Stem Hangers:  1/2-inch (13-mm) steel tubing with swivel ball fittings and ceiling canopy.  Finish same as fixture.

C. Twin-Stem Hangers:  Two, 1/2-inch (13-mm) steel tubes with single canopy designed to mount a single fixture.  Finish same as fixture.

D. Wires:  ASTM A 641/A 641M, Class 3, soft temper, zinc-coated steel, [12 gage (2.68 mm)] <Insert wire size>.

Coordinate first paragraph below with Drawings to identify humid spaces.

E. Wires for Humid Spaces:  ASTM A 580/A 580M, Composition 302 or 304, annealed stainless steel, [12 gage (2.68 mm)] <Insert wire size>.

F. Rod Hangers:  3/16-inch (5-mm) minimum diameter, cadmium-plated, threaded steel rod.

G. Hook Hangers:  Integrated assembly matched to fixture and line voltage and equipped with threaded attachment, cord, and locking-type plug.

2.12 RETROFIT KITS FOR FLUORESCENT LIGHTING FIXTURES

A. Comply with UL 1598 listing requirements.

1. Reflector Kit:  UL 1598, Type I.  Suitable for two- to four-lamp, surface-mounted or recessed lighting fixtures by improving reflectivity of fixture surfaces.

2. Ballast and Lamp Change Kit:  UL 1598, Type II.  Suitable for changing existing ballast, lamps, and sockets.

2.13 REQUIREMENTS FOR INDIVIDUAL LIGHTING FIXTURES

Delete this Article if lighting fixtures are scheduled on Drawings.  Retain and revise to suit Project if each lighting fixture is to be specified in detail here instead of scheduling on Drawings.  See Editing Instruction No. 1 in the Evaluations for discussion of schedules.  Refer to Interior Lighting Fixture Schedule at the end of the Evaluations for use on Drawings.

Copy paragraph and subparagraphs below and re-edit for each type of lighting fixture in Project.  Assign a unique fixture designation for each type specified, and use these designations on Drawings to show where each fixture is required.

A. Fixture Type <Insert Drawing designation>:

Retain "Basis-of-Design Product" Subparagraph and list below with "Basis-of-Design Product" Subparagraph in Part 2 "Manufacturers" Article.

1. Basis-of-Design Product:  <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Delete subparagraph above or below.  Retain list of manufacturers with either subparagraph.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

2. [Available ]Manufacturers:

a. <Insert, in separate subparagraphs, manufacturer's name.>

Revise subparagraphs below to list detailed specifications for lighting fixture being described.  Delete inapplicable subparagraphs; add others to suit description needs.

3. Voltage:  [120] [277] [480]-V ac.

4. Mounting:  [Recessed ceiling] [Recessed wall] [Semirecessed] [Pendant] [Surface ceiling] [Surface wall] [Suspended] <Insert mounting height of pendant, wall, and suspended fixture.>

5. Nominal Dimensions:  <Insert nominal dimensions.>

Use NEMA or ANSI designation for lamp description in subparagraph below if possible.

6. Lamps:  <Insert quantity and description if not indicated elsewhere.>

Retain three subparagraphs below for linear or compact fluorescent fixture types.  See Editing Instruction No. 9 in the Evaluations for discussion of alternative ballast types.

7. Ballast Type:  [Electronic instant start] [Electronic programmed start] [Electronic dimming] [Electronic bi-level] [Electromagnetic] [Low temperature].

See Editing Instruction No. 7 in the Evaluations for discussion of BF.

8. BF:  <Insert value.>

9. Quantity of Ballasts per Fixture:  <Insert number.>

Retain subparagraph below for HID fixture types.

10. Ballast Type:  [Electronic] [Electronic continuous dimming] [Electronic bi-level dimming] [Electromagnetic], compatible with lamp type indicated.

Delete first subparagraph below unless fixture is one of a group for which ballast fuses will be needed by maintenance staff or for other reasons.  See Editing Instruction No. 5 in the Evaluations for discussion of ballast fusing.

11. Ballast Fuse:  Factory installed, slow-blow type rated between 2.65 and 3.0 times the line current.

12. Lens:  <Describe types, materials, and features not indicated elsewhere.>

13. External Finish:  <Insert descriptions.>

14. Trim and Hardware:  [Spring-loaded door latches] <Describe trim items and desired optional features>.

15. Special Environmental Conditions:  <Describe conditions such as corrosive, damp, or wet locations.>

16. Other Features:  <Insert special features.>

Retain first five subparagraphs below for lighting fixtures with critical illumination and visual-comfort performance requirements.

17. Minimum CU for typical RCR shall be as follows (typical cavity reflectances are ceiling, 80 percent; wall, 50 percent; and floor, 20 percent):  RCR [3] [5] [7] <Insert required value> CU.

18. Minimum Spacing to Mounting Height Ratio:  <Insert value.>

19. Minimum Visual Comfort Probability:  <Insert value> for room dimensions <Insert nominal length, width, and height in feet (m)>.

20. Maximum Luminance Ratio:  <Insert value.>

See Editing Instruction No. 8 in the Evaluations for discussion of minimum LER.

21. Minimum LER:  <Insert value.>

22. Other Requirements:  <Insert special features and characteristics.>

Delete two subparagraphs below if Samples and mockups are not required.

23. Submit Sample.

24. Provide lighting fixtures as needed for mockups.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Lighting fixtures:  Set level, plumb, and square with ceilings and walls.  Install lamps in each fixture.

NFPA 70 requires minimum support for fixtures.  Retain first paragraph and subparagraphs below for more specific support requirements and for requirements exceeding code minimums.  Units in seismic areas may require additional supports and restraining devices beyond those specified here.  See Editing Instruction No. 2 in the Evaluations.

B. Support for Lighting Fixtures in or on Grid-Type Suspended Ceilings:  Use grid as a support element.

1. Install a minimum of four ceiling support system rods or wires for each fixture.  Locate not more than 6 inches (150 mm) from lighting fixture corners.

2. Support Clips:  Fasten to lighting fixtures and to ceiling grid members at or near each fixture corner with clips that are UL listed for the application.

3. Fixtures of Sizes Less Than Ceiling Grid:  Install as indicated on reflected ceiling plans or center in acoustical panel, and support fixtures independently with at least two 3/4-inch (20-mm) metal channels spanning and secured to ceiling tees.

Retain subparagraph below if Project is in a seismic area.

4. Install at least one independent support rod or wire from structure to a tab on lighting fixture.  Wire or rod shall have breaking strength of the weight of fixture at a safety factor of 3.

C. Suspended Lighting Fixture Support:

1. Pendants and Rods:  Where longer than 48 inches (1200 mm), brace to limit swinging.

2. Stem-Mounted, Single-Unit Fixtures:  Suspend with twin-stem hangers.

3. Continuous Rows:  Use tubing or stem for wiring at one point and tubing or rod for suspension for each unit length of fixture chassis, including one at each end.

D. Air-Handling Lighting Fixtures:  Install with dampers closed and ready for adjustment.

E. Adjust aimable lighting fixtures to provide required light intensities.

F. Connect wiring according to Division 16 Section "Conductors and Cables."

3.2 FIELD QUALITY CONTROL

A. Test for Emergency Lighting:  Interrupt power supply to demonstrate proper operation.  Verify transfer from normal power to battery and retransfer to normal.

B. Prepare a written report of tests, inspections, observations, and verifications indicating and interpreting results.  If adjustments are made to lighting system, retest to demonstrate compliance with standards.

END OF SECTION 16511END OF SECTION 16511

INTERIOR LIGHTING
16511 - 1

