Copyright 2002 AIA
MASTERSPEC
06/02 (R 06/03)

Copyright 2003 (R 06/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16727 - SOUND-MASKING EQUIPMENT
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes electronic noise generators, amplifiers, wiring, loudspeakers, controls, and auxiliary components to generate, amplify, distribute, and reproduce digitally synthesized and stabilized pink background noise to improve speech privacy in zones of coverage.

1.3 DEFINITIONS

Retain definitions that remain after this Section has been edited.

A. Test and Calibration Conditions:  Spaces completely furnished but unoccupied, lights and HVAC systems on, HVAC system testing and balancing completed, ceiling components in place.

B. Covered Spaces:  Spaces above which masking speakers are installed.

C. Pink Noise:  Random noise signal with equal energy in each octave.

D. Sound Masking:  Covering up of one sound by another.

1.4 SYSTEM DESCRIPTION

Edit this Article to indicate extent of system coverage required.  Coordinate with Drawings to indicate extent of system or individual zones to be covered.  Revise number of channels and modify number of zones to suit Project.  See Evaluations.

A. Zones:  Single-zone coverage.

B. Zones:  Multiple-zone coverage.

Retain one of first three paragraphs below to specify number of channels.  See Evaluations.

C. Channels:  Single channel of masking sound to each zone.

D. Channels:  Separate channel of masking sound to each of two groups of speakers in each zone.

E. Channels:  Separate channel of masking sound to each of three groups of speakers in each zone.

F. Signal Levels:  Individually adjustable for each of 14 one-third octave bands centered at 200 through 4000 Hz, for sound-masking noise channels.

First paragraph and subparagraphs below specify system performance for typical office occupancies.  Revise to suit other applications.

G. Sound-Power Level Produced by System:  Match NC 40 contour between 400 and 2000 Hz, with smooth roll-off above and below those frequencies.

1. Initial Level:  40 dB, A-weighted.

2. Final Adjusted Level:  40 to 50 dB, A-weighted.  Determine final level for each space individually by measurement as specified in Part 3.

3. Measurements:  Made under calibration conditions.

H. Maximum Local Variance of Sound-Power Level:  6 dB for the 500-Hz octave band and 3 dB for the 1000-, 2000-, and 4000-Hz octave bands for 75 percent of the locations in covered spaces.

I. Maximum Average Range of Sound-Power-Level Deviation:  2 dB in the 250-, 2000-, and 4000-Hz octave bands and 1.5 dB for the 500- and 1000-Hz octave bands for all locations.

J. Directional Effect:  People in covered spaces under calibration conditions cannot determine source of masking sound.

K. Uniformity with Respect to Time:  One-minute time-averaged sound-pressure level of any octave band of masking sound from 250 to 8000 Hz remains constant in any space to within a standard deviation of 2 dB when measured over a 30-minute period.

L. Sound Quality:  No audible hum or noise from this system in covered spaces when noise generators are off and power amplifiers are on with input volume controls set at 50 percent.

1.5 SUBMITTALS

A. Product Data:  For each component.  Include nationally recognized testing laboratory listing data.

B. Shop Drawings:  Dimensioned plans and elevations showing minimum clearances and installed features and devices for system components.  Show types and locations of masking speakers and their wiring connections, channel assignments, and axis orientations.  Show ducts, beams, and other significant sound-reflecting and -absorbing elements in ceiling space and show locations of partitions below ceiling.  Include a diagram showing interconnection of major system components for each zone and channel and indicating grounding connections.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Product Certificates:  For sound-masking equipment and components, signed by product manufacturer.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For [Installer] [manufacturer] [testing agency].

E. Record of Final Field Tests and Measurements:  Include final tuned tap and control adjustment settings of system.

F. Operation and Maintenance Data:  For sound-masking equipment and components to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1 Section "[Closeout Procedures] [Operation and Maintenance Data]," include data for each type of product, including all features and operating sequences, both automatic and manual.

1.6 QUALITY ASSURANCE

A. Installer Qualifications:  An experienced installer of sound-masking equipment.  Refer to Division 1 Section "References" for definition of an experienced installer.

B. Manufacturer Qualifications:  A prime system manufacturer who maintains or sponsors a service center capable of providing training, parts, and emergency maintenance and repairs at Project site with a [24] <Insert number>-hour maximum response time.

Retain first paragraph below if Contractor or manufacturer selects testing agency.

C. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct testing of sound-masking systems according to ASTM E 548.  Required experience includes having tested a minimum of five different systems within the last five years, each system similar in size and complexity to Project system.

D. Source Limitations:  Obtain equipment components from a single source who assumes responsibility for compatibility of items used.

E. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

F. Comply with NFPA 70.

G. Comply with UL 813, unless a more stringent standard is specified in Part 2.

1.7 COORDINATION

A. Coordinate quantity and arrangement of speaker assemblies with ceiling space configuration and with components occupying ceiling space, including structural members, pipes, air-distribution components, raceways, cable trays, recessed lighting fixtures, and other items.

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra products described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Sound-Masking Speaker Assemblies:  [One] <Insert number> for each 10 of each type used, but no fewer than one.

2. Fuses:  [One] <Insert number> for each type used, but no fewer than one.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Atlas Sound LP.

2. Dukane Corporation; Communications Systems Div.

3. Dynasound, Inc.

4. Lencore Acoustics Corp.

5. LynTec, Inc.

6. Moeller, K. R. Associates Ltd.

7. Proudfoot Company (The).

8. Sound Advance Systems Inc.

9. <Insert manufacturer's name.>

2.2 PRODUCTS AND EQUIPMENT

A. Components:  Modular plug-in, heavy-duty, industrial-grade integrated circuit devices.

B. AC Supply Voltage Tolerance:  105 to 130 V with no degradation of system performance.

C. Protection from Power Line Surges:  Integral surge suppressors listed under UL 1449; complying with IEEE C62.41, Category B; and with the following features:

1. Suppression Level:  300 V.

2. Maximum Response Time:  5 nanoseconds.

3. Circuit:  Multistage, using inductors and silicon-avalanche zener diodes or equivalent.

4. Indicator Lamp:  Neon or light-emitting diode located on control panel and arranged to extinguish on failure of protection.

5. Fuses:  Externally accessible.

D. Component Housings:  Suitable for mounting in standard 19-inch (480-mm) relay racks, with connections at rear and controls either on rear panel or protected by a screw-fastened security cover.

2.3 NOISE GENERATOR AND FILTER UNITS

A. Pink Noise Generator:  Output octave bands from 30 to 4000 Hz.

B. Filters for One-Third Octave Bands:  Adjustable from 10 dB of boost to 10 dB of cut at each center frequency.

C. High-Pass Filter:  Approximate range of cutoff adjustment is 37 to 400 Hz.

D. Low-Pass Filter:  Approximate range of cutoff adjustment is 3.4 to 20 kHz.

E. High-Cut Filter:  Approximate range of cutoff adjustment is 180 to 9000 Hz with slope varying to 12 dB per octave.

2.4 PROGRAMMABLE AUDIO-LEVEL CONTROL UNIT

This Article specifies an optional feature providing automatic adjustment of masking sound to suit predictably recurring changes in occupancy patterns.

A. Automatic Sound-Power-Level Changes:  Six system channel changes, four times per day, and capable of different time settings for each day of week.

B. Level Changes:  Programmable from front panel of unit, and automatically incremented over a period long enough for sound-level variations to be imperceptible to occupants of covered spaces.

C. Program Memory:  Nonvolatile for one year, minimum, without power.  When re-energized after a power outage, control starts at zero level and automatically advances system sound level at same rate used for programmed level changes.

2.5 POWER AMPLIFIERS

A. Power Amplifiers:  Comply with EIA SE-101-A, and have the following minimum features:

1. Mounting:  Rack mounted.

2. Output Regulation:  Less than 2 dB from zero to full load.

3. Total Harmonic Distortion:  Less than 3 percent, at rated power output from 50 to 12,000 Hz.

4. Signal-to-Noise Ratio:  60 dB or greater, at rated output.

5. Frequency Response:  Within plus or minus 2 dB from 50 to 12,000 Hz.

2.6 MASKING SPEAKER ASSEMBLIES

A. Speakers:  Comply with EIA SE-103; cone type, with the following minimum features:

1. Minimum Axial Sensitivity:  45 dB.

2. Frequency Response:  Within plus or minus 3 dB from 50 to 15,000 Hz.

3. Size:  8 inches (200 mm) with 1-inch (25-mm) voice coil and minimum 5-oz. (142-g) ceramic magnet, unless otherwise indicated.

4. Dispersion Angle:  100 degrees.

5. Rated Output Level:  10 W.

B. Configuration:  Dual 8-inch (200-mm) and dual 5-inch (125-mm) units mounted on metal baffles and arranged for optimum, multidirectional, angular sound distribution.  Arrange units for suspension from the building structure above the ceiling.

C. Matching Transformers:  Comply with EIA-160, full-power rated with 4 standard taps, and a maximum insertion loss of 0.5 dB.

D. Assemblies installed in air-handling spaces shall comply with NFPA 70 requirements for rate of heat-release and rate of smoke-release characteristics.  Tests for these requirements shall be according to UL 2043.

2.7 WIRE

A. Speaker Wire:  Untinned, twisted-pair, solid-copper wire with PVC jacket; listed and labeled for environmental air plenums where cable is indicated in plenum spaces and is not indicated to be in raceway.

2.8 COMPONENT MOUNTING RACKS

A. Configuration:  Comply with EIA-310-D.  Factory-fabricated units designed for interchangeable mounting, forced or convection air cooling, wiring connection, and enclosure of standard 19-inch (482-mm) relay rack modules.

Delete first paragraph below if Drawings show mounting requirements, or edit both paragraphs below to suit Project.

B. Mounting Provisions:  Equipped for freestanding floor mounting.

C. Cabinet:  Factory-finished steel with component mounting rails and prewired plug strips for component power connections.  Full front and rear doors with continuous hinges, handles, and cylindrical keyed locks.

PART 3 -  EXECUTION

3.1 INSTALLATION

Add requirements for seismic restraints in first paragraph below in high-seismic-risk zones.

A. Speaker Assemblies:  Suspend with chains from building structure above ceilings so bottom of assembly is 6 to 8 inches (150 to 200 mm) above upper plane of finished ceiling material.  Use eyebolts on speaker assemblies for attachment.  Suspend independently of supports for components of other building systems.

B. Speaker Connections:  For two- or three-channel systems, connect speaker assemblies alternatively so masking sound is redundant throughout zones of coverage.

If wiring methods for system are not indicated on Drawings, delete two of first three paragraphs below and modify remaining paragraph to suit Project.  Otherwise, delete all three paragraphs and coordinate with Drawings.

C. Wiring Method:  Install wiring in raceways, unless otherwise indicated.  Conceal raceways, except in unfinished indoor spaces.

D. Wiring Method:  Install wiring in raceways, except in accessible indoor ceiling spaces and attics and in hollow gypsum board partitions, and unless otherwise indicated.  Conceal raceways and wiring, except in unfinished spaces.

E. Wiring Method:  Cable.  Conceal cable in accessible ceilings, walls, and floors where possible.

F. Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess.  Provide and use lacing bars and distribution spools.

G. Pulling Cable:  Do not exceed manufacturer's recommended pulling tensions.  Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between normal termination points.  Remove and discard cable where damaged during installation and replace it with new cable.

Retain paragraph below for cable wiring method.

H. Exposed Cable:  Install parallel to building lines, follow surface contours, and support as recommended by manufacturer.

Coordinate first paragraph below with Drawings.

I. Grounding:  As recommended by manufacturers, unless more stringent requirements are indicated.  Ground equipment and conductors to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.  Install 5-ohm ground at main equipment location.  Measure, record, and report ground resistance.

J. Impedance Matching:  For system components, including connecting cable, provide end-to-end level and impedance-matched signal paths.  Use matching networks and balancing devices at connections where necessary to avoid mismatches.

K. Splices, Taps, and Terminations:  Make splices, taps, and terminations on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

3.2 IDENTIFICATION

A. Identify system components, wiring, cabling, and terminals according to Division 16 Section "Electrical Identification."  Use color-coded conductors and apply wire and cable marking tape to designate wires and cables so media are identified in coordination with system wiring diagrams.

B. Label speaker assemblies as to channel and zone.

3.3 FIELD QUALITY CONTROL

A. Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform field tests and inspections and prepare test reports.

Retain paragraph above or below.  Retain below if testing agency services are in Contract.  Delete both paragraphs if a qualified testing agency is not required.

B. Testing Agency:  Engage a qualified independent testing and inspecting agency to perform field tests and inspections and prepare test reports.

Retain first paragraph and subparagraphs below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustment.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

C. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.  Include the following:

1. Operational Test:  Start system to confirm proper operation.  Remove malfunctioning units, replace with new units, and retest.  Make initial sound-spectrum and -level adjustments for each zone.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3. Inspection:  Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.

4. Pretesting:  Tune, align, and adjust system and pretest components, wiring, and functions to verify they comply with specified material, installation, and performance requirements.  Correct deficiencies and retest until satisfactory performance and conditions are achieved.

5. Masking Sound-Power-Level Adjustments:  Adjust independently for each space to minimum level between 40 and 50 dB that will provide speech privacy between adjacent workstations while complying with other system requirements.

D. Final Acceptance Testing:  Provide a minimum of 10 days' notice of acceptance test performance schedule.  Schedule tests after pretesting has been successfully completed.

1. Test Conditions:  As defined in "Test and Calibration Conditions" Paragraph in Part 1 of this Section.  Perform tests as specified below, as required by ASTM E 1041, and as required to verify performance specified in Part 2 "System Description" Article.

2. Instrumentation:  Use a professional-quality, sound-level meter with octave-band filters and documentation of recent calibration against recognized standards.

3. Record test observations, readings, and corrective actions.

4. System Tests:  Include the following for each system zone:

a. Speaker Circuit Impedance Test:  Measure impedance at 1 kHz with amplifier disconnected, using a professional impedance meter or bridge.  Locate and correct faults denoted by abnormal readings.

b. Ambient Sound-Level Tests:  With system off, measure ambient sound level in one-third octave bands.  Also measure ambient sound level as a single, wide-band, A-weighted reading.

c. Amplifier Noise Test:  Check for performance specified in "System Description" Article with masking noise generator off and amplifiers on.

d. System Noise Test:  With masking noise signal on and amplifiers adjusted at a working level 10 dB above ambient sound level, check for hum, buzz, rattle, or other operating deficiencies.

e. Spatial Uniformity Test:  Measure sound level at locations no greater than 15 feet (4.6 m) o.c. throughout covered spaces to determine compliance with specified performance level.

f. Frequency Response Adjustment and Test:  Adjust one-third octave frequency bands and other unit filters to provide response.  Coordinate with NC 40 contour defined below between 200 and 2000 Hz, with smooth natural roll-off from those frequencies.

 PRIVATE tbl1@dom1
	BAND
	RELATIVE SOUND-POWER LEVEL - dB
	ENCLOSED OFFICES

	
	
	

	200
	Plus 4
	Minus 2

	250
	Plus 3
	Minus 2

	315
	Plus 2
	Minus 2.5

	400
	Plus 1
	Minus 3

	500
	0
	Minus 4

	630
	Minus 1
	Minus 5

	800
	Minus 2
	Minus 6

	1000
	Minus 3
	Minus 7

	1250
	Minus 4
	Minus 8.5

	1600
	Minus 5
	Minus 10

	2000
	Minus 6
	Minus 12


5. Adjust level of masking sound for each space so one-third octave band centered at 500 Hz has final selected sound-power level for that space.  Measure deviation from listed values in one-third octave bands from 400 to 2000 Hz.  Measured values must not deviate from those listed by more than 4 dB for open plan areas and 8 dB for enclosed offices.  The total of individual band deviations in eight bands must not exceed 16 dB for open plan areas and 30 dB for enclosed offices.

6. Walk-through Test:  People in covered spaces cannot discern speaker locations.

7. Temporal Stability Test:  Check for uniformity of time by measuring sound level in each of 14 octave bands at one-minute intervals over a 30-minute test period.  Deviations must not exceed limits specified in Part 2 "System Description" Article.

E. Retest:  Correct deficiencies identified by tests and observations and retest until meeting specified requirements.

F. Recording Control Settings and System Adjustments:  Record final control settings and programming, and final tap setting of speaker matching transformers.  Record final sound-level measurements and observations.

3.4 ADJUSTING

A. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain services.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 16727

SOUND-MASKING EQUIPMENT
16727 - 1

