Copyright 2000 AIA
GSA VERSION MASTERSPEC(
06/00 (GSA 03/03)


Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15515 - WATER-TUBE BOILERS
PART 1 -  GENERAL

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

1.1 RELATED DOCUMENTS

A. Drawings, and the general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section. 

1.2 SUMMARY

A. This Section includes [packaged,] [factory-fabricated] [and] [factory-fabricated and] [field]-assembled, [atmospheric-gas] [forced-draft gas] [oil] [combination gas- and oil]-fired, water-tube boilers, trim, and accessories for generating [heating water] [steam] and shall include the following features:

1. DDC microprocessor based controls [shall comply with ANSI/ASHRAE Standard 135].
B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Equipment Insulation" for insulation materials and application for pumps, tanks, hydronic specialties, and other equipment.

2. Division 15 Section "Pipe Insulation" for insulation for piping systems.

3. Division 15 Section “Basic Materials and Methods” for additional material specifications.

4. Division 15 Section “Building Automation Systems” for additional control related equipment.

5. Division 15 Section “Temperature Controls” for additional control related requirements.

6. Division 15 Section “Testing, Adjusting, and Balancing” for additional related requirements.

7. Division 15 Section “Operations and Maintenance” for additional related requirements.

1.3 DEFINITIONS

A. K:
Thousand (1000) units

B. M:
Million (1,000,000) units

1.4 SUBMITTALS

A. Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

Signed and sealed Shop Drawings are necessary only for very large boilers.

B. Shop Drawings:  For boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other Work.  [Shop Drawings shall be signed and sealed by a qualified registered professional engineer.]

Retain subparagraphs below if equipment is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

1. For installed products indicated in accordance with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

2. Design Calculations:  Calculate requirements for selecting vibration isolators [and seismic restraints] and for designing vibration isolation bases.

3. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.

Retain subparagraph below if equipment includes wiring.

4. Wiring Diagrams:  Detail power, signal, and control wiring.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls" and with seismic-related requirements in Parts 2 and 3 of this Section.

C. Manufacturer Seismic Qualification Certification:  Submit certification that the water-tube boiler, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when anchored to a concrete base.  Include the following:

1. Basis for Certification:  Indicate whether the certification to withstand seismic forces is based on actual tests of assembled components or on a calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Source quality-control test reports.

Retain first paragraph below for steam boilers operating at more than 15 psig (104 kPa) or hot-water boilers operating at more than 160 psig (1100 kPa) or 250 deg F (120 deg C).

E. ASME "A" Stamp Certification and Report:  Submit "A" stamp certificate of authorization, and document hydrostatic testing of piping external to boiler.

F. Startup service reports.

G. Operation and Maintenance Data:  For water-tube boilers to include in emergency, operation, and maintenance manuals.

H. Warranties:  Special warranties specified in this Section.

1.5 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings shall indicate size, profiles, and dimensional requirements of cast-iron boilers and shall be based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  These shall be listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

C. ASME Compliance:  Fabricate and label cast-iron boilers in accordance with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

D. ASHRAE/IESNA 90.1 Compliance:  Water-tube boilers shall have a minimum efficiency in accordance with ASHRAE Standard 90.1, Table 6.2.1F.

Retain paragraph below for oil-fired boilers.

E. UL Compliance:  Test water-tube boilers in accordance with UL 726, "Oil-Fired Boiler Assemblies."

Retain below for gas-fired boilers.

F. UL Compliance:  Test water-tube boilers in accordance with UL 795, "Commercial-Industrial Gas Heating Equipment."

1.6 COORDINATION

A. Coordinate the size and location of concrete bases.  Cast anchor-bolt inserts into the bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Determine the means and methods necessary to install the equipment specified herein.  For repairs, alterations, additions and other forms of installation of equipment specified in this section into existing conditions, develop a plan including the delivery of the equipment to the site and into the space allocated for the equipment as indicated on the contract documents.  Demolition to existing features of the building or site required to accomplish the delivery and installation of the equipment to be approved by the contracting officer for this project.   Demolition to existing features of the building or site required to accomplish the delivery and installation of the equipment is included in the scope of work for this project.  Repairs and new work required to replace feature of the building or site altered in the process of delivering and installing the equipment is included in the scope of work.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 15 Section "Heating Boilers and Accessories."  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which the manufacturer agrees to repair or replace the controls and heat exchangers of cast-iron boilers at no additional cost to the owner which fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

B. Warranty Period for Drums, Tubes, Headers, Cabinets, and Atmospheric Gas Burner:  [Five] <Insert number> years from date of Substantial Completion, pro rata.

C. Warranty Period for Pressure Vessel:  [20] <Insert number> years from date of Substantial Completion, for thermal shock.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with these specifications, manufacturers offering products that may be incorporated into the Work include, but are not limited to, those listed below:

1. Ajax Boiler, Inc.

2. Bryan Steam Corporation.

3. Cleaver-Brooks; Div. of Aqua-Chem, Inc.

4. Donlee Technologies Inc.

5. Parker Boiler Co.

6. Rite Engineering & Mfg. Corp.

7. <Insert manufacturer's name. >

2.2 PACKAGED WATER-TUBE BOILERS

A. Description:  Boilers shall be factory-fabricated, -assembled, and -tested water-tube boilers with heat exchanger sealed pressure-tight, built on a steel base; including insulated jacket, flue-gas vent, combustion-air intake connections, water supply and return connections, and controls.

Retain paragraph above for factory-assembled boilers or paragraph below for field-assembled boilers.

B. Description:  Boilers shall be factory-fabricated and field-assembled and -tested water-tube boilers with heat exchanger sealed pressure-tight, built on a steel base; including insulated jacket, flue-gas vent, combustion-air intake connections, water supply and return connections, and controls.
Retain paragraph below for projects in seismic areas.

C. Fabricate base and attachment to pressure vessel with reinforcement strong enough to resist boiler movement during a seismic event when boiler base is anchored to building structure.

Delete paragraph and subparagraphs below if characteristics and capacities are scheduled on Drawings.

D. Base shall be fabricated and attached to the pressure vessel with reinforcement strong enough to resist boiler movement during both a thermal and a seismic event when the boiler base is anchored to the building structure.

1. Heating Medium:  [Heating water] [Steam].

2. Maximum Design Pressure Rating:  [104 kPa (15 psig)] [1035 kPa (150 psig)] [1725 kPa (250 psig)] <Insert kPa (psig)>.

Retain subparagraph above for steam boilers and below for hot-water boilers.

3. Maximum Design Pressure Rating:  [420 kPa (60 psig)] [690 kPa (100 psig)] [966 kPa (140 psig)] [1100 kPa (160 psig)] <Insert kPa (psig)>.

Retain two subparagraphs below for steam boilers.

4. Operating Pressure:  <Insert kPa (psig). >

5. Steam Flow Rate:  <Insert kg/s (lb/h). >

Retain four subparagraphs below for hot-water boilers.

6. Entering-Water Temperature:  <Insert deg C (deg F). >

7. Leaving-Water Temperature:  <Insert deg C (deg F). >

8. Water Flow Rate:  <Insert L/s (gpm). >

9. Maximum Pressure Drop:  <Insert kPa (psig). >

In first subparagraph below, AFUE is not available for commercial boilers rated more than 300,000 Btuh (87.9 kW).  Specify standing or intermittent pilot with minimum AFUE.

10. Minimum Efficiency:  

a. Gas-fired, less than 87.9 kW (300,000 BTUH) input

1) Hot water:  80% AFUE

2) Steam:  75% AFUE

b. Gas-fired, greater than 87.9 kW (300,000 BTUH) input: 80% combustion efficiency.

c. Oil-fired, less than 87.9 kW (300,000 BTUH) input: 80% AFUE

d. Oil-fired, greater than 87.9 kW (300,000 BTUH) input: 80% combustion efficiency.

11. Number of Passes:  [One] [Two] <Insert number>.

12. Water Capacity:  <Insert L (gal.). >

Retain one of four subparagraphs below for rating methods.

13. AGA Output Capacity:  <Insert kW (kBh). >

14. DOE Output Capacity:  <Insert kW (kBh). >

15. Output Capacity:  <Insert kW (kBh). >

16. Equivalent Direct Radiation:  <Insert W (EDR). >

2.3 PACKAGED WATER-TUBE BOILER COMPONENTS

Retain one of first two paragraphs and associated subparagraphs below for heat-exchanger design.  Retain first paragraph and associated subparagraphs for straight-tube design; second, for bent-tube design.

A. Heat-Exchanger Design:  Straight steel tubes rolled into steel headers.

1. Accessible head plates at both ends.

2. Handholes in headers for waterside inspections.

3. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

4. Lifting lugs on top of boiler.

Retain subparagraph below for hot-water boilers only.

5. Built-in air separator.

B. Heat-Exchanger Design:  Bent steel tubes [swedged] [welded] into steel headers [with membrane waterwall design]. [Limit tube configurations to [two] [four] <Insert designer's preference>.
1. Accessible drain and blowdown tappings, both high and low, for surface and mud removal.

2. Accessible inspection ports in drum, mud legs, and tube manifolds.

3. Lifting lugs on top of boiler.

Retain subparagraph below for hot-water boilers only.

4. Built-in air separator.

The need for refractory insulation around combustion chamber is reduced by a membrane waterwall (tube wall) construction design offered by some manufacturers.

C. Combustion Chamber:  Chamber shall be equipped with a minimum [50-mm (2-1/2-inch)] [75-mm (3-inch)] [100-mm (4-inch)], 1480 deg C (2700 deg F) poured refractory on floor and minimum [50-mm (2-inch)] [89-mm (3-1/2-inch)] lap-jointed cast refractory with fiber-blanket joint seals on sidewalls.  Provide flame observation ports, front and back.

D. Casing:  Casing shall have the features listed below:

1. Insulation:  Minimum [250-mm- (-inch-) thick lightweight refractory; 25-mm- (1-inch-) thick insulating board; galvanized-steel membrane, and] 50-mm- (2-inch-) thick mineral-fiber insulation surrounding the heat exchanger and combustion chamber.

2. Top Flue Connection:  Constructed of [aluminized] [stainless] steel.

Retain one of first two subparagraphs below.

3. Jacket:  Mirror-finish stainless steel, with screw-fastened closures.

4. Jacket:  Sheet metal, with screw-fastened closures and [baked-enamel] [powder-coated] protective finish.

5. Mounting base to secure boiler to concrete base.

6. Control Compartment Enclosure:  NEMA 250, Type 1A.

Retain second option below if boiler is forced-draft type.  Retain first option for atmospheric burner.

E. [Draft Diverter] [Barometric Damper]:  Galvanized-steel assembly with flue-gas thermometer.

2.4 FUEL-FIRED BOILERS

A. Fuel-fired boilers shall comply with the requirements of ASHRAE/IESNA Standard 90.1 Section 6, Heating, Ventilating and Air Conditioning and Table 6.2.1.F.  Fuel-fired boilers shall also comply with the requirements of Section 7.  Service water heating and the fuel fired equipment portion of Table 7.2.2.

1. Fuel-fired boilers shall have factory-mounted controls and devices that allow for measuring, monitoring, and controlling energy consumption, output, and operating efficiencies prescribed in Section 6:  Heating, Ventilation, and Air Conditioning and Section 7:  Service Water Heating of ASHRAE/IESNA Standard 90.1 and Code of Federal Regulations (CFR) 10-CFR-435.  Factory-mounted controls shall include a controller with an LED panel capable of calculating and indicating the values required to verify the efficiencies and operating characteristics identified in ASHRAE/IESNA Standard 90.1.

2.5 ATMOSPHERIC GAS BURNER

A. Burner Tubes and Orifices:  [Stainless steel] [Cast iron], for [natural] [propane] gas.

Delete three subparagraphs below if capacities are scheduled on Drawings; if not, retain one of three input rating methods.

1. AGA Input:  <Insert kW (kBh). >

2. I=B=R Input:  <Insert kW (kBh). >

3. Gas Input:  <Insert mL/s (cfh). >

Gas train description below applies to commercial boilers.  Retain any of three control sequences with any of five safety requirements.

B. Gas Train Controls:  Control devices shall be of the [full-modulation] [on-off] [off-low-high] control sequence and shall comply with the requirements in [IRI] [FMG] [ASME CSD-1] [UL].
C. Gas Train Accessories:  Provide an approved manual shutoff gas valve, pressure regulator, and pilot adjustment.  Pilot shall have its own separate shutoff valve.

D. Pilot:  [Standing] [Intermittent-electric-spark] pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

E. Combustion Air:  The burner shall be configured to induce combustion air directly from the room.

2.6 FORCED-DRAFT GAS BURNER

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for [natural] [propane] gas.

Delete subparagraph below if capacities are scheduled on Drawings.

1. AGA Input:  <Insert kW (kBh). >

2. I=B=R Input:  <Insert kW (kBh). >

3. Gas Input:  <Insert mL/s (cfh). >

B. Blower:  Forward-curved, centrifugal fan integral to burner, directly driven by an electric motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If characteristics other than those in "Motors" Section are required, add subparagraphs below to suit Project.

1. Refer to Division 15 Section "Motors" for general requirements.

2. Minimum Motor Sizes:  <Insert horsepower. >

3. RPM:  3450.

4. Electrical Characteristics:  [120 V, single phase] [240 V, three phase], [460 V three-phase] 60 Hz.
5. Full-Load Amperes:  <Insert amperes. >

6. Minimum Circuit Ampacity:  <Insert amperes. >

7. Maximum Overcurrent Protection:  <Insert amperes. >

In first paragraph below, retain any of three control sequences with any of four safety requirements.

C. Gas Train Controls:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [IRI] [FMG] [ASME CSD-1] [UL].
D. Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

Retain below to decrease oxides of nitrogen emissions.

E. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen:  [20] <Insert amount> ppm.

2.7 OIL BURNER

A. Burner:  Welded construction with multivane, stainless steel, flame retention diffuser for fuel oil.

Delete subparagraph below if capacities are scheduled on Drawings.

1. Oil Input:  <Insert L/h (gph). >

B. Blower:  Forward-curved, centrifugal fan integral to burner, directly driven by an electric motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If characteristics other than those in "Motors" Section are required, add subparagraphs below to suit Project.

1. Refer to Division 15 Section "Motors" for general requirements.

2. Minimum Motor Sizes:  <Insert horsepower. >

3. RPM:  3450.

4. Electrical Characteristics:  [120 V, single phase] [240 V, three phase], [460 V three-phase] 60 Hz.
5. Full-Load Amperes:  <Insert amperes. >

6. Minimum Circuit Ampacity:  <Insert amperes. >

7. Maximum Overcurrent Protection:  <Insert amperes. >

In first paragraph below, retain any of three control sequences with any of four safety requirements.

C. Oil Supply:  Control devices shall be of the [modulating] [on-off] [low-high-low] type.  Control sequence shall comply with the requirements in [IRI] [FMG] [ASME CSD-1] [UL].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in subparagraph below to suit Project.

1. Two-stage, gear-type oil pump [integral to and directly driven by blower] shall be capable of producing 2100-kPa (300-psig) discharge pressure and 50.7-kPa (15-in. Hg) vacuum.  Include suction-line, manual, gate-type shutoff valve; removable-mesh-type oil strainer; 0- to 101.3-kPa (0- to 30-in. Hg) vacuum; 0- to 210-kPa (0- to 30-psig) vacuum-pressure gage; 0- to 2100-kPa (0- to 300-psig) oil-nozzle pressure gage; and nozzle-line, solenoid-safety-shutoff oil valve.

D. Oil Supply Accessories:  Furnish a two-stage; gear-type oil pump [integral to and directly driven by blower] [skid mounted electric motor driven,] [boiler base mounted, electric motor driven pump] shall be capable of producing 2100-kPa (300-psig) discharge pressure and 50.7-kPa (15-in. Hg) vacuum.  Include suction-line, manual, gate-type shutoff valve; removable-mesh-type oil strainer; 0- to 101.3-kPa (0- to 30-in. Hg) vacuum; 0- to 210-kPa (0- to 30-psig) vacuum-pressure gage; 0- to 2100-kPa (0- to 300-psig) oil-nozzle pressure gage; and nozzle-line, solenoid-safety-shutoff oil valve.

E. Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid using [cadmium sulfide] [ultraviolet scanner] flame-safety control.

Retain below to decrease oxides of nitrogen emissions.

F. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

1. Maximum Oxides of Nitrogen:  [20] <Insert amount> ppm.

2.8 COMBINATION GAS AND OIL BURNER

A. Burner:  Welded construction with multivane, stainless-steel, flame-retention diffuser for fuel oil and [natural] [propane] gas.

Delete two subparagraphs below if capacities are scheduled on Drawings.

1. AGA Input:  <Insert kW (kBh). >

2. I=B=R Input:  <Insert kW (kBh). >

3. Gas Input:  <Insert mL/s (cfh). >

4. Oil Input:  <Insert mL/s (gph). >

B. Blower:  Forward-curved, centrifugal fan integral to burner, directly driven by an electric motor; with adjustable, dual-blade damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If characteristics other than those in "Motors" Section are required, add subparagraphs below to suit Project.

1. Refer to Division 15 Section "Motors" for general requirements.

2. Minimum Motor Sizes:  <Insert horsepower. >

3. RPM:  3450.

4. Electrical Characteristics:  [120 V, single phase] [240 V, three phase], [460 V three-phase] 60 Hz.

5. Full-Load Amperes:  <Insert amperes. >

6. Minimum Circuit Ampacity:  <Insert amperes. >

7. Maximum Overcurrent Protection:  <Insert amperes. >

In paragraph below, retain any of three control sequences with any of three safety requirements.

C. Oil Supply:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [IRI] [FMG] [ASME CSD-1] [UL].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in subparagraph below to suit Project.

1. Two-stage, gear-type oil pump [integral to and directly driven by blower] shall be capable of producing 2100-kPa (300-psig) discharge pressure and 50.7-kPa (15-in. Hg) vacuum.  Include suction-line, manual, gate-type shutoff valve; removable-mesh-type oil strainer; 0- to 101.3-kPa (0- to 30-in. Hg) vacuum; 0- to 210-kPa (0- to 30-psig) vacuum-pressure gage; 0- to 2100-kPa (0- to 300-psig) oil-nozzle pressure gage; and nozzle-line, solenoid-safety-shutoff oil valve.

In first paragraph below, retain any of three control sequences with any of four safety requirements.

D. Gas Train:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [IRI] [FMG] [ASME CSD-1] [UL].
E. Gas Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with electronic supervision of burner flame.

F. Oil Pilot:  [Intermittent] [Interrupted]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid with [cadmium sulfide] [ultraviolet scanner] flame-safety control.

Retain below to decrease oxides of nitrogen emissions.

G. Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

H. Maximum Oxides of Nitrogen:  [20] <Insert amount> ppm.

2.9 HEATING-WATER BOILER TRIM

Delete this Article for steam boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (120 deg C).

A. All included devices shall be sized in accordance with ANSI B31.9, "Building Services Piping."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

B. Aquastat Controllers:  Operating [, firing rate,] and high limit.

C. Safety Relief Valve:  Relief Valve shall be ASME rated [210 kPa (30 psig)] [310 kPa (45 psig)] [517 kPa (75 psig)] <Insert kPa (psig)>.

Delete subparagraph below if capacities are scheduled on Drawings.

1. Pressure Setting:  Relief valve setting shall be<Insert kPa (psig). >

D. Altitude and Temperature Gage:  Combination altitude and temperature gauge shall have a minimum 89-mm- (3-1/2-inch-) diameter, combination water-pressure and temperature gage.  Gages shall have operating-pressure and -temperature ranges so normal operating range is at approximately 50 percent of full range.

E. Boiler Air Vent:  Shall be [Automatic] [Manual].

F. Drain Valve:  Shall be a minimum DN 20 (NPS 3/4) hose-end gate valve.

Retain paragraph below if pump is a component of water-tube boiler.  Coordinate with Division 15 Section "Hydronic Pumps."

G. Recirculating Pump:  Boiler recirculating pump shall be non-overloading, horizontal, in-line pump with[ rubber-mounted,] split- capacitor motor having thermal-overload protection and [oil] [grease] [system]-lubricated bearings; designed to operate at specified boiler pressures and temperatures.

Retain paragraph and subparagraphs below if expansion tank is a component of water-tube boiler.  Coordinate with Division 15 Section "Hydronic Piping."

H. Expansion Tank:  [The expansion tank shall be welded carbon steel, rated for operating pressure and temperature or minimum 860-kPa (125-psig) working pressure and 115 deg C (240 deg F) operating temperature.  Separate air charge from system water to maintain design expansion capacity by a flexible butyl-rubber bladder securely sealed into tank.  Include hose-end gate drain valve, pressure gage with minimum 75-mm (3-inch) dial, and air-charging fitting.  Factory fabricate and test tank with taps installed and labeled according to ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.]
Delete first two subparagraphs below if capacities are scheduled on Drawings.

1. Tank Volume:  <Insert L (gal.).>

2. Acceptance Volume:  <Insert L (gal.).>

3. Charging Pressure:  <Insert kPa (psig).>

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic-water heaters.

I. Tankless Heater:  Tankless water heater shall have a carbon-steel header with copper-tube heat exchanger, mounted in an upper port of cast-iron sections and sealed with fiber gasket.

1. Tappings DN 50 (NPS 2) and Smaller:  Threaded ends shall be in accordance with ASME B1.20.1 for pipe threads.

2. Tappings DN 65 (NPS 2-1/2) and Larger:  Flanged ends shall be in accordance with ASME B16.5 for steel and stainless-steel flanges and shall be in accordance with ASME B16.24 for copper and copper-alloy flanges.

Delete four subparagraphs below if capacities are scheduled on Drawings.

3. Minimum Water Flow:  <Insert L/s (gpm).>

4. Maximum Pressure Drop:  <Insert kPa (psig).>

5. Entering-Water Temperature:  <Insert deg C (deg F).>

6. Leaving-Water Temperature:  <Insert deg C (deg F).>

2.10 STEAM BOILER TRIM

Delete this Article for hot-water boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 15 psig (104 kPa).

A. All included devices shall be sized in accordance with ANSI B31.9, "Building Services Piping."

Retain option in paragraph below if using modulating or low-high-low firing sequence.

B. Pressure Controllers:  Operating[, firing rate,] and high limit.

Retain first paragraph and subparagraphs below if safety valve is a component of water-tube boiler.  Coordinate with Division 15 Section "Steam and Condensate Piping."

C. Safety Relief Valve:

1. Size and Capacity:  Relief valve shall be as required for equipment in accordance with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Delete first subparagraph below if capacities are scheduled on Drawings.

a. Pressure Setting:  <Insert kPa (psig).>

2. Bronze Safety Relief Valves:  Class 250, forged copper-alloy disc; fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

a. Drip-Pan Elbow:  Cast iron and having threaded inlet and outlet with threads in accordance with ASME B1.20.1.

D. Pressure Gage:  Pressure gage shall be a minimum 89-mm (3-1/2-inch) diameter, 0- to 210-kPa (0- to 30-psig) range.

E. Water Column:  Provide a minimum 300-mm (12-inch) glass gage with shutoff cocks.

F. Drain Valves:  Drain valves shall be a minimum DN 20 (NPS 3/4) or nozzle size with hose-end connection.

In first paragraph below, retain option if boiler operating pressure exceeds 100 psig (690 kPa).

G. Blowdown Valves:  Provide factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.  [Blowdown valves shall be combination of slow and quick acting as required by ANSI B31.1.]
H. Stop Valves:  Boiler inlets and outlets, except safety relief valves or pre-heater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and same size or larger than nozzle.  Valves larger than DN 50 (NPS 2) shall have rising stem.

Retain first paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

I. Stop-Check Valves:  Provide factory-installed stop-check valve at the boiler outlet with free-blow drain valve factory installed between the two valves and visible when operating as a stop-check valve.

Coordinate paragraph and subparagraphs below with other Division 15 Sections for domestic-water heaters.

J. Tankless Heater:  Tankless water heater shall have a carbon-steel header with copper-tube heat exchanger, mounted in an upper port of cast-iron sections and sealed with fiber gasket.

1. Tappings DN 50 (NPS 2) and Smaller:  Threaded ends shall be in accordance with ASME B1.20.1 for pipe threads.

2. Tappings DN 65 (NPS 2-1/2) and Larger:  Flanged ends shall be in accordance with ASME B16.5 for steel and stainless-steel flanges and shall be in accordance with ASME B16.24 for copper and copper-alloy flanges.

Delete four subparagraphs below if capacities are scheduled on Drawings.

3. Minimum Water Flow:  <Insert L/s (gpm).>

4. Maximum Pressure Drop:  <Insert kPa (psig).>

5. Entering-Water Temperature:  <Insert deg C (deg F).>

6. Leaving-Water Temperature:  <Insert deg C (deg F).>]

2.11 ELECTRIC MOTORS FOR BLOWERS

A. All electric motors used for blowers on burners and boiler trim pumps shall comply with the requirements of Section 11:  Energy Cost Budget Method and Table 10.2 of ASHRAE/IESNA Standard 90.1.

2.12 BURNER OPERATING CONTROLS

A. Description:  In order to maintain safe operating conditions, provide, as a minimum, the following burner safety controls to limit the operation of burner.

In subparagraph below, retain "pressure" option for steam boiler and "temperature" option for hot-water boiler.

1. High Cutoff:  [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design [pressure] [temperature].

In subparagraph below, retain first option for steam boilers and second option for hot-water boilers.

2. Low-Water Cutoff Switch:  [Float and electronic probe] [Electronic probe] shall prevent burner operation on low water.  Cutoff switch shall be [manual] [automatic]-reset type.

First two subparagraphs below apply only to atmospheric burners.  Some boilers may be equipped with only one of the following two switches.  Verify availability with boiler manufacturer.

3. Blocked Vent Safety Switch:  Manual-reset switch factory mounted on draft diverter.

4. Rollout Safety Switch:  Factory mounted on boiler combustion chamber.

5. Alarm Bell:  Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

2.13 BOILER OPERATING CONTROLS

Retain paragraph below if controls are specified in Division 15 Section "HVAC Instrumentation and Controls."

A. Control systems for new boilers installed into existing conditions shall interface with existing control systems while having the characteristics specified herein.  Boilers installed in new conditions shall interface with the controls specified in this section and Section 15900, “Building Automation Systems” and Section 15901, “Temperature Controls.”

Delete paragraph above and retain two paragraphs and associated subparagraphs below if controls are components of water-tube boilers.  Coordinate with Division 15 Section "HVAC Instrumentation and Controls."

B. Boiler operating controls shall be microprocessor-based and shall include the following devices and features:

1. Control Transformer:  115 V shall be fed from a single dedicated electric circuit.  Controls and other ancillaries shall be sub-fed from the boiler control panel.

2. Motorized Vent Damper:  Interlocked with burner to open before burner is operating.  If damper fails to open, stop burner operation.

Retain two subparagraphs below for steam boilers.

3. Operating Pressure Control:  Factory wired and mounted to cycle burner.

4. Low-Water Cutoff and Pump Control:  Cycle feedwater pump(s) for makeup water control.

Retain one of three subparagraphs below for operating control sequences.  Retain first subparagraph for steam boilers; second or third, for hot-water boilers.

5. Sequence of Operation:  Electric, factory-fabricated, and field-installed panel to control burner firing rate to maintain a constant steam pressure.  Maintain pressure set point plus or minus 10 percent.

6. Sequence of Operation:  Electric, factory-fabricated, and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

7. Sequence of Operation:  Electric, factory-fabricated, and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature.  At [minus 17 deg C (0 deg F)] <Insert temperature> outside-air temperature, set supply-water temperature at [93 deg C (200 deg F)] <Insert temperature>; at [15 deg C (60 deg F)] <Insert temperature> outside-air temperature, set supply-water temperature at [60 deg C (140 deg F)] <Insert temperature>.

Retain subparagraph below with any of three sequences retained above.

a. Include automatic, alternating-firing sequence for multiple boilers.

2.14 BUILDING AUTOMATION SYSTEM INTERFACE

A. The boiler manufacturer shall provide factory-installed DDC microprocessor based hardware and software to enable the Building Automation System (BAS) to monitor and control the boiler and to display the boiler status and alarms specified in this paragraph and else where in this specification.  The boiler controls shall interface seamlessly with other DDC microprocessor-based building subsystems as shown on the drawings and as specified in this and other sections of the specifications.  Interface shall be [BACnet compatible] [LONtalk compatible] [Electronic to match existing].

1. Any boiler application where the boiler controls interface with a Building Automation System (BAS) having [BACnet] [LONtalk/LONworks] [Controls to match existing] compatibility, the boiler shall be provided with a factory-mounted controller having [BACnet] [LONtalk/LONworks] [Controls to match existing] compatibility.  Control devices mounted on the boiler or otherwise used to measure, monitor, or control the boiler operations and functions shall have full [BACnet] [LONtalk/LONworks] [Controls to match existing] compatibility.  Controls and control devices associated with the boiler shall function with [BACnet] [LONtalk/LONworks] [Controls to match existing] compatibility without the need or used of gateways, product specific or proprietary devices.

B. The interface between the boiler controls and BAS shall enable the BAS to read as separate and discreet points significant values and alarms on the boiler.  Use of a single set of contacts to send an alarm will not be acceptable.  The contractor shall furnish and install necessary hardware, wiring, computing equipment and software, as defined in this specification and as required for the boiler to operate in accordance with the sequence of operation.

C. As a minimum the interface shall allow the following inputs, outputs and functions.

1. Boiler operating and alarm status.

2. Burner status.

3. Burner capacity.

4. Boiler [steam][water] pressure.

5. [Entering and leaving water temperatures][Steam pressure].

6. Boiler tripped by high/low pressure or high/low temperature or high/low fuel pressure or high/low water level.

7. Loss of electrical power.

8. Boiler [steam][water] flow.

2.15 VENTING KITS

Vent dampers are used only on boilers with atmospheric burners.

D. Vent Damper:  Motorized, 24-V ac, UL listed for use with standing pilot or intermittent ignition on atmospheric burner boiler equipped with draft hood.  Interlock vent damper with the burner.

Retain one of two paragraphs below if venting kit is a component of water-tube boiler.  Coordinate with Division 15 Section "Breechings, Chimneys, and Stacks."

Consider using ASTM A 959, Type 29-4C, stainless-steel vent kit if boiler efficiency exceeds 83 percent.

E. Kit:  [ASTM A 959, Type 29-4C, stainless-steel] [Stainless-steel], [horizontal] [vertical] vent terminal, [wall] [roof] passage thimble, indoor wall plate, vent adapter, condensate trap, and sealant.

F. Combustion-Air Intake:  Stainless-steel, [horizontal] [vertical] vent terminal with screen, inlet air coupling, and sealant.

Retain below only for boilers with efficiency less than 83 percent.

G. Chimney and Type B Vent Adapter:  Vent adapter and sealant.

2.16 SOURCE QUALITY CONTROL

A. The manufacturer shall test and inspect factory-assembled boilers, before shipping, in accordance with ASME Boiler and Pressure Vessel Code:  Section IV.

Retain paragraph below for factory-assembled water-tube boilers.

B. Burner and Hydrostatic Test:  The manufacturer shall factory adjust the burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen, and carbon monoxide in flue gas and set to achieve rated combustion efficiency; perform hydrostatic test.  Boiler shall be factory hydrostatically tested. 

Retain below if Owner wants to witness source quality-control testing.

C. Owner shall be allowed access to observe first-hand the quality-control testing of cast-iron boilers.  Architect shall be notified 14 days in advance of testing.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before the boiler is installed, examine rough-in conditions for concrete equipment bases, anchor-bolt sizes and locations, and venting, piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

1. Boiler locations indicated on the Drawings are approximate.  The contractor shall determine the exact locations before roughing-in for venting, piping and electrical connections.

B. The contractor shall examine mechanical spaces to verify suitable conditions exist where the boilers will be installed.  Proceed with the boiler installation only after unsatisfactory conditions have been corrected.

3.2 BOILER INSTALLATION

A. Install boilers level on a concrete base.  Concrete base shall be as specified in Division 15 Section "Basic Mechanical Materials and Methods," and concrete materials and installation shall be as specified in Division 3.

Revise paragraph and subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.

B. Concrete Bases:  Boilers shall be anchored to concrete base.

1. Install dowel rods to connect the concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 450-mm (18-inch) centers around the full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into the structural concrete floor.

3. Accurately place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Cast-in-place concrete materials and placement requirements shall be as specified in Division 3.

Retain first paragraph below for equipment supported on slabs-on-grade.

C. Vibration Isolation:  Rubber pads with a minimum static deflection of [6.35 mm (0.25 inch)] <Insert deflection> shall be utilized.  Vibration isolation devices and installation requirements shall be as specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

D. Install gas-fired boilers according to NFPA 54.

Retain paragraph above for gas-fired boilers and paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

E. Install oil-fired boilers according to NFPA 31.

Delete first two paragraphs below if boiler is delivered fully assembled.

F. Assemble boiler tubes in sequence and seal each tube joint.

G. Assemble and install boiler trim.

H. Install electrical devices furnished with boiler but not specified to be factory mounted.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements shall be as specified in other applicable Division 15 Sections.  The drawings indicate the general arrangement of piping, fittings, and specialties.

B. Connect gas piping full size to boiler gas-train inlet with a flanged or union-type connection.

Retain paragraph above for gas-fired boilers and first paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

C. Connect oil piping full size to burner inlet with shutoff valve and a flanged or union type connection.

D. Connect hot-water piping to the supply and return boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

E. Connect steam and condensate piping to the supply and return and blowdown-boiler tappings with shutoff valve and union or flange and joint at each connection.

F. Install piping from safety relief valves to nearest floor drain on heating water boilers.

Retain paragraph above for hot-water boilers and paragraph below for steam boilers.  Delete both if safety valves are specified in Division 15 Section "Steam and Condensate Piping" or "Hydronic Piping."

G. Install piping from safety valves to drip-pan elbow with the discharge of the valve through the roof and the drain piping to the nearest floor drain.

Edit first paragraph below to suit Project.  Delete option if vent is specified in this Section.

H. Connect breeching full size to boiler outlet. [ Refer to Division 15 Section "Breechings, Chimneys, and Stacks" for venting materials.]
I. Install flue-gas recirculation duct from vent to burner.  Refer to Division 15 Section "Breechings, Chimneys, and Stacks" for recirculation duct materials.

J. Install piping, venting, wiring and ancillaries adjacent to boiler in an approved arrangement to allow complete service and maintenance.

K. Ground equipment according to Division 16 Section "Grounding and Bonding."

L. Connect wiring according to Division 16 Section "Conductors and Cables."

M. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.4 STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

A. The contractor shall engage a factory-authorized service representative to test, inspect, and adjust the boiler, its components and the equipment installation and to perform startup services.

B. Perform installation and startup checks according to manufacturer's written instructions.

C. Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

D. Operational Test:  Start units to confirm proper motor rotation and unit operation.  Adjust air-fuel ratio and combustion controls.

E. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Retain first paragraph below for field-assembled water-tube boilers.

F. Burner Test:  Adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen, and carbon monoxide in flue gas and to achieve rated combustion efficiency.

G. Adjust initial temperature set points.

H. Set field-adjustable switches and circuit breaker trip ranges as indicated.

I. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting the system to suit actual occupied conditions.  Provide up to two visits to the site outside of normal occupancy hours for this purpose, without additional cost to the Owner.

J. Prepare a written report that documents the testing procedures and their results.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain water-tube boilers.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15515

WATER-TUBE BOILERS
15515 – 1

