Copyright 1998 AIA
GSA VERSION MASTERSPEC
6/98 (GSA 03/04)

Copyright 1998 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15520 - FEEDWATER EQUIPMENT
-------------------------------------------------------------------------------------------------------------------------------

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

-------------------------------------------------------------------------------------------------------------------------------

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

-------------------------------------------------------------------------------------------------------------------------------Adjust list below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Feedwater pumps and receivers.

2. Vacuum type feedwater pumps and receivers.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated.  Include manufacturer's technical Product Data; rated capacity of selected model; temperature and net positive suction head required characteristics; pump performance curve with selection points clearly indicated; shipping, installed, and operating weights; furnished specialties; and accessories.

B. Shop Drawings:  Detail fabrication and installation and indicate dimensions, weights, loadings, required clearances, method of field assembly, and components.

1. Wiring Diagrams:  Power, signal, and control wiring.  Differentiate between manufacturer installed and field installed wiring.

C. Maintenance Data:  For feedwater units to include in maintenance manuals specified in Division 1.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below if Project is located in a seismic zone.

-------------------------------------------------------------------------------------------------------------------------------

D. Manufacturer Seismic Qualification Certification:  Submit certification that feedwater units will withstand seismic forces possible at Project site.  Include the following:

1. Basis of Certification:  Indicate whether certification is based on actual test of assembled components or on calculation.

-------------------------------------------------------------------------------------------------------------------------------The subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Optional definition is used for essential facilities where equipment must operate immediately after an earthquake.

-------------------------------------------------------------------------------------------------------------------------------

2. The term "withstand" means "the unit will remain in place without separation of internal and external parts during a seismic event [and the unit will be fully operational after the event]."

3. Dimensioned Outline Drawings of Equipment:  Identify center of gravity and locate and describe mounting and anchorage provisions.

4. Detailed description of equipment anchorage devices on which certification is based and their installation requirements.

1.4 QUALITY ASSURANCE

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Revise below to identify specific proprietary system or indicate on Drawings.  Correlate with Division 1 requirements.

-------------------------------------------------------------------------------------------------------------------------------

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of feedwater units and are based on the specific types and models indicated.  Other manufacturers' products complying with requirements may be considered.  Refer to Division 1 Section "Substitutions."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Preparation for Shipping:  Clean flanges and exposed metal surfaces and treat with anticorrosion compound after assembly and testing.  Protect flanges, pipe openings, and nozzles with wooden flange covers or with screwed in plugs.

B. Store units in dry location.

C. Retain protective flange covers and machined surface protective coatings during storage.

D. Protect bearings and couplings against damage from sand, grit, and other foreign matter.

E. Comply with manufacturer's written rigging instructions.

1.6 COORDINATION

A. Coordinate size and location of concrete base.  Cast anchor bolt inserts into base.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Section "Cast-in-Place Concrete."

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Feedwater Units:

a. Alyan Pump.

b. Aurora/Pentair Pump Group.

c. BFS Industry Incorporated.

d. Bryan Boilers; Bryan Steam Corp.

e. Burnham.

f. Cleaver-Brooks; Div. of Aqua-Chem, Inc.

g. Deaerator Designs.

h. Dixon Boiler Works.

i. Donlee Technologies, Inc.; Boiler Div.

j. Flotronics, Inc.

k. Fulton.

l. Gerow Equipment Co.; Pump & Hydraulic Division.

m. Hurst Boiler & Welding Co., Inc.

n. ITT Fluid Handling; ITT Fluid Technology Corp.

o. Kewanee Boiler Manufacturing Co.

p. Lattner Boiler Manufacturing Co.

q. Lockwood Products, Inc.

r. MEPCO (Marshall Engineering Products Co.).

s. Parker Boiler Co.

t. PVI Industries Inc.

u. Roth Pump Co.; a subsidiary of Roy E. Roth Co.

v. Sellers Engineering Co.

w. Shippensburg Pump Co., Inc.

x. Skidmore.

y. Smith-Koch, Inc.

z. Stickle Steam Specialties.

aa. Superior Boiler Works, Inc.

ab. U.S. Deaerator Co.

ac. U.S. Filter.

2. Vacuum Producers:

a. Alyan Pump.

b. Dixon Boiler Works.

c. Flotronics, Inc.

d. ITT Fluid Handling; ITT Fluid Technology Corp.

e. Lockwood Products, Inc.

f. MEPCO (Marshall Engineering Products Co.).

g. Shippensburg Pump Co., Inc.

h. Skidmore.

i. U.S. Deaerator Co.

j. U.S. Filter.

2.2 FEEDWATER UNITS

A. Description:  Factory assembled and tested unit consisting of a condensate receiver, feedwater pumps, controls, and the following features and accessories:

1. [Liquid filled][Dial type] thermometer graduated in both Fahrenheit and Celsius.

2. Gage glass with stops at top and bottom.

3. Inlet strainer.

4. Lifting eyes.

5. Companion flanges.

6. Pump discharge check valve.

7. Pump discharge pressure gauge.

8. Pump suction isolation valve.

9. Pump discharge isolation valve.

-------------------------------------------------------------------------------------------------------------------------------Select mechanical or electrical makeup-water control from subparagraph below.

-------------------------------------------------------------------------------------------------------------------------------

10. Makeup Water Assembly:  [Float operated, makeup water valve] [Electric level switch and piston operated, packless, solenoid valve]; inlet strainer; and three valve bypass.

11. Feedwater Heater:  Sparge tube, thermostat, and control valve.

-------------------------------------------------------------------------------------------------------------------------------Select pipe schedule from subparagraph below.

-------------------------------------------------------------------------------------------------------------------------------

12. Factory Furnished Pipe, DN 65 (NPS 2 1/2) and Smaller:  ASTM A 53, Type S (seamless), Grade A, Schedule  [40] [80], with threaded joints and malleable iron fittings of class to match pressure rating of pipe.

13. Factory Furnished Pipe, DN 75 (NPS 3) and Larger:  ASTM A 53, Type E (electric resistance welded), Grade A, Schedule  [40] [80], with welded joints and malleable iron fittings of class to match pressure rating of pipe.

B. Receiver Material:  [Close grain cast iron] [Welded steel].

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below for welded steel receivers only and select finish.

-------------------------------------------------------------------------------------------------------------------------------

1. Finish:  [Painted exterior] [Galvanized after fabrication] [Epoxy coated with electrolytic corrosion inhibitor anode].

-------------------------------------------------------------------------------------------------------------------------------Retain applicable subparagraphs below.  Do not specify both electrolyte anode and a lining.

-------------------------------------------------------------------------------------------------------------------------------

2. Interior Finish:  [Galvanized][Epoxy coated][with electrolyte corrosion-inhibiting anode].

3. Arrangement:  [Recessed below floor] [Floor mounted].

-------------------------------------------------------------------------------------------------------------------------------Modify language in subparagraph below if Project is located in a seismic area.

-------------------------------------------------------------------------------------------------------------------------------

4. Mounting Frame:  Structural steel stand to support receiver and pumps.  [Fabricate stand with bracing adequate for seismic forces according to authorities having jurisdiction and to allow anchoring mounting frame to floor.]

-------------------------------------------------------------------------------------------------------------------------------Select one of two paragraphs and associated subparagraphs below and edit for desired pump construction.

-------------------------------------------------------------------------------------------------------------------------------

C. Vertical Feedwater Pump:  Flange mounted, closed coupled, [single stage,] [multi stage,] radially split case design centrifugal pump; rated for 1200 kPa (175 psig) minimum working pressure and a continuous water temperature of 107 deg C (225 deg F); with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Seals:  Mechanical.

3. Motor:  [Open dripproof] [Totally enclosed fan cooled].  Comply with requirements in Division 15 Section "Motors."

D. Horizontal Feedwater Pump:  Base mounted, [single stage,] [multi stage,] [radially][horizontally] split case design centrifugal pump; rated for 1200 kPa (175 psig) minimum working pressure and a continuous water temperature of 107 deg C (225 deg F); with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Coupling:  [Close] [Flexible].

3. Seals:  Mechanical.

4. Motor:  [Open dripproof] [Totally enclosed fan cooled].  Comply with requirements in Division 15 Section "Motors."

E. Feedwater Pump Control Panel:  Unit mounted, factory wired, and including the following:

1. NEMA 250, Type 2 enclosure.

2. Combination magnetic starters for each pump, with three overload relays, [fused disconnect switch] [circuit breaker], and cover interlock.

3. Numbered terminal block.

4. Removable control mounting plate.

5. Electric alternator for duplex units.

6. Pilot lights for pump running and alarm.

7. Alarm bell and silence switch.

8. Elapsed time run meter, graduated in hours.

9. Fusible, control circuit transformer where motor voltage exceeds 130 V.

10. Native BACnet , ASHRAE 135, microprocessor controls to be factory installed, supplied by Division 15 Sections "Building Automation System" and “Temperature Controls”.
F. Factory-installed, [native BACnet, ASHRAE 135,][ or ][LonWorks compatible] self-contained microprocessor controls specified under Division 15 Sections "Building Automation System" and “Temperature Controls” to communicate with central system.

-------------------------------------------------------------------------------------------------------------------------------Select one of three paragraphs below.  Select first for simplex feedwater system, single feedwater pump.  Select second for duplex pump units with operating and standby pumps.  Select third for modulating level control valve.

-------------------------------------------------------------------------------------------------------------------------------

G. Feedwater Pump Control Sequence:  Boiler water level controller starts simplex unit with momentary test push button.  Low level receiver float switch opens makeup water solenoid valve.

H. Feedwater Pump Control Sequence:  Boiler water level controller starts lead pump; alternator switches lead and lag pumps after each cycle.  Low level receiver float switch opens makeup water solenoid valve.

I. Feedwater Pump Control Sequence:  Lead pump runs continuously; boiler water level controller modulates feedwater control valve; electric interlock with boiler control starts lead pump when boiler starts.  Low level receiver float switch opens makeup water solenoid valve.

2.3 FACTORY INSULATION

-------------------------------------------------------------------------------------------------------------------------------Factory applied insulation and jacket should be limited to assemblies less than 3.7 meters (12 feet) in height as shipping methods risk damage.

-------------------------------------------------------------------------------------------------------------------------------

A. Insulation.

1. Type:  fiberglass blanket.

2. Thickness:  50 mm (2 inches).

3. Density:  <Insert Number> (1 lb. per cubit foot).

4. Resistance:  R-3.

B. Jacket:  0.75 mm (22 gauge) steel.

2.4 VACUUM PRODUCER

A. Description:  Receiver mounted, consisting of multijet vacuum producer, centrifugal pump and motor assembly mounted on separation chamber, and automatic pressure and water temperature controls.  Include the following accessories:

1. Thermometer:  [Liquid filled] [Dial type] register in Celsius (Fahrenheit).

2. Vacuum Gage:  Dial type register in millimeters of mercury (inches of mercury).

3. Gage Glass:  Stops top and bottom.

4. Air suction check valve.

5. Lifting eyes.

6. Companion flanges.

7. Low water cutoff switch.

8. Cooling Water Control:  Aquastat, inlet strainer; and packless, piston pilot, electric solenoid valve.

9. Air vent.

10. Overflow Drain:  Overflow drain from vacuum producer receiver.

B. Factory Furnished Pipe, DN 65 (NPS 2 1/2) and Smaller:  ASTM A 53, Type S (seamless), Grade A, Schedule  [40] [80], with threaded joints and malleable iron fittings of class to match pressure rating of pipe.

C. Factory Furnished Pipe, DN 75 (NPS 3) and Larger:  ASTM A 53, Type E (electric resistance welded), Grade A, Schedule  [40] [80], with welded joints and malleable iron fittings of class to match pressure rating of pipe.

D. Receiver Material:  [Close grained cast iron] [Welded steel].

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below for welded steel receivers only and select finish.

-------------------------------------------------------------------------------------------------------------------------------

1. Finish:  [Painted exterior] [Epoxy coated with electrolytic corrosion inhibitor anode].

-------------------------------------------------------------------------------------------------------------------------------Select one of two paragraphs and associated subparagraphs below and edit for desired pump construction.

-------------------------------------------------------------------------------------------------------------------------------

E. Vertical Vacuum Producer Pump:  Flange mounted, closed coupled, single stage, radially split case design centrifugal pump; rated for 1200 kPa (175 psig) minimum working pressure and a continuous water temperature of 107 deg C (225 deg F); with the following features:

1. Impeller:  Bronze.

2. Shaft:  Stainless steel.

3. Seals:  Mechanical.

4. Motor:  [Open dripproof] [Totally enclosed fan cooled].  Comply with requirements in Division 15 Section "Motors."

F. Horizontal Vacuum Producer Pump:  Base mounted, single stage, radially split case design centrifugal pump; rated for 1200 kPa (175 psig) minimum working pressure and a continuous water temperature of 107 deg C (225 deg F); with the following features:

1. Impeller:  Bronze.

2. Shaft:  Stainless steel.

3. Coupling:  [Close] [Flexible].

4. Seals:  Mechanical.

5. Motor:  [Open dripproof] [Totally enclosed fan cooled].  Comply with requirements in Division 15 Section "Motors."

G. Vacuum Unit Control Panel:  Unit mounted, factory wired, and including the following:

1. NEMA 250, Type 2 enclosure.

2. Compliant with UL standards.

3. Combination magnetic starters for each air pump, with three overload relays, [fused disconnect switch] [circuit breaker] and cover interlock.

4. Vacuum Switches for Simplex Vacuum Producer Pumps:  Include pressure adjustment, and test push button.  Factory set to operate pump between 75 and 150 mm (3 and 6 inches) of mercury.

5. Vacuum Switches for Duplex Vacuum Producer Pumps:  Include pressure adjustment, and test push button.  Factory set so one pump operates for 10.1 to 16.9 kPa (3 to 5 inches of mercury) and both pumps operate for 13.5 to 20.2 kPa (4 to 6 inches of mercury).

6. Numbered terminal block.

7. Removable control mounting plate.

8. Electric alternator for duplex units.

9. Pilot lights for pump running and alarm.

10. Alarm bell and silence switch.

11. Elapsed time run meter, graduated in hours.

12. Fusible control circuit transformer where motor voltage exceeds 130 V.

13. Native BACnet , ASHRAE 135, microprocessor controls to be factory installed, supplied by Division 15 Sections "Building Automation System" and “Temperature Controls”.
H. Vacuum Producer Control Sequence:  Cycle pumps to maintain vacuum pressure set point.

2.5 SOURCE QUALITY CONTROL

-------------------------------------------------------------------------------------------------------------------------------Select one ASME code below for high- or low-pressure system as required by Project.

-------------------------------------------------------------------------------------------------------------------------------

A. ASME Compliance:  [ASME B31.1, "Power Piping," for high pressure systems more than 15 psig (104 kPa)] [ASME B31.9, "Building Services Piping," for low pressure systems equal to or less than 15 psig (104 kPa)].  Safety valves and pressure vessels shall bear the appropriate ASME label.

B. Test performance and certify test results on feedwater unit, according to ASME PTC 12.1, "Closed Feedwater Heaters."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine equipment foundation and anchor bolt locations for compliance with requirements for installation and other conditions affecting performance.

B. Examine rough in for condensate return piping systems to verify actual locations of piping connections before equipment installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install unit level and plumb and to permit access for maintenance.

B. Support piping independent of pumps.

C. Install base mounted pumps on concrete bases with grouted base frames.

D. Install parts and accessories shipped loose.

3.3 CONNECTIONS

-------------------------------------------------------------------------------------------------------------------------------Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

-------------------------------------------------------------------------------------------------------------------------------

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Connect makeup water piping and cooling water piping with reduced pressure backflow preventers.

D. Install overflow drain piping to nearest floor drain.

E. Install vents and extend to outdoors; terminate with elbow turned down and an insect screen.

F. Ground equipment.

1. Tighten electrical connectors and terminals according to manufacturer's published torque tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

G. Connect to Building Automation System.

3.4 FIELD QUALITY CONTROL

-------------------------------------------------------------------------------------------------------------------------------Retain one of two paragraphs below.  Retain "Manufacturer's Field Service" Paragraph if field quality control testing is performed by manufacturer's service representative.

-------------------------------------------------------------------------------------------------------------------------------

A. Testing:  Perform the following field quality control testing:

1. After installing unit and after electrical circuitry has been energized, test for compliance with requirements.

B. Repair or replace malfunctioning units.  Retest as specified above after repairs or replacements are made.

C. Manufacturer's Field Service:  Engage a factory authorized service representative to perform the following:

1. Inspect field assembled components, equipment installation, and piping and electrical connections for compliance with manufacturer's written instructions.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3. Check bearing lubrication.

4. Verify proper motor rotation.

5. Start up service.

6. Report results in writing within 10 working days.
3.5 ADJUSTING

A. Adjust boiler water level controls to properly stage unit.

B. Set field adjustable makeup water and cooling water controls.

3.6 CLEANING

A. Clean equipment internally; remove coatings applied for protection during shipping and storage, foreign material, and oily residue according to manufacturer's written instructions.

B. Clean strainers.

3.7 DEMONSTRATION

A. Engage a factory authorized service representative, specified in Section 01700 “Execution Requirements”,  to train Owner's maintenance personnel for [a minimum of] [1 hour] [2] [4] <Insert Number Here > hours to adjust, operate, and maintain units.  Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment and schedules.

1. Review data in maintenance manuals.  Refer to Division 1 Section, "Contract Closeout."

-------------------------------------------------------------------------------------------------------------------------------Delete subparagraph above or below depending on which Section is retained in Division 1.

-------------------------------------------------------------------------------------------------------------------------------

2. Review data in maintenance manuals.  Refer to Division 1 Section, "Operation and Maintenance Data."

3. Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION 15520

FEEDWATER EQUIPMENT
15520 - 6

