Copyright 2000 AIA
GSA VERSION MASTERSPEC
9/00 (GSA 03/04)

Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15555 - DRAFT CONTROL DEVICES
-------------------------------------------------------------------------------------------------------------------------------Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

-------------------------------------------------------------------------------------------------------------------------------

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

1. Draft inducer fans.

2. Venturi draft inducer fans.

3. Mechanical draft vent fans.

4. Vent exhaust fans.

5. Barometric dampers.

6. Vent dampers.

7. Combustion air fans.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  Show fabrication and installation details for [fans] [dampers] [fans and dampers].  Include plans, elevations, sections, details, and attachments to other work.  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, hangers and seismic restraints, and location and size of each field connection.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below if equipment includes wiring.

-------------------------------------------------------------------------------------------------------------------------------

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Operation and Maintenance Data:  For draft control devices to include in emergency, operation, and maintenance manuals.

D. Warranties:  Special warranties specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 WARRANTY

------------------------------------------------------------------------------------------------------------------------------- Coordinate with Division 1 Section, "Product Requirements".

-------------------------------------------------------------------------------------------------------------------------------

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of [draft inducer fans] [venturi draft inducer fans] [mechanical draft vent fans] [vent exhaust fans] [barometric dampers] [vent dampers] [combustion air fans] that fail in materials or workmanship within specified warranty period.

1. Failures include failure of the fan due to corrosion.

-------------------------------------------------------------------------------------------------------------------------------Verify available warranties for units and components and insert number below.

-------------------------------------------------------------------------------------------------------------------------------

2. Warranty Period:  [Two] [10] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2.2 DRAFT INDUCER FANS

A.  Available Manufacturers:

1. Babco Inc.

2. Bramec Corporation.

3. Effikal International Inc.

4. EXHAUSTO, Inc.

5. FAMCO.

6. Field Controls L.L.C.; the Venting Solutions Company.

7. Quickdraft; a Litzler Company.

8. Snappy Air Distribution Products.

9. Tec-Air, Inc.

10. Tjernlund Products Inc.

11. Tutco; Subsidiary of Smiths Industries.

12. Wing Draft Inducers; Subsidiary of Smiths Industries.

13. <Insert manufacturer's name.>

B. Fan Construction:  Galvanized steel housing and radial blade centrifugal fan.

1. Fan Motor:  Permanent split capacitor type.

C. Controls:

1. Draft proving switch.

2. Control kit to cycle fan with gas flow to a single burner.

2.3 VENTURI DRAFT INDUCER FANS

A.  Available Manufacturers:

1. Quickdraft; a Litzler Company.

2. <Insert manufacturer's name.>

B. Fan Construction:  Enameled steel venturi tube for vents 508 mm (20 inches) in diameter and smaller, and ASTM A 666, Type 304 stainless steel venturi tube for vents 559 to 1219 mm (22 to 48 inches) in diameter.  [Galvanized] [Enameled] steel fan housing with radial blade centrifugal wheel.

1. Fan Motor:  Permanent split capacitor type.

C. Controls:

1. Draft proving switch.

2. Control kit to cycle fan with gas flow to a single burner.

2.4 MECHANICAL DRAFT VENT FANS

A.  Available Manufacturers:

1. Babco Inc.

2. Bramec Corporation.

3. Effikal International Inc.

4. EXHAUSTO, Inc.

5. FAMCO.

6. Field Controls L.L.C.; the Venting Solutions Company.

7. Quickdraft; a Litzler Company.

8. Snappy Air Distribution Products.

9. Tec-Air, Inc.

10. Tjernlund Products Inc.

11. Tutco; Subsidiary of Smiths Industries.

12. Wing Draft Inducers; Subsidiary of Smiths Industries.

13. <Insert manufacturer's name.>

B. Fan Construction:  Forward curved centrifugal fan and scroll fabricated of galvanized steel; with direct drive, ball bearing motor lubricated with synthetic oil; internal cooling fan; stainless steel shaft; and integral pressure sensing switch.

1. Fan Motor:  Permanent split capacitor type.

C. Controls:

1. Draft proving switch.

2. Control kit to cycle fan with gas flow to [a single] [multiple] burner(s).

D. Accessories: 

1. Stainless steel wall vent hood.

2.5 VENT EXHAUST FANS

A.  Available Manufacturers:

1. EXHAUSTO, Inc.

2. Field Controls L.L.C.; the Venting Solutions Company.

3. Tjernlund Products Inc.

4. <Insert manufacturer's name.>

B. General:  Centrifugal fan with [variable] [constant] speed control mounted at end of [sidewall] [vertical] vent.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for fans exposed to flue gases up to 640 deg F (337 deg C).

-------------------------------------------------------------------------------------------------------------------------------

C. Test Standard:  UL 378.

-------------------------------------------------------------------------------------------------------------------------------Some manufacturers have cast aluminum or stainless steel wheels available only in certain size ranges.  Verify options with manufacturer selected.

-------------------------------------------------------------------------------------------------------------------------------

D. Fan Construction:  [Galvanized steel] [Stainless steel] housing [painted manufacturer's standard color of baked enamel].  [Galvanized] [Stainless steel] vent. [Stainless steel] wheel.  Backward inclined centrifugal or axial fan wheel statically and dynamically balanced.  Provide access to clean the discharge area.[ Concentric makeup air inlet duct surrounding the vent to allow zero clearance to combustibles.]

E. Motor:  Fully enclosed,[ variable speed duty,] permanent split capacitor, out of the airstream, with prelubricated and sealed ball bearings.

F. Constant Speed Controls:  Boiler interlock relay starts fan when burner control cycles on.  Pressure switch permits burner operation via interlock with boiler.  Fan proving switch is adjustable between minus 17 and minus 37 Pa (minus 0.07 and minus 0.15 inch wg).

-------------------------------------------------------------------------------------------------------------------------------Retain only one of the paragraphs either above or below.

-------------------------------------------------------------------------------------------------------------------------------

G. Variable Speed Controls:  Boiler interlock relay starts fan when burner control cycles on.  Constant pressure regulator and 120 V transformer and controls for automatic modulation of fan speed maintain preset negative pressure between 0 and minus 249 Pa (0 and minus 1.0 inch wg).  Include indicator lights, XT-sensor, chimney probe, and fan proving switch adjustable between minus 17 and minus 37 Pa (minus 0.07 and minus 0.15 inch wg).  Include probe and tubing.

2.6 BAROMETRIC DAMPERS

A.  Available Manufacturers:

1. Babco Inc.

2. Bramec Corporation.

3. Effikal International Inc.

4. FAMCO.

5. Field Controls L.L.C.; the Venting Solutions Company.

6. Quickdraft; a Litzler Company.

7. Snappy Air Distribution Products.

8. Tec-Air, Inc.

9. Tjernlund Products Inc.

10. Tutco; Subsidiary of Smiths Industries.

11. Wing Draft Inducers; Subsidiary of Smiths Industries.

12. <Insert manufacturer's name.>

B. Damper Construction:  High temperature enamel painted steel damper and housing with galvanized steel breeching connection.  Adjustable counterweight with lock.  Include knife edge bearings that do not require lubrication.

2.7 VENT DAMPERS

A.  Available Manufacturers:

1. Effikal International Inc.

2. Field Controls L.L.C.; the Venting Solutions Company.

3. Johnson Controls, Inc.; Controls Group.

4. <Insert manufacturer's name.>

B. Damper Construction:  Stainless steel damper blade, shaft, and vent pipe with metal, prelubricated bearings.

1. 24 V ac motor sized to power damper open and closed in approximately 15 seconds in each direction.  Power is off when damper is at rest.

2. Comply with ANSI Z21.66.

C. Controls:

1. 115 V to 24 V control transformer.

2. Keyed wiring harness.

3. Damper end switch to prove damper is open.

4. Interlock with boiler to permit burner operation when damper is open.

5. Hold open switch for troubleshooting boiler controls.

6. Factory-installed, [native BACnet, ASHRAE 135,][ or ][LonWorks compatible] self-contained microprocessor controls specified under Division 15 Sections "Building Automation System" and “Temperature Controls” to communicate with central system.

2.8 COMBUSTION AIR FANS

A.  Available Manufacturers:

1. EXHAUSTO, Inc.

2. Field Controls L.L.C.; the Venting Solutions Company.

3. Tjernlund Products Inc.

4. <Insert manufacturer's name.>

B. Fan Construction:  Galvanized steel housing; with steel forward curved fan and scroll; direct drive, totally enclosed, fan cooled, shaded pole motor with ball bearings; stainless steel shaft; and integral pressure sensing switch.

1. Fan Motor:  [115] [208] [230] V, single phase motor.

C. Controls:

1. Fan proving switch to permit burner operation when combustion air fan is operating.

2. Multiple appliance control starts fan with operation of any one of [three] [four] appliances.

3. Modulating control in response to pressure differential.

4. Manual reset, high limit switch stops operation with 71 deg C (160 deg F) room temperature.

5. Optional Controls:

a. Alarm circuit.

b. Low limit.

c. Interface relay for vent exhaust fan, draft inducer fan, or mechanical draft vent fan.

d. Galvanized intake hood.

e. Factory-installed, native BACnet , ASHRAE 135, microprocessor specified by Division 15 Section "Building Automation System" and “Temperature Controls”.

2.9 MOTORS

-------------------------------------------------------------------------------------------------------------------------------Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section, "Motors".  If characteristics other than these are required, add paragraphs below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

A. Comply with requirements in Division 15 Section, "Motors."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install listed components in a manner conforming to the listing.

B. Secure barometric dampers to breechings with hardware compatible with connected materials.

C. Locate barometric and motorized vent dampers as close to draft hood collar as possible.

D. Secure barometric and motorized vent dampers to appliances, breechings, or chimneys with hardware compatible with connected materials.

-------------------------------------------------------------------------------------------------------------------------------Retain three paragraphs below if using draft inducer fans.

-------------------------------------------------------------------------------------------------------------------------------

E. Install draft inducer fans in single wall vent section that is designed to couple with other vent materials.

F. Secure draft inducer fans to appliances, breechings, or stacks with hardware compatible with connected materials.

G. Install draft inducer fans with clearances for service and maintenance.

-------------------------------------------------------------------------------------------------------------------------------Retain below for combustion-air fans.

-------------------------------------------------------------------------------------------------------------------------------

H. Install PVC intake duct that is sized according to manufacturer's written instructions.

3.2 CONNECTIONS

A. Ground equipment according to Division 16 Section "Grounding and Bonding."

B. Connect wiring according to Division 16 Section "Conductors and Cables."

3.3 STARTUP SERVICE

-------------------------------------------------------------------------------------------------------------------------------Delete this Article if factory authorized service representative is not required.

-------------------------------------------------------------------------------------------------------------------------------

A. Engage a factory authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. <Insert startup steps if any.>

B. Remove and replace malfunctioning components and recheck.

3.4 ADJUSTING

A. Set field adjustable switches and controls.

3.5 DEMONSTRATION

A. Engage a factory authorized service representative, specified in Section 01700 “Execution Requirements”, to train Owner's maintenance personnel for [a minimum of] [1 hour] [2] [4] <Insert Number Here > hours to adjust, operate, and maintain draft control devices.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15555

DRAFT CONTROL DEVICES
15555 - 6

