Copyright 2000 AIA
GSA VERSION MASTERSPEC
12/00 (GSA 03/04)

Copyright 2000 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15840 - AIR TERMINAL UNITS
-------------------------------------------------------------------------------------------------------------------------------Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

-------------------------------------------------------------------------------------------------------------------------------

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

-------------------------------------------------------------------------------------------------------------------------------Adjust list below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Bypass single duct air terminal units

2. Fan-powered air terminal units.

3. Induction air terminal units.

4. Shutoff single duct air terminal units.

5. Integral diffuser air terminal units.

B. Related Sections include the following:

-------------------------------------------------------------------------------------------------------------------------------List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

-------------------------------------------------------------------------------------------------------------------------------

1. Division 15 Sections, "Building Automation Systems” and “Temperature Controls” for control devices including thermostats.

2. Division 15 Section, "Sound Control Devices" for air transfer boots.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated, include rated capacities, furnished specialties, sound power ratings, and accessories.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field connection.

1. Include a schedule showing unique model designation, room location, model number, size, and accessories furnished.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below if equipment includes wiring.

-------------------------------------------------------------------------------------------------------------------------------

2. Wiring Diagrams:  Power, signal, and control wiring.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

-------------------------------------------------------------------------------------------------------------------------------

C. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

-------------------------------------------------------------------------------------------------------------------------------Edit subparagraphs below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Ceiling suspension assembly members.

2. Method of attaching hangers to building structure.

3. Size and location of initial access modules for acoustical tile.

4. Ceiling-mounted items including lighting fixtures, diffusers, grilles, speakers, sprinklers, access panels, and special moldings.

D. Operation and Maintenance Data:  For air terminal units to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1 Section, "[Closeout Procedures] [Operation and Maintenance Data]," include the following:

1. Instructions for resetting minimum and maximum air volumes.

2. Instructions for adjusting software set points.

1.4 QUALITY ASSURANCE

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

-------------------------------------------------------------------------------------------------------------------------------

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of air terminal units and are based on the specific system indicated.  Refer to Division 1 Section, "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. NFPA Compliance:  Install air terminal units according to NFPA 90A, "Standard for the Installation of Air Conditioning and Ventilating Systems."

D. Compliance: UL Standards.
E. ARI Compliance:  Certified under ARI 880; Units shall bear ARI seal.
1.5 DELIVERY, STORAGE AND HANDLING
A. Contractor shall receive, store and deliver to the jobsite the materials for this project.
B. Materials, which are to be specified to be factory mounted in equipment furnished by others, such as components for terminal equipment, shall be shipped directly to the manufacturer of that equipment for factory installation.

1.6 COORDINATION

-------------------------------------------------------------------------------------------------------------------------------Edit this Article to delete or add types of construction that penetrate or are supported by ceilings.

-------------------------------------------------------------------------------------------------------------------------------

A. Coordinate layout and installation of air terminal units and suspension system with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2.2 BYPASS SINGLE DUCT AIR TERMINAL UNITS

A.  Available Manufacturers:

1. Carnes.

2. Krueger.

3. METALAIRE, Inc.; Metal Industries Inc.

4. Nailor Industries of Texas Inc.

5. Price Industries.

6. Titus.

7. <Insert manufacturer's name.>

B. Configuration:  Diverting damper assembly inside unit casing with control components located inside a protective metal shroud.

C. Casing:  0.85 mm (0.034 inch) steel, double-walled.
D. Casing Insulation:  25-mm-(1-inch-) thick, coated, fibrous-glass complying with ASTM C 1071; secured with adhesive.

E. Air Inlet:  Round stub connection for duct attachment.

F. Air Outlet:  S-slip and drive connections.

G. Access:  Removable panels for access to diverter and other parts requiring service, adjustment, or maintenance; with airtight gasket.

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for units with mechanical volume regulators.

-------------------------------------------------------------------------------------------------------------------------------

H. Diverter Assembly:  [Galvanized steel gate, with polyethylene linear bearings] [Aluminum blade, with nylon fitted pivot points].

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below for multi-outlet section, or indicate number of outlets and outlet sizes on Drawings or in a schedule.

-------------------------------------------------------------------------------------------------------------------------------

I. Multi outlet Attenuator Section:  With [two] [three] [four] <Insert number> [150 mm (6 inch )] [200 mm (8 inch )] [250 mm (10 inch )] diameter collars; each with locking butterfly balancing damper.

-------------------------------------------------------------------------------------------------------------------------------If heating coil is required, retain one of two paragraphs below.  PBS-P100 restricts zones where hot-water coils can be used

-------------------------------------------------------------------------------------------------------------------------------

J. Hot-Water Heating Coil:  Copper tube, mechanically expanded into copper plate fins; leak tested underwater to 1380 kPa (200 psig); and factory installed.

-------------------------------------------------------------------------------------------------------------------------------Use of electric heating coils is restricted and must be authorized by the Office of the Chief Architect.

-------------------------------------------------------------------------------------------------------------------------------

K. Electric Heating Coil:  Slip-in type, open coil design with integral control box factory wired and installed.  Include the following features:

1. Primary and secondary overtemperature protection.

-------------------------------------------------------------------------------------------------------------------------------Retain applicable subparagraphs below.

-------------------------------------------------------------------------------------------------------------------------------

2. Nickel chrome 80/20 heating elements.

3. Airflow switch.

4. Non interlocking disconnect switch.

5. Fuses (for coils more than 48 A).

6. SCR temperature control

7. Mercury contactors.

8. Pneumatic electric switches and relays.

9. Magnetic contactor for each step of control (for three phase coils).

10. SCR for temperature control.

2.3 FAN POWERED AIR TERMINAL UNITS

-------------------------------------------------------------------------------------------------------------------------------

Fan powered VAV boxes may be used for perimeter and top floor interior zone applications.

-------------------------------------------------------------------------------------------------------------------------------

A. Available Manufacturers:

1. Anemostat; a Mestek Company.

2. Carnes.

3. Environmental Technologies, Inc.; Enviro Air Div.

4. Krueger.

5. METALAIRE, Inc.; Metal Industries Inc.

6. Nailor Industries of Texas Inc.

7. Price Industries.

8. Titus.

9. Trane Co. (The); Worldwide Applied Systems Group.

10. Tuttle & Bailey.

11. <Insert manufacturer's name.>

B. Configuration:  Volume damper assembly and fan in series or in parallel arrangement inside unit casing with control components inside a protective metal shroud.

C. Casing:  0.85 mm (0.034 inch) steel, double-walled, with insulation between walls.
D. Casing Insulation:  25-mm-(1-inch-) thick, coated, fibrous-glass complying with ASTM C 1071; secured with adhesive.

E. Volume Damper:  Galvanized steel with peripheral gasket and self lubricating bearings.

-------------------------------------------------------------------------------------------------------------------------------Leakage rates vary among manufacturers and with pressure rating.  Edit subparagraph below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Maximum Damper Leakage:  ARI 880 rated, 2 percent of nominal airflow at [750 Pa (3 inch wg)] [1500 Pa (6 inch wg)] inlet static pressure.

2. Damper Position:  Normally [open] [closed].

F. Fan Section:  Galvanized steel plenum, with direct drive, forward curved fan with air filter and backdraft damper.

-------------------------------------------------------------------------------------------------------------------------------Motor characteristics, such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, retain paragraphs below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Motor:  [Multispeed] <Insert other type>.  Comply with requirements in Division 15 Section "Motors."

a. Speed Control:  Infinitely adjustable with pneumatic electric and electronic controls.  Minimum voltage stop to ensure motor cannot operate in stall mode.
b. Fan Motor Assembly Isolation:  Rubber isolators.

2. Air Filter:  [50 mm (2 inch)] [25 mm (1 inch)] thick, [fiberglass throwaway] [polyurethane] with filter rack.

-------------------------------------------------------------------------------------------------------------------------------If heating coil is required, retain one of two paragraphs below.  PBS-P100 restricts zones where hot-water coils can be used to units installed in top floors and perimeter zones.
-------------------------------------------------------------------------------------------------------------------------------

G. Hot-Water Heating Coil:  Copper tube, mechanically expanded into copper plate fins; leak tested underwater to 1380 kPa (200 psig); and factory installed.  Heating coils for units installed in top floors and perimeter zones.
-------------------------------------------------------------------------------------------------------------------------------Use of electric heating coils is restricted and must be authorized by the Office of the Chief Architect.

-------------------------------------------------------------------------------------------------------------------------------

H. Electric Heating Coil:  Slip-in type, open coil design with integral control box factory wired and installed.  Include the following features:

1. Primary and secondary overtemperature protection.

-------------------------------------------------------------------------------------------------------------------------------Retain applicable subparagraphs below.

-------------------------------------------------------------------------------------------------------------------------------

2. Nickel chrome 80/20 heating elements.

3. Fan interlock contacts.

4. Non interlocking disconnect switch.

5. Fuses (for coils more than 48 A).

6. SCR temperature control

7. Mercury contactors.

8. Pneumatic electric switches and relays.

9. Magnetic contactor for each step of control (for three phase coils).

10. SCR for temperature control.

I. Factory Mounted and Wired Controls:  Electrical components shall be mounted in control box with removable cover.  Incorporate single point electrical connection to power source.

1. Control Transformer:  Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of controls and power source.

2. Wiring Terminations:  Fan and controls to terminal strip, and terminal lugs shall match quantities, sizes, and materials of branch circuit conductors.  Enclose terminal lugs in terminal box that is sized according to NFPA 70.

3. Disconnect Switch:  Factory mounted, fused type.

J. Control Panel Enclosure:  NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

K. Electric Controls:  24-V damper actuator with wall-mounting electric thermostat and appropriate mounting hardware.

-------------------------------------------------------------------------------------------------------------------------------Retain the following only for small retrofit or renovation projects in a facility with pneumatic controls.

-------------------------------------------------------------------------------------------------------------------------------

L. Pneumatic Controls:  Damper operator, velocity controller, and thermostat shall be compatible with temperature controls specified in Division 15 Section "Building Automation System."

1. Pneumatic Damper Operator:  [55 to 90 kPa (8 to 13 psig)] [21 to 90 kPa (3 to 13 psig)] spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static pressure variations up to 1000 Pa (4 inch wg); and shall have a multipoint velocity sensor at air inlet.

M. Electronic Controls:  Bidirectional damper operator and microprocessor-based controller with integral airflow transducer and room sensor shall be compatible with temperature controls specified in Division 15 Section "Building Automation Systems" and shall have the following features:

-------------------------------------------------------------------------------------------------------------------------------Retain applicable subparagraphs below.

-------------------------------------------------------------------------------------------------------------------------------

1. Proportional, plus integral control of room temperature.

2. Time-proportional reheat-coil control.

3. Occupied and unoccupied operating mode.

4. Remote reset of airflow or temperature set points.

5. Adjusting and monitoring with portable terminal.

6. Communication with temperature-control system specified in Division 15 Section "Building Automation System."

N. Control Sequence for series boxes:

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraphs below regarding electronic controls or retain subparagraphs regarding pneumatic electric controls.

-------------------------------------------------------------------------------------------------------------------------------

1. Central system fan operating in occupied mode, provide sequence of controls as follows:

a. Fan runs continuously.

b. If central duct system pressure varies, modulate volume damper to maintain constant primary airflow.

c. On heating demand, energize heating coil.

2. Central system fan operating in unoccupied mode, provide sequence for controls as follows:

a. On heating demand, energize air terminal unit fan [and heating coil].

b. Maintain field adjustable setback temperature.

O. Control Sequence for parallel boxes:

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraphs below regarding electronic controls or retain subparagraphs regarding pneumatic electric controls.

-------------------------------------------------------------------------------------------------------------------------------

1. Central system fan operating in occupied mode, provide sequence of controls as follows:

a. During full cooling open primary air damper for full flow while fan is off.

b. As cooling load decreases, modulate primary air volume damper to reduce flow.
c. As cooling decreases further, start fan.

d. If central duct system pressure varies, modulate volume damper to maintain constant primary airflow.

e. If no cooling or heating demand, control enters field adjustable, no load band.

f. On further heating demand, energize heating coil.

2. Central system fan operating in unoccupied mode, provide sequence for controls as follows:

a. On heating demand, energize air terminal unit fan [and heating coil].

b. Maintain field adjustable setback temperature.

2.4 INDUCTION AIR TERMINAL UNITS

A.  Available Manufacturers:

1. Price Industries.

2. Tuttle & Bailey.

3. <Insert manufacturer's name.>

B. Configuration:  Volume damper assembly inside unit casing with mechanical induction damper mounted on casing and control components located inside a protective metal shroud.

C. Casing:  0.85 mm (0.034 inch) steel, double-walled, with insulation between walls.
1. Casing Insulation:  25-mm- (1-inch-) thick, coated, fibrous-glass complying with ASTM C 1071; secured with adhesive.

2. Air Inlet:  Round stub connection for duct attachment.

3. Air Outlet:  S-slip and drive connections[, size matching inlet size].

4. Access:  Removable panels for access to dampers and other parts requiring service, adjustment, or maintenance; with airtight gasket.

D. Volume Damper:  Galvanized steel with peripheral gasket and self lubricating bearings.

-------------------------------------------------------------------------------------------------------------------------------Leakage rates vary among manufacturers and with pressure rating.  Edit subparagraph below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Maximum Damper Leakage:  ARI 880 rated, 2 percent of nominal airflow at [750 Pa (3 inch wg)] [1500 Pa (6 inch wg)] inlet static pressure.

2. Damper Position:  Normally [open] [closed].

E. Induction Damper:  Galvanized steel, multi blade assembly with self lubricating bearings.

-------------------------------------------------------------------------------------------------------------------------------If heating coil is required, retain the paragraph below.  PBS-P100 restricts zones where hot-water coils can be used.
-------------------------------------------------------------------------------------------------------------------------------

F. Hot-Water Heating Coil:  Copper tube, mechanically expanded into copper plate fins; leak tested underwater to 1380 kPa (200 psig); and factory installed.

-------------------------------------------------------------------------------------------------------------------------------

Retain the following paragraph only for small retrofit or renovation projects in a facility with pneumatic controls.

-------------------------------------------------------------------------------------------------------------------------------

G. Pneumatic Controls:  Damper operator, velocity controller, induction damper operator, and thermostat shall be compatible with temperature controls specified in Division 15 Section "Temperature Controls."

1. Damper Operator:  Pneumatic, 35 to 70 kPa (5 to 10 psig) spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static pressure variations up to 1000 Pa (4 inch wg); and shall have a multipoint velocity sensor at air inlet.

3. Induction Damper Operator:  Pneumatic, spring range matching reset range of controller.

4. Thermostat:  Wall mounting pneumatic type with appropriate mounting hardware.

H. Electronic Controls:  Pneumatic damper operators, electronic controller integral airflow transducer, and electronic thermostat with the following features:

1. Damper Actuator:  Pneumatic, 5- to 10-psig (35- to 70-kPa) spring range.

2. Velocity Controller:  Factory calibrated and field adjustable at thermostat to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Induction Damper Operator:  Pneumatic, spring range matching reset range of controller.

4. Thermostat:  Wall-mounting electronic type with the following features:

-------------------------------------------------------------------------------------------------------------------------------

Retain applicable subparagraphs below.

-------------------------------------------------------------------------------------------------------------------------------

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

2.5 SHUTOFF SINGLE DUCT AIR TERMINAL UNITS

-------------------------------------------------------------------------------------------------------------------------------

Note: Full shutoff boxes are limited to perimeter zone units.    

-------------------------------------------------------------------------------------------------------------------------------

A. Available Manufacturers:

1. Anemostat; a Mestek Company.

2. Carnes.

3. Environmental Technologies, Inc.; Enviro Air Div.

4. Krueger.

5. METALAIRE, Inc.; Metal Industries Inc.

6. Nailor Industries of Texas Inc.

7. Phoenix Controls Corporation.

8. Price Industries.

9. Titus.

10. Trane Co. (The); Worldwide Applied Systems Group.

11. Trox USA, Inc.

12. Tuttle & Bailey.

13. Warren Technology.

14. <Insert manufacturer's name.>

B. Configuration:  Volume damper assembly inside unit casing with control components located inside a protective metal shroud.

C. Casing:  0.85 mm (0.034 inch) steel, double-walled, with insulation between walls.
1. Casing Insulation:  1/2-inch- (13-mm-) thick, coated, fibrous-glass complying with ASTM C 1071; secured with adhesive.

2. Air Inlet:  Round stub connection or S-slip and drive connections for duct attachment.

3. Air Outlet:  S-slip and drive connections[, size matching inlet size].

4. Access:  Removable panels for access to dampers and other parts requiring service, adjustment, or maintenance; with airtight gasket.

------------------------------------------------------------------------------------------------------------------------------- Retain first paragraph for units with mechanical volume regulators.  Retain second paragraph below for units with system-air-powered volume regulators.

-------------------------------------------------------------------------------------------------------------------------------

D. Regulator Assembly:  Extruded aluminum or galvanized steel components; key damper blades onto shaft with nylon fitted pivot points located inside unit casing.

1. Automatic Flow Control Assembly:  Combined spring rates shall be matched for each volume regulator size with machined dashpot for stable operation.

2. Factory calibrated and field adjustable assembly with shaft extension for connection to externally mounted control actuator.

E. Regulator Assembly:  System air powered bellows section incorporating polypropylene bellows for volume regulation and thermostatic control.  Bellows shall operate at temperatures from minus 18 to plus 60 deg C (0 to 140 deg F); shall be impervious to moisture and fungus; shall be suitable for 2500 Pa (10 inch wg) static pressure; and shall be factory tested for leaks.

F. Volume Damper:  Galvanized steel with peripheral gasket and self lubricating bearings.

-------------------------------------------------------------------------------------------------------------------------------Leakage rates vary among manufacturers and with pressure rating.  Edit subparagraph below to suit Project.

-------------------------------------------------------------------------------------------------------------------------------

1. Maximum Damper Leakage:  ARI 880 rated, [2] [3] percent of nominal airflow at [750 Pa (3 inch wg)] [1500 Pa (6 inch wg)] inlet static pressure.

2. Damper Position:  Normally [open] [closed].

G. Attenuator Section:  0.85 mm (0.034 inch) steel sheet metal.

1. Lining:  None

H. Multi Outlet Attenuator Section:  With [two] [three] [four] <Insert number> [150 mm (6 inch)] [200 mm (8 inch)] [250 mm (10 inch)] diameter collars; each with locking butterfly balancing damper.

I. Electric Controls:  Damper actuator.

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

-------------------------------------------------------------------------------------------------------------------------------Retain the following paragraph and subparagraphs only for small retrofit or renovation projects in a facility with pneumatic controls.

-------------------------------------------------------------------------------------------------------------------------------

J. Pneumatic Controls:  Damper operator, velocity controller, and thermostat shall be compatible with temperature controls specified in Division 15 Section "Building Automation System."

1. Pneumatic Damper Operator:  [55 to 90 kPa (8 to 13 psig)] [21 to 90 kPa (3 to 13 psig)] spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static pressure variations up to 1000 Pa (4 inch wg); and shall have a multipoint velocity sensor at air inlet.

K. Electronic Controls:  Bidirectional damper operator and microprocessor-based thermostat with integral airflow transducer and room sensor shall be compatible with temperature controls specified in other Division 15 Sections and shall have the following features:

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting electronic type with the following features:

-------------------------------------------------------------------------------------------------------------------------------Retain applicable subparagraphs below.

-------------------------------------------------------------------------------------------------------------------------------

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

L. DDC Controls:  Single-package unitary controller and actuator specified in Division 15 Section "Building Automation System."

-------------------------------------------------------------------------------------------------------------------------------Select paragraph above when control components are specified with the control system; select paragraph and subparagraphs below when control components are packaged with the equipment.

-------------------------------------------------------------------------------------------------------------------------------

M. DDC Controls:  Bidirectional damper operators and microprocessor-based controller and room sensor shall be compatible with temperature controls specified in Division 15 Section " Building Automation System." and shall have the following features:

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Terminal Unit Controller:  Pressure-independent, variable-air-volume controller with electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes, and having the following features:

-------------------------------------------------------------------------------------------------------------------------------Retain applicable subparagraphs below.

-------------------------------------------------------------------------------------------------------------------------------

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Occupied and unoccupied operating mode.

d. Remote reset of airflow or temperature set points.

e. Adjusting and monitoring with portable terminal.

3. Communication with temperature-control system specified in Division 15 Section "Building Automation System."

N. Control: Self-contained microprocessor control.

O. Control Sequence:

1. Suitable for operation with duct pressures between 60 and 750 Pa (0.25 and 3.0 inch wg) inlet static pressure.

2. Factory mounted and piped, 5 micron filter; velocity-resetting, adjustable, high limit control; and amplifying relay.

2.6 INTEGRAL DIFFUSER AIR TERMINAL UNITS

A.  Available Manufacturers:

1. Acutherm.

2. Warren Technology.

3. <Insert manufacturer's name.>

B. Configuration:  Volume damper assembly inside unit casing with [integral] [attached] [linear slot] [square ceiling] [louver face] [perforated] diffuser.

-------------------------------------------------------------------------------------------------------------------------------Retain casing paragraph below if appropriate to unit.

-------------------------------------------------------------------------------------------------------------------------------

C. Casing:  0.85 mm (0.034 inch) steel, double-walled, with insulation between walls.
1. Casing Insulation:  25-mm-(1-inch-)  thick, coated, fibrous-glass complying with ASTM C 1071; secured with adhesive.

2. Air Inlet:  Round stub connections for duct attachment.

D. Volume Damper:  Galvanized steel with peripheral gasket and self lubricating bearings.

1. Damper Position:  Normally [open] [closed].

E. Diffuser:  Galvanized steel insulated plenum with extruded aluminum or sheet steel diffuser, having fixed or variable geometry designed to operate from 100 percent to minimum airflow, manual adjustment of airflow direction, and white baked enamel finish.

-------------------------------------------------------------------------------------------------------------------------------Retain the following paragraphs only for small retrofit or renovation projects in a facility with pneumatic controls.

-------------------------------------------------------------------------------------------------------------------------------

F. Pneumatic Controls:  Damper operator[, velocity controller,] and thermostat shall be compatible with temperature controls specified in Division 15 Section "Building Automation System."

1. Pneumatic Damper Operator:  [55 to 90 kPa (8 to 13 psig)] [21 to 90 kPa (3 to 13 psig)] spring range.

G. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static pressure variations up to 1000 Pa (4 inch wg); and shall have a multipoint velocity sensor at air inlet. 
H. Electric Controls:  Damper actuator and thermostat.

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Thermostat:  Wall-mounting electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

-------------------------------------------------------------------------------------------------------------------------------Retain the following paragraphs only for small retrofit or renovation projects in a facility with pneumatic controls.

-------------------------------------------------------------------------------------------------------------------------------

I. Pneumatic Controls:  Damper operator[, velocity controller,] and thermostat shall be compatible with temperature controls specified in Division 15 Section "Building Automation System."

1. Pneumatic Damper Operator:  [55- to 90-kPa (8- to 13-psig)] [21- to 90-kPa (3- to 13-psig)] spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 1000 Pa (4-inch wg); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting pneumatic type with appropriate mounting hardware.

J. Electronic Controls:  Bidirectional damper operator and microprocessor-based thermostat with integral airflow transducer and room sensor shall be compatible with temperature controls specified in other Division 15 Sections and shall have the following features:

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 1000 Pa (4-inch wg); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting electronic type with the following features:

-------------------------------------------------------------------------------------------------------------------------------

Retain applicable subparagraphs below.
-------------------------------------------------------------------------------------------------------------------------------

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

2.7 CONTROLS

A. Factory-installed, [native BACnet, ASHRAE 135,][ or ][LonWorks compatible] self-contained microprocessor controls specified under Division 15 Sections "Building Automation System" and “Temperature Controls” to communicate with central system.
B. Each air terminal unit shall be capable of being monitored by the Building Automation System.

C. Terminal unit manufacturer to:

1. Provide control transformers [and fan relay for fan powered boxes].

2. Install and test controls supplied under Division 15 Section, "Building Automation System".

2.8 SOURCE QUALITY CONTROL

A. Identification:  Label each air terminal unit with plan number, nominal airflow, maximum and minimum factory set airflows, coil type, and ARI certification seal.

B. Verification of Performance:  Rate air terminal units according to ARI 880.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install air terminal units level and plumb.  Maintain sufficient clearance for normal service and maintenance.  Provide air transfer boot at plenum opening according to Division 15 Section "Sound Control Devices".

B. Provide access panels in adjacent walls or ceilings.

3.2 CONNECTIONS

-------------------------------------------------------------------------------------------------------------------------------Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  These requirements may be reduced or omitted.

-------------------------------------------------------------------------------------------------------------------------------

A. Install return air boots.

B. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

C. Install piping adjacent to air terminal units to allow service and maintenance.

D. Hot Water Piping:  In addition to requirements in Division 15 Section "Hydronic Piping," connect heating coils to supply with shutoff valve, strainer, control valve, and union or flange; and to return with balancing valve and union or flange.

E. Connect ducts to air terminal units according to Division 15 Section "Metal Ducts."

F. Ground units with electric heating coils according to Division 16 Section "Grounding and Bonding."

G. Connect wiring according to Division 16 Section "Conductors and Cables."

H. Tighten electrical connectors and terminals according to manufacturer's published torque tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.3 FIELD QUALITY CONTROL

-------------------------------------------------------------------------------------------------------------------------------Retain paragraph below to require a factory authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain options to suit Project; delete both if only an inspection before field testing is required.

-------------------------------------------------------------------------------------------------------------------------------

A. Manufacturer's Field Service:  Engage a factory authorized service representative, specified in Section 01700 “Execution Requirements”, to inspect[, test, and adjust] field assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. After installing air terminal units and after electrical circuitry has been energized, test for compliance with requirements.

-------------------------------------------------------------------------------------------------------------------------------Retain subparagraph below for air terminal units with hot water coils.

-------------------------------------------------------------------------------------------------------------------------------

2. Leak Test:  After installation, fill water coils and test for leaks.  Repair leaks and retest until no leaks exist.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning units and retest as specified above.

3.4 STARTUP SERVICE

-------------------------------------------------------------------------------------------------------------------------------Delete this Article if factory authorized service representative is not required.

-------------------------------------------------------------------------------------------------------------------------------

A. Engage a factory authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions and do the following:

a. Verify that inlet duct connections are as recommended by air terminal unit manufacturer to achieve proper performance.

b. Verify that controls and control enclosure are accessible.

c. Verify that control connections are complete.

d. Verify that nameplate and identification tag are visible.

e. Verify that controls respond to inputs as specified.

f. Verify that noise criteria are met.

B. Setting for units supplying ventilation air:

1. Minimum setting for each unit is the greater of the following three quanitities:

a. 30% of maximum design airflow.

b. 2.0 L/s per square meter (0.4 cfm/square foot).

c. Minimum airflow in accordance with ASHRAE 62.
3.5 DEMONSTRATION

Engage a factory authorized service representative, specified in Section 01700 “Execution Requirements”, to train Owner's maintenance personnel for [a minimum of] [1 hour] [2] [4] <Insert Number Here > hours to adjust, operate, and maintain air terminal units.  Refer to Division 1 Section, "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15840

AIR TERMINAL UNITS
15840 - 14

