Copyright 1999 AIA
GSA VERSION MASTERSPEC
6/99 (GSA 03/05)

Copyright 1999, The American Institute of Architects (AIA)

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15110 - VALVES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following general-duty valves:

Adjust list below to suit Project.

1. Bronze angle valves.

2. Cast-iron angle valves.

3. Copper-alloy ball valves.

4. Forged brass ball valves.

5. Ferrous-alloy ball valves.

6. Ferrous-alloy butterfly valves.

7. High-pressure butterfly valves.

8. Bronze check valves.

9. Gray-iron swing check valves.

10. Ferrous-alloy wafer check valves.

11. Spring-loaded, lift-disc check valves.

12. Bronze gate valves.

13. Cast-iron gate valves.

14. Bronze globe valves.

15. Cast-iron globe valves.

16. Cast-iron plug valves.

17. Stainless Steel needle valves.

18. Resilient-seated, cast-iron, eccentric plug valves.

19. Chainwheel actuators.

B. Related Sections include the following:

List below only those sections that specify products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 piping Sections for general-duty and specialty valves for site construction piping.

2. Division 13 fire-suppression piping and fire pump Sections for fire-protection valves.

3. Division 15 Section "Mechanical Identification" for valve tags and charts.

4. Division 15 Section "HVAC Instrumentation and Controls" for control valves and actuators.

5. Division 15 piping Sections for specialty valves applicable to those Sections only.

1.3 DEFINITIONS

A. The following are standard abbreviations for valves:

Retain abbreviations that remain after this Section has been edited.  Materials abbreviated below are used for butterfly valve liners or ball valve seats.  Add other material abbreviations if required.  Valve packing materials are not included in this Section but may be added for specific application.

1. CWP:  Cold working pressure.

2. EPDM:  Ethylene-propylene-diene terpolymer rubber.

3. NBR:  Acrylonitrile-butadiene rubber.

4. PTFE:  Polytetrafluoroethylene plastic.

5. SWP:  Steam working pressure.

6. TFE:  Tetrafluoroethylene plastic.

7. WOG:  Water Oil Gas.

1.4 SUBMITTALS

A. Product Data:  For each type of valve indicated.  Include body, seating, and trim materials; valve design; pressure and temperature classifications; end connections; arrangement; dimensions; and required clearances.  Include list indicating valve and its application.  Include rated capacities; shipping, installed, and operating weights; furnished specialties; and accessories.

1.5 QUALITY ASSURANCE

ASME B31.9 in paragraph below should cover piping systems in Part 3 "Valve Applications" Article up to 125 psig (860 kPa).  Higher-pressure systems are covered by ASME B31.1.  Domestic water, sanitary waste, and storm drainage piping are covered by plumbing codes, but valves in this Section are suitable for those applications.

A. ASME Compliance:  [ASME B31.1 for power piping valves and]ASME B31.9 for building services piping valves.

1. Exceptions:  Domestic hot- and cold-water[, sanitary waste, and storm drainage] piping valves unless referenced.

B. ASME Compliance for Ferrous Valves:  ASME B16.10 and ASME B16.34 for dimension and design criteria.

C. NSF Compliance:  NSF 61 for valve materials for potable-water service.

1.6 DELIVERY, STORAGE, AND HANDLING

Information below is paraphrased from MSS.

A. Prepare valves for shipping as follows:

1. Protect internal parts against rust and corrosion.

2. Protect threads, flange faces, grooves, and weld ends.

3. Set angle, gate, and globe valves closed to prevent rattling.

4. Set ball and plug valves open to minimize exposure of functional surfaces.

5. Set butterfly valves closed or slightly open.

6. Block check valves in either closed or open position.

B. Use the following precautions during storage:

1. Maintain valve end protection.

2. Store valves indoors and maintain at higher than ambient dew-point temperature.  If outdoor storage is necessary, store valves off the ground in watertight enclosures.

C. Use sling to handle large valves; rig sling to avoid damage to exposed parts.  Do not use handwheels or stems as lifting or rigging points.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where subparagraph titles below introduce lists, the following requirements apply for product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.  
Caution:  Valve categories and types and manufacturer lists in the following articles were obtained from valve manufacturers' catalogs available when this Section was updated.  Other valve categories, types, materials, and features not listed in these articles are available and may be added if required.
The purpose of listing manufacturers is to inform contractors of manufacturers with the capacity to provide the product(s) specified.  Long lists should be edited to a modest length representing general geographical availability.
2.2 VALVES, GENERAL

A. Refer to Part 3 "Valve Applications" Article for applications of valves.

B. Bronze Valves:  DN 50 (NPS 2) and smaller with threaded ends, unless otherwise indicated.

C. Ferrous Valves:  DN 65 (NPS 2-1/2) and larger with flanged ends, unless otherwise indicated.

Caution:  Edit pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required.

D. Valve Pressure and Temperature Ratings:  Not less than indicated and as required for system pressures and temperatures.

E. Valve Sizes:  Same as upstream pipe, unless otherwise indicated.

F. Valve Actuators:

1. Chainwheel:  For attachment to valves, of size and mounting height, as indicated in the "Valve Installation" Article in Part 3.

2. Gear Drive:  For quarter-turn valves DN 200 (NPS 8) and larger.

3. Handwheel:  For valves other than quarter-turn types.

4. Lever Handle:  For quarter-turn valves DN 150 (NPS 6) and smaller, except plug valves.

5. Wrench:  For plug valves with square heads.  Furnish Owner with 1 wrench for every 10 plug valves, or fraction thereof, for each size square plug head.

G. Extended Valve Stems:  On insulated valves.

H. Valve Flanges:  ASME B16.1 for cast-iron valves, ASME B16.5 for steel valves, and ASME B16.24 for bronze valves.

I. Valve Grooved Ends:  AWWA C606.

Although soldered connections are common in smaller sizes of plumbing piping, they are not recommended for valves in HVAC service.  Soldering and brazing methods used to achieve required pressure-temperature ratings may damage internal valve parts.  Special installation requirements for soldered valves may make threaded valves more cost-effective.

1. Solder Joint:  With sockets according to ASME B16.18.

a. Caution:  Use solder with melting point below 454 deg C (840 deg F) for angle, check, gate, and globe valves; below 216 deg C (421 deg F) for ball valves.

2. Threaded:  With threads according to ASME B1.20.1.

J. Valve Bypass and Drain Connections:  MSS SP-45.

2.3 BRONZE ANGLE VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type 1, Bronze Angle Valves with Metal Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Stockham Div.

c. Hammond Valve.

d. Milwaukee Valve Company.

e. NIBCO INC.

f. Red-White Valve Corp.

2. Type 2, Bronze Angle Valves with Nonmetallic Disc:

a. American Valve, Inc.

b. Cincinnati Valve Co.

c. Crane Co.; Crane Valve Group; Crane Valves.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Div.

f. Grinnell Corporation.

g. Hammond Valve.

h. NIBCO INC.

i. Powell, Wm. Co.

3. Type 3, Bronze Angle Valves with Metal Disc and Renewable Seat:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Milwaukee Valve Company.

g. NIBCO INC.

B. Bronze Angle Valves, General:  MSS SP-80, with ferrous-alloy handwheel.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Type 1, Class 125, Bronze Angle Valves:  Bronze body with bronze disc [and union-ring bonnet].

No manufacturers for valves in first paragraph below were located.  Verify availability if required.

D. Type 1, Class 150, Bronze Angle Valves:  Bronze body with bronze disc [and union-ring bonnet].

E. Type 1, Class 200, Bronze Angle Valves:  Bronze body with bronze disc [and union-ring bonnet].

F. Type 2, Class 125, Bronze Angle Valves:  Bronze body with [nonmetallic] [PTFE or TFE] <Insert other> disc [and union-ring bonnet].

G. Type 2, Class 150, Bronze Angle Valves:  Bronze body with [nonmetallic] [PTFE or TFE] <Insert other> disc [and union-ring bonnet].

H. Type 2, Class 200, Bronze Angle Valves:  Bronze body with [nonmetallic] [PTFE or TFE] <Insert other> disc [and union-ring bonnet].

No manufacturers for valves in first paragraph below were located.  Verify availability if required.

I. Type 3, Class 125, Bronze Angle Valves:  Bronze body with bronze disc and renewable seat.[ Include union-ring bonnet.]

J. Type 3, Class 150, Bronze Angle Valves:  Bronze body with bronze disc and renewable seat.[ Include union-ring bonnet.]

K. Type 3, Class 200, Bronze Angle Valves:  Bronze body with bronze disc and renewable seat.[ Include union-ring bonnet.]

2.4 CAST-IRON ANGLE VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type II, Cast-Iron Angle Valves with Metal Seats:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Div.

d. NIBCO INC.

B. Cast-Iron Angle Valves, General:  MSS SP-85, Type II.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Class 125, Cast-Iron Angle Valves:  Bronze mounted with gray-iron body and bronze seats.

D. Class 250, Cast-Iron Angle Valves:  Bronze mounted with gray-iron body and bronze seats.

2.5 COPPER-ALLOY BALL VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. One-Piece, Copper-Alloy Ball Valves:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Div.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. DynaQuip Controls.

f. Grinnell Corporation.

g. Jamesbury, Inc.

h. Kitz Corporation of America.

i. Legend Valve & Fitting, Inc.

j. NIBCO INC.

k. Watts Industries, Inc.; Water Products Div.

2. Two-Piece, Copper-Alloy Ball Valves:

a. Conbraco Industries, Inc.; Apollo Div.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. DynaQuip Controls.

f. Flow-Tek, Inc.

g. Grinnell Corporation.

h. Hammond Valve.

i. Honeywell Braukmann.

j. Jamesbury, Inc.

k. Jomar International, LTD.

l. Kitz Corporation of America.

m. Legend Valve & Fitting, Inc.

n. Milwaukee Valve Company.

o. Nexus Valve Specialties.

p. NIBCO INC.

q. R & M Energy Systems (Borger, TX).

r. Red-White Valve Corp.

s. Richards Industries; Marwin Ball Valves.

t. Watts Industries, Inc.; Water Products Div.

3. Three-Piece, Copper-Alloy Ball Valves:

a. Conbraco Industries, Inc.; Apollo Div.

b. DynaQuip Controls.

c. Grinnell Corporation.

d. Hammond Valve.

e. Jamesbury, Inc.

f. Kitz Corporation of America.

g. NIBCO INC.

h. PBM, Inc.

i. Red-White Valve Corp.

j. Worcester Controls.

4. Safety-Exhaust, Copper-Alloy Ball Valves:

a. Conbraco Industries, Inc.; Apollo Div.

b. DynaQuip Controls.

c. Grinnell Corporation.

d. Hammond Valve.

e. Jamesbury, Inc.

f. Milwaukee Valve Company.

g. NIBCO INC.

B. Copper-Alloy Ball Valves, General:  MSS SP-110.

Caution:  Two-piece ball valves with a full or regular port are recommended for most services.  One-piece ball valves are suitable if economy is main consideration.  Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. One-Piece, Copper-Alloy Ball Valves:  Brass or bronze body with chrome-plated bronze ball, PTFE or TFE seats, and [2760-kPa (400-psig) minimum] [4140-kPa (600-psig)] CWP rating.

D. Two-Piece, Copper-Alloy Ball Valves:  [Brass or bronze] [Forged-brass] [Bronze] body with [full] [regular]-port, chrome-plated bronze ball; [PTFE or TFE] <Insert other> seats; and [4140-kPa (600-psig)] <Insert other> minimum CWP rating and blowout-proof stem.

E. Three-Piece, Copper-Alloy Ball Valves:  [Brass or bronze] [Forged-brass] [Bronze] body with [full] [regular]-port, chrome-plated bronze ball; [PTFE or TFE] <Insert other> seats; and [4140-kPa (600-psig)] <Insert other> minimum CWP rating and blowout-proof stem.

F. Safety-Exhaust, Copper-Alloy Ball Valves:  Two-piece bronze body with exhaust vent opening, chrome-plated ball with vent, blowout-proof stem, locking handle, and working pressure rating [for compressed air of at least 860 kPa (125 psig)] [of 2760-kPa (400-psig) CWP] [of 4140-kPa (600-psig) CWP].

2.6 FORGED BRASS BALL VALVES

A. Available Manufactures:

1. One-Piece, Forged Brass Ball Valves:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Div.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. DynaQuip Controls.

f. Grinnell Corporation.

g. Jamesbury, Inc.

h. Kitz Corporation of America.

i. Legend Valve & Fitting, Inc.

j. NIBCO INC.

k. Watts Industries, Inc.; Water Products Div.

2. Two-Piece, Forged Brass Ball Valves:

a. Conbraco Industries, Inc.; Ball Valves:

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. DynaQuip Controls.
f. Flow-Tek, Inc.

g. Grinnell Corporation.

h. Hammond Valve.

i. Honeywell Braukmann.

j. Jamesbury, Inc.

k. Jomar International, LTD.

l. Kitz Corporation of America.

m. Legend Valve & Fitting, Inc.

n. Milwaukee Valve Company.

o. Nexus Valve Specialties.

p. NIBCO INC.

q. R & M Energy Systems (Borger, TX).

r. Red-White Valve Corp.

s. Richards Industries; Marwin Ball Valves.

t. Watts Industries, Inc.; Water Products Div.

3. Three-Piece, Forged Brass Ball Valves:

a. Conbraco Industries, Inc.; Apollo Div.
b. DynaQuip Controls.

c. Grinnell Corporation.

d. Hammond Valve.

e. Jamesbury, Inc.

f. Kitz Corporation of America.

g. NIBCO INC.

h. PBM, Inc.

i. Red-White Valve Corp.

j. Worcester Controls.

4. Safety-Exhaust, Forged Brass Ball Valves:

a. Conbraco Industries, Inc.; Apollo Div.

b. DynaQuip Controls.

c. Grinnell Corporation.

d. Hammond Valve.

e. Jamesbury, Inc.

f. Milwaukee Valve Company.

g. NIBCO INC.

B. Forges Brass Ball Valves, General:  MSS SP-110.

Caution:  Two-piece ball valves with a full or regular port are recommended for most services.  One-piece ball valves are suitable if economy is main consideration.  Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. One-Piece Forged Brass Ball Valves:  Forged brass body with chrome-plated bronze ball, PTFE or GIF seats, blowout proof stem and [2760-kPa (400-psig) minimum] [4140-kPa (600-psig)] non-shock WOG rating.

D. Two-Piece, Forged Brass Ball Valves:  Forged brass body with [full] [regular]-port, chrome-plated bronze ball; [PTFE] <Insert other> seats; and [4140-kPa (600-psig)] <Insert other> minimum non shock WOG rating and blowout-proof stem.
E. Three-Piece, Forged Brass Ball Valves:  Forged brass body with [full] [regular]-port, chrome-plated bronze ball; [PTFE] <Insert other> seats; and [4140-kPa (600-psig)] <Insert other> minimum non shock WOG rating and blowout-proof stem.

F. Safety-Exhaust, Forged Brass Ball Valves:  Two-piece bronze body with exhaust vent opening, chrome-plated ball with vent, blowout-proof stem, locking handle, and working pressure rating [for compressed air of at least 860 kPa (125 psig)] [of 2760-kPa (400-psig) CWP] [of 4140-kPa(600-psig) CWP], with locking handle.

2.7 FERROUS-ALLOY BALL VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. American Valve, Inc.

2. Conbraco Industries, Inc.; Apollo Div.

3. Cooper Cameron Corp.; Cooper Cameron Valves Div.

4. Crane Co.; Crane Valve Group; Stockham Div.

5. Flow-Tek, Inc.

6. Foster Valve Co.

7. Hammond Valve.

8. Jamesbury, Inc.

9. Jomar International, LTD.

10. Kitz Corporation of America.

11. KTM Products, Inc.

12. McCANNA, Incorporated.

13. Milwaukee Valve Company.

14. NIBCO INC.

15. PBM, Inc.

16. Richards Industries; Marwin Ball Valves.

17. Worcester Controls.

B. Ferrous-Alloy Ball Valves, General:  MSS SP-72, with flanged ends.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Ferrous-Alloy Ball Valves:  Class 150, full [or regular] port.

D. Ferrous-Alloy Ball Valves:  Class 300, full [or regular] port.

2.8 FERROUS-ALLOY BUTTERFLY VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Flangeless, Ferrous-Alloy Butterfly Valves:

a. American Valve, Inc.

b. Bray International, Inc.

c. Cooper Cameron Corp.; Cooper Cameron Valves Div.

d. Crane Co.; Crane Valve Group; Center Line.

e. Crane Co.; Crane Valve Group; Stockham Div.

f. Dover Corp.; Dover Resources Company; Norriseal Div.

g. General Signal; DeZurik Unit.

h. Grinnell Corporation.

i. Hammond Valve.

j. Kitz Corporation of America.

k. Legend Valve & Fitting, Inc.

l. Metraflex Co.

m. Milwaukee Valve Company.

n. Mueller Steam Specialty.

o. NIBCO INC.

p. Process Development & Control.

q. Red-White Valve Corp.

r. Techno Corp.

s. Tyco International, Ltd.; Tyco Valves & Controls.

t. Watts Industries, Inc.; Water Products Div.

2. Single-Flange, Ferrous-Alloy Butterfly Valves:

a. American Valve, Inc.

b. Bray International, Inc.

c. Cooper Cameron Corp.; Cooper Cameron Valves Div.

d. Crane Co.; Crane Valve Group; Center Line.

e. Crane Co.; Crane Valve Group; Jenkins Valves.

f. Crane Co.; Crane Valve Group; Stockham Div.

g. Dover Corp.; Dover Resources Company; Norriseal Div.

h. General Signal; DeZurik Unit.

i. Grinnell Corporation.

j. Hammond Valve.

k. Kitz Corporation of America.

l. Legend Valve & Fitting, Inc.

m. Metraflex Co.

n. Milwaukee Valve Company.

o. Mueller Steam Specialty.

p. NIBCO INC.

q. Process Development & Control.

r. Red-White Valve Corp.

s. Techno Corp.

t. Tyco International, Ltd.; Tyco Valves & Controls.

u. Watts Industries, Inc.; Water Products Div.

3. Flanged, Ferrous-Alloy Butterfly Valves:

a. Bray International, Inc.

b. Cooper Cameron Corp.; Cooper Cameron Valves Div.

c. Grinnell Corporation.

d. Mueller Steam Specialty.

e. Tyco International, Ltd.; Tyco Valves & Controls.

4. Grooved-End, Ductile-Iron Butterfly Valves:

a. Central Sprinkler Co.; Central Grooved Piping Products.

b. Grinnell Corporation.

c. Hammond Valve.

d. McWane, Inc.; Kennedy Valve Div.

e. Milwaukee Valve Company.

f. Mueller Steam Specialty.

g. NIBCO INC.

h. Victaulic Co. of America.

B. Ferrous-Alloy Butterfly Valves, General:  MSS SP-67, Type I, for tight shutoff, with disc and lining suitable for potable water, unless otherwise indicated.

Add specific materials, attributes, and features to paragraphs below to suit Project.  For absolute bubble tight end of line shut off, specify falling pattern with seat molded into the body.
C. Flangeless, 1035-kPa (150-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer type with [one] [one- or two] [two]-piece stem.

D. Flangeless, 1207-kPa (175-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer type with [one] [one- or two] [two]-piece stem.

E. Flangeless, 1380-kPa (200-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer type with [one] [one- or two] [two]-piece stem.

F. Flangeless, 1725-kPa (250-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer type with [one] [one- or two] [two]-piece stem.

G. Flangeless, 2070-kPa (300-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer type with [one] [one- or two] [two]-piece stem.

H. Single-Flange, 1035-kPa (150-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer-lug type with [one] [one- or two] [two]-piece stem.

I. Single-Flange, 1207-kPa (175-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer-lug type with [one] [one- or two] [two]-piece stem.

J. Single-Flange, 1380-kPa (200-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer-lug type with [one] [one- or two] [two]-piece stem.

K. Single-Flange, 1725-kPa (250-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer-lug type with [one] [one- or two] [two]-piece stem.

L. Single-Flange, 2070-kPa (300-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Wafer-lug type with [one] [one- or two] [two]-piece stem.

M. Flanged, 1035-kPa (150-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Flanged-end type with [one] [one- or two] [two]-piece stem.

N. Flanged, 1207-kPa (175-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Flanged-end type with [one] [one- or two] [two]-piece stem.

O. Flanged, 1380-kPa (200-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Flanged-end type with [one] [one- or two] [two]-piece stem.

P. Flanged, 1725-kPa (250-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Flanged-end type with [one] [one- or two] [two]-piece stem.

Q. Flanged, 2070-kPa (300-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Flanged-end type with [one] [one- or two] [two]-piece stem.

R. Grooved-End, 1207-kPa (175-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Ductile-iron or steel body with grooved or shouldered ends.

S. Grooved-End, 2070-kPa (300-psig) CWP Rating, Ferrous-Alloy Butterfly Valves:  Ductile-iron or steel body with grooved or shouldered ends.

2.9 HIGH-PRESSURE BUTTERFLY VALVES

The title of this valve category is misleading.  MSS SP-68 calls these valves "high-pressure butterfly valves," but they are not necessarily rated for high pressures.  Most manufacturers call these valves "high-performance butterfly valves."

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Bray International, Inc.

2. Cooper Cameron Corp.; Cooper Cameron Valves Div.

3. Crane Co.; Crane Valve Group; Flowseal.

4. General Signal; DeZurik Unit.

5. Grinnell Corporation.

6. Jamesbury, Inc.

7. Pratt, Henry Company.

8. Process Development & Control.

9. Tyco International, Ltd.; Tyco Valves & Controls.

10. Xomox Corporation.

B. High-Pressure Butterfly Valves, General:  MSS SP-68.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Flangeless, Class 150, High-Pressure Butterfly Valves:  Wafer type.

D. Single-Flange, Class 150, High-Pressure Butterfly Valves:  Wafer type.

E. Flangeless, Class 300, High-Pressure Butterfly Valves:  Wafer-lug type.

F. Single-Flange, Class 300, High-Pressure Butterfly Valves:  Wafer-lug type.

2.10 BRONZE CHECK VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type 1, Bronze, Horizontal Lift Check Valves with Metal Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Stockham Div.

d. Red-White Valve Corp.

e. Walworth Co.

2. Type 2, Bronze, Horizontal Lift Check Valves with Nonmetallic Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Walworth Co.

3. Type 1, Bronze, Vertical Lift Check Valves with Metal Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Red-White Valve Corp.

4. Type 2, Bronze, Vertical Lift Check Valves with Nonmetallic Disc:

a. Grinnell Corporation.

b. Kitz Corporation of America.

c. Milwaukee Valve Company.

5. Type 3, Bronze, Swing Check Valves with Metal Disc:

a. American Valve, Inc.

b. Cincinnati Valve Co.

c. Crane Co.; Crane Valve Group; Crane Valves.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Div.

f. Grinnell Corporation.

g. Hammond Valve.

h. Kitz Corporation of America.

i. Legend Valve & Fitting, Inc.

j. Milwaukee Valve Company.

k. NIBCO INC.

l. Powell, Wm. Co.

m. Red-White Valve Corp.

n. Walworth Co.

o. Watts Industries, Inc.; Water Products Div.

6. Type 4, Bronze, Swing Check Valves with Nonmetallic Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Hammond Valve.

g. McWane, Inc.; Kennedy Valve Div.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. Red-White Valve Corp.

k. Walworth Co.

l. Watts Industries, Inc.; Water Products Div.

B. Bronze Check Valves, General:  MSS SP-80.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Type 1, Class 125, Bronze, Horizontal Lift Check Valves:  Bronze body with bronze disc and seat.

D. Type 1, Class 125, Bronze, Vertical Lift Check Valves:  Bronze body with bronze disc and seat.

E. Type 1, Class 150, Bronze, Horizontal Lift Check Valves:  Bronze body with bronze disc and seat.

F. Type 1, Class 150, Bronze, Vertical Lift Check Valves:  Bronze body with bronze disc and seat.

G. Type 1, Class 200, Bronze, Horizontal Lift Check Valves:  Bronze body with bronze disc and seat.

H. Type 1, Class 200, Bronze, Vertical Lift Check Valves:  Bronze body with bronze disc and seat.

I. Type 2, Class 125, Bronze, Horizontal Lift Check Valves:  Bronze body with nonmetallic disc and bronze seat.

J. Type 2, Class 125, Bronze, Vertical Lift Check Valves:  Bronze body with nonmetallic disc and bronze seat.

K. Type 2, Class 150, Bronze, Horizontal Lift Check Valves:  Bronze body with nonmetallic disc and bronze seat.

No manufacturers for valves in first three paragraphs below were located.  Verify availability if required.

L. Type 2, Class 150, Bronze, Vertical Lift Check Valves:  Bronze body with nonmetallic disc and bronze seat.

M. Type 2, Class 200, Bronze, Horizontal Lift Check Valves:  Bronze body with nonmetallic disc and bronze seat.

N. Type 2, Class 200, Bronze, Vertical Lift Check Valves:  Bronze body with nonmetallic disc and bronze seat.

O. Type 3, Class 125, Bronze, Swing Check Valves:  Bronze body with bronze disc and seat.

P. Type 3, Class 150, Bronze, Swing Check Valves:  Bronze body with bronze disc and seat.

Q. Type 3, Class 200, Bronze, Swing Check Valves:  Bronze body with bronze disc and seat.

R. Type 4, Class 125, Bronze, Swing Check Valves:  Bronze body with nonmetallic disc and bronze seat.

S. Type 4, Class 150, Bronze, Swing Check Valves:  Bronze body with nonmetallic disc and bronze seat.

T. Type 4, Class 200, Bronze, Swing Check Valves:  Bronze body with nonmetallic disc and bronze seat.

2.11 GRAY-IRON SWING CHECK VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type I, Gray-Iron Swing Check Valves with Metal Seats:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Flomatic Valves.

f. Grinnell Corporation.

g. Hammond Valve.

h. Kitz Corporation of America.

i. Legend Valve & Fitting, Inc.

j. Milwaukee Valve Company.

k. Mueller Co.

l. NIBCO INC.

m. Powell, Wm. Co.

n. Red-White Valve Corp.

o. Walworth Co.

p. Watts Industries, Inc.; Water Products Div.

2. Type II, Gray-Iron Swing Check Valves with Composition to Metal Seats:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Div.

c. Mueller Co.

d. Watts Industries, Inc.; Water Products Div.

3. Grooved-End, Ductile-Iron Swing Check Valves:

a. Grinnell Corporation.

b. Mueller Co.

c. Victaulic Co. of America.

B. Gray-Iron Swing Check Valves, General:  MSS SP-71.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Type I, Class 125, gray-iron, swing check valves with metal seats.

D. Type I, Class 250, gray-iron, swing check valves with metal seats.

E. Type II, Class 125, gray-iron, swing check valves with composition to metal seats.

No manufacturers for valves in first paragraph below were located.  Verify availability if required.

F. Type II, Class 250, gray-iron, swing check valves with composition to metal seats.

G. 1207-kPa (175-psig) CWP Rating, Grooved-End, Swing Check Valves:  Ductile-iron body with grooved or shouldered ends.

H. 2070-kPa (300-psig) CWP Rating, Grooved-End, Swing Check Valves:  Ductile-iron body with grooved or shouldered ends.

2.12 FERROUS-ALLOY WAFER CHECK VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Single-Plate, Ferrous-Alloy, Wafer Check Valves:

a. Gestra, Inc.

b. McWane, Inc.; Kennedy Valve Div.

c. Mueller Co.

d. Techno Corp.

e. Tyco International, Ltd.; Tyco Valves & Controls.

f. Wheatley Gaso, Inc.

2. Dual-Plate, Ferrous-Alloy, Wafer Check Valves:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Div.

c. Flomatic Valves.

d. Gestra, Inc.

e. Grinnell Corporation.

f. Gulf Valve Co.

g. Metraflex Co.

h. Mueller Steam Specialty.

i. NIBCO INC.

j. Red-White Valve Corp.

k. SSI Equipment, Inc.

l. Techno Corp.

m. Val-Matic Valve & Mfg. Corp.

n. Valve and Primer Corp.

o. Watts Industries, Inc.; Water Products Div.

3. Dual-Plate, Ferrous-Alloy, Wafer-Lug Check Valves:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Gulf Valve Co.

c. Valve and Primer Corp.

4. Dual-Plate, Ferrous-Alloy, Double-Flanged-Type Check Valves:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Gulf Valve Co.

c. Techno Corp.

B. Ferrous-Alloy Wafer Check Valves, General:  API 594, spring loaded.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Single-Plate, Class 125 or 150, Ferrous-Alloy, Wafer Check Valves:  Flangeless body.

D. Single-Plate, Class 250 or 300, Ferrous-Alloy, Wafer Check Valves:  Flangeless body.

E. Single-Plate, Class 125 or 150, Ferrous-Alloy, Wafer-Lug Check Valves:  Single-flange body.

F. Single-Plate, Class 250 or 300, Ferrous-Alloy, Wafer-Lug Check Valves:  Single-flange body.

G. Single-Plate, Class 125 or 150, Ferrous-Alloy, Double-Flanged Check Valves:  Flanged-end body.

H. Single-Plate, Class 250 or 300, Ferrous-Alloy, Double-Flanged Check Valves:  Flanged-end body.

I. Dual-Plate, Class 125 or 150, Ferrous-Alloy, Wafer Check Valves:  Flangeless body.

J. Dual-Plate, Class 250 or 300, Ferrous-Alloy, Wafer Check Valves:  Flangeless body.

K. Dual-Plate, Class 125 or 150, Ferrous-Alloy, Wafer-Lug Check Valves:  Single-flange body.

L. Dual-Plate, Class 250 or 300, Ferrous-Alloy, Wafer-Lug Check Valves:  Single-flange body.

M. Dual-Plate, Class 125 or 150, Ferrous-Alloy, Double-Flanged Check Valves:  Flanged-end body.

N. Dual-Plate, Class 250 or 300, Ferrous-Alloy, Double-Flanged Check Valves:  Flanged-end body.

2.13 SPRING-LOADED, LIFT-DISC CHECK VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Caution:  Some valve manufacturers recommend that their lift-disc check valves not be used for compressed-air or steam services.

1. Type I, Wafer Lift-Disc Check Valves:

a. Mueller Steam Specialty.

2. Type II, Compact-Wafer, Lift-Disc Check Valves:

a. Durabla Fluid Technology, Inc.

b. Flomatic Valves.

c. GA Industries, Inc.

d. Grinnell Corporation.

e. Hammond Valve.

f. Metraflex Co.

g. Milwaukee Valve Company.

h. Mueller Steam Specialty.

i. Multiplex Manufacturing Co.

j. NIBCO INC.

k. SSI Equipment, Inc.

l. Val-Matic Valve & Mfg. Corp.

m. Valve and Primer Corp.

3. Type III, Globe Lift-Disc Check Valves:

a. Durabla Fluid Technology, Inc.

b. Flomatic Valves.

c. GA Industries, Inc.

d. Grinnell Corporation.

e. Hammond Valve.

f. Metraflex Co.

g. Milwaukee Valve Company.

h. Multiplex Manufacturing Co.

i. NIBCO INC.

j. SSI Equipment, Inc.

k. Val-Matic Valve & Mfg. Corp.

l. Valve and Primer Corp.

4. Type IV, Threaded Lift-Disc Check Valves:

a. Check-All Valve Mfg. Co.

b. Durabla Fluid Technology, Inc.

c. Grinnell Corporation.

d. Legend Valve & Fitting, Inc.

e. Metraflex Co.

f. Milwaukee Valve Company.

g. Mueller Steam Specialty.

h. NIBCO INC.

i. Watts Industries, Inc.; Water Products Div.

B. Lift-Disc Check Valves, General:  FCI 74-1, with spring-loaded bronze or alloy disc and bronze or alloy seat.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Type I, Class 125, Wafer Lift-Disc Check Valves:  Wafer style with cast-iron shell with diameter matching companion flanges.

D. Type I, Class 250, Wafer Lift-Disc Check Valves:  Wafer style with cast-iron shell with diameter matching companion flanges.

E. Type II, Class 125, Compact-Wafer, Lift-Disc Check Valves:  Compact-wafer style with cast-iron shell with diameter made to fit within bolt circle.

F. Type II, Class 250, Compact-Wafer, Lift-Disc Check Valves:  Compact-wafer style with cast-iron shell with diameter made to fit within bolt circle.

G. Type III, Class 125, Globe Lift-Disc Check Valves:  Globe style with cast-iron shell and flanged ends.

H. Type III, Class 250, Globe Lift-Disc Check Valves:  Globe style with cast-iron shell and flanged ends.

I. Type IV, Class 125, Threaded Lift-Disc Check Valves:  Threaded style with bronze shell and threaded ends.

J. Type IV, Class 150, Threaded Lift-Disc Check Valves:  Threaded style with bronze shell and threaded ends.

2.14 BRONZE GATE VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type 1, Bronze, Nonrising-Stem Gate Valves:

a. American Valve, Inc.

b. Cincinnati Valve Co.

c. Crane Co.; Crane Valve Group; Crane Valves.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Div.

f. Grinnell Corporation.

g. Hammond Valve.

h. Kitz Corporation of America.

i. Legend Valve & Fitting, Inc.

j. Milwaukee Valve Company.

k. NIBCO INC.

l. Powell, Wm. Co.

m. Red-White Valve Corp.

n. Walworth Co.

o. Watts Industries, Inc.; Water Products Div.

2. Type 2, Bronze, Rising-Stem, Solid-Wedge Gate Valves:

a. American Valve, Inc.

b. Cincinnati Valve Co.

c. Crane Co.; Crane Valve Group; Crane Valves.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Div.

f. Grinnell Corporation.

g. Hammond Valve.

h. Kitz Corporation of America.

i. Milwaukee Valve Company.

j. NIBCO INC.

k. Powell, Wm. Co.

l. Red-White Valve Corp.

m. Walworth Co.

3. Type 3, Bronze, Rising-Stem, Split-Wedge Gate Valves:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Grinnell Corporation.

d. NIBCO INC.

B. Bronze Gate Valves, General:  MSS SP-80, with ferrous-alloy handwheel.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Type 1, Class 125, Bronze Gate Valves:  Bronze body with nonrising stem and bronze solid wedge [and union-ring bonnet].

D. Type 1, Class 150, Bronze Gate Valves:  Bronze body with nonrising stem and bronze solid wedge [and union-ring bonnet].

E. Type 1, Class 200, Bronze Gate Valves:  Bronze body with nonrising stem and bronze solid wedge [and union-ring bonnet].

F. Type 2, Class 125, Bronze Gate Valves:  Bronze body with rising stem and bronze solid wedge [and union-ring bonnet].

G. Type 2, Class 150, Bronze Gate Valves:  Bronze body with rising stem and bronze solid wedge [and union-ring bonnet].

H. Type 2, Class 200, Bronze Gate Valves:  Bronze body with rising stem and bronze solid wedge [and union-ring bonnet].

I. Type 3, Class 125, Bronze Gate Valves:  Bronze body with rising stem and bronze split wedge [and union-ring bonnet].

J. Type 3, Class 150, Bronze Gate Valves:  Bronze body with rising stem and bronze split wedge [and union-ring bonnet].

K. Type 3, Class 200, Bronze Gate Valves:  Bronze body with rising stem and bronze split wedge [and union-ring bonnet].

2.15 CAST-IRON GATE VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type I, Cast-Iron, Nonrising-Stem Gate Valves:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Hammond Valve.

g. Kitz Corporation of America.

h. Legend Valve & Fitting, Inc.

i. Milwaukee Valve Company.

j. NIBCO INC.

k. Powell, Wm. Co.

l. Red-White Valve Corp.

m. Walworth Co.

n. Watts Industries, Inc.; Water Products Div.

2. Type I, Cast-Iron, Rising-Stem Gate Valves:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Hammond Valve.

g. Kitz Corporation of America.

h. Legend Valve & Fitting, Inc.

i. Milwaukee Valve Company.

j. NIBCO INC.

k. Powell, Wm. Co.

l. Red-White Valve Corp.

m. Walworth Co.

n. Watts Industries, Inc.; Water Products Div.

B. Cast-Iron Gate Valves, General:  MSS SP-70, Type I.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Class 125, NRS, Bronze-Mounted, Cast-Iron Gate Valves:  Cast-iron body with bronze trim, nonrising stem, and solid-wedge disc.

D. Class 125, OS&Y, Bronze-Mounted, Cast-Iron Gate Valves:  Cast-iron body with bronze trim, rising stem, and solid-wedge disc.

E. Class 125, NRS, All-Iron, Cast-Iron Gate Valves:  Cast-iron body with cast-iron trim, nonrising stem, and solid-wedge disc.

F. Class 125, OS&Y, All-Iron, Cast-Iron Gate Valves:  Cast-iron body with cast-iron trim, rising stem, and solid-wedge disc.

G. Class 250, NRS, Bronze-Mounted, Cast-Iron Gate Valves:  Cast-iron body with bronze trim, nonrising stem, and solid-wedge disc.

H. Class 250, OS&Y, Bronze-Mounted, Cast-Iron Gate Valves:  Cast-iron body with bronze trim, rising stem, and solid-wedge disc.

I. Class 250, NRS, All-Iron, Cast-Iron Gate Valves:  Cast-iron body with cast-iron trim, nonrising stem, and solid-wedge disc.

J. Class 250, OS&Y, All-Iron, Cast-Iron Gate Valves:  Cast-iron body with cast-iron trim, rising stem, and solid-wedge disc.

2.16 BRONZE GLOBE VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type 1, Bronze Globe Valves with Metal Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Hammond Valve.

g. Kitz Corporation of America.

h. Legend Valve & Fitting, Inc.

i. Milwaukee Valve Company.

j. NIBCO INC.

k. Powell, Wm. Co.

l. Red-White Valve Corp.

m. Walworth Co.

2. Type 2, Bronze Globe Valves with Nonmetallic Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Hammond Valve.

g. Kitz Corporation of America.

h. McWane, Inc.; Kennedy Valve Div.

i. Milwaukee Valve Company.

j. NIBCO INC.

k. Powell, Wm. Co.

l. Red-White Valve Corp.

m. Walworth Co.

3. Type 3, Bronze Globe Valves with Renewable Seat and Metal Disc:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Hammond Valve.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Walworth Co.

B. Bronze Globe Valves, General:  MSS SP-80, with ferrous-alloy handwheel.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Type 1, Class 125, Bronze Globe Valves:  Bronze body with bronze disc [and union-ring bonnet].

D. Type 1, Class 150, Bronze Globe Valves:  Bronze body with bronze disc [and union-ring bonnet].

E. Type 1, Class 200, Bronze Globe Valves:  Bronze body with bronze disc [and union-ring bonnet].

F. Type 2, Class 125, Bronze Globe Valves:  Bronze body with [nonmetallic] [PTFE or TFE] <Insert other> disc [and union-ring bonnet].

G. Type 2, Class 150, Bronze Globe Valves:  Bronze body with [nonmetallic] [PTFE or TFE] <Insert other> disc [and union-ring bonnet].

H. Type 2, Class 200, Bronze Globe Valves:  Bronze body with [nonmetallic] [PTFE or TFE] <Insert other> disc [and union-ring bonnet].

I. Type 3, Class 125, Bronze Globe Valves:  Bronze body with bronze disc and renewable seat.[ Include union-ring bonnet.]

J. Type 3, Class 150, Bronze Globe Valves:  Bronze body with bronze disc and renewable seat.[ Include union-ring bonnet.]

K. Type 3, Class 200, Bronze Globe Valves:  Bronze body with bronze disc and renewable seat.[ Include union-ring bonnet.]

2.17 CAST-IRON GLOBE VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Type I, Cast-Iron Globe Valves with Metal Seats:

a. Cincinnati Valve Co.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Div.

e. Grinnell Corporation.

f. Hammond Valve.

g. Kitz Corporation of America.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. Powell, Wm. Co.

k. Red-White Valve Corp.

l. Walworth Co.

B. Cast-Iron Globe Valves, General:  MSS SP-85.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Type I, Class 125, Cast-Iron Globe Valves:  Gray-iron body with bronze seats.

D. Type I, Class 250, Cast-Iron Globe Valves:  Gray-iron body with bronze seats.

2.18 CAST-IRON PLUG VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
MSS SP-78 includes Types I, II, III, and IV for valve construction, but these types offer little help in selection.  MSS SP-78 also refers to "lubricated" and "nonlubricated" types, which are terms used in this Article.

1. Lubricated-Type, Cast-Iron Plug Valves:

a. Milliken Valve Co., Inc.

b. Nordstrom Valves, Inc.

c. Olson Technologies; Homestead Div.

d. R & M Energy Systems (Tomball, TX).

e. Walworth Co.

2. Nonlubricated-Type, Cast-Iron Plug Valves:

a. General Signal; DeZurik Unit.

b. Grinnell Corporation.

c. Mueller Flow Technologies.

d. Tyco International, Ltd.; Tyco Valves & Controls.

e. Wheatley Gaso, Inc.

f. Xomox Corporation.

B. Cast-Iron Plug Valves, General:  MSS SP-78.

Add specific materials, attributes, and features to paragraphs below to suit Project.

C. Class 125 or 150, lubricated-type, cast-iron plug valves.

D. Class 250 or 300, lubricated-type, cast-iron plug valves.

E. Class 125 or 150, nonlubricated-type, cast-iron plug valves.

F. Class 250, nonlubricated-type, cast-iron plug valves.

2.19 RESILIENT-SEATED, CAST-IRON, ECCENTRIC PLUG VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. General Signal; DeZurik Unit.

2. Milliken Valve Company.

3. Olson Technologies; Homestead Div.

4. Pratt, Henry Company.

5. Val-Matic Valve & Mfg. Corp.

The standard for resilient-seated, eccentric plug valves covers NPS 3 (DN 80) and larger.  Similar smaller valves are available.

Add specific materials, attributes, and features to paragraphs below to suit Project.

B. Resilient-Seated, Cast-Iron, Eccentric Plug Valves, DN 65 (NPS 2-1/2) and Smaller:  Design similar to MSS SP-108, and rated for 1207-kPa (175-psig) minimum CWP.

1. Resilient Seating Material:  Suitable for potable-water service, unless otherwise indicated.

C. Resilient-Seated, Cast-Iron, Eccentric Plug Valves, DN 80 (NPS 3) and Larger:  MSS SP-108, and rated for 1207-kPa (175-psig) minimum CWP.

1. Resilient Seating Material:  Suitable for potable-water service, unless otherwise indicated.

2.20 STAINLESS STEEL NEEDLE VALVES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Dragon Valves, Inc.

2. Hoke Incorporated.
3. Kerotest Mfg Corp.

4. Noshok, Inc.

5. Parker Hannifin Corp.

6. Swagelock.

Needle valves are suggested for use between pressure gauges and pressure tap on piping and equipment.  They provide tight shutoff and damping of liquid pulsations without requiring a separate pulse damping device.

Stainless steel body, [304] [316] [AISI 1213] [<Insert other material>] DN 4 mm to 12 mm (1/8-inch to ½ inch NPT), [Hard seat, soft seat] [<Insert other seat materials>]  Pressure rating [4100 kPa  (600 psig)] [41000 kPa  (6000 psig)] [<Insert other pressure rating>].
2.21 CHAINWHEEL ACTUATORS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Babbitt Steam Specialty Co.

2. Roto Hammer Industries, Inc.

B. Description:  Valve actuation assembly with sprocket rim, brackets, and chain.

Retain only ductile iron in first subparagraph below unless another material is required.  Delete zinc coating unless required.

1. Sprocket Rim with Chain Guides:  [Ductile iron] [Cast iron] [Aluminum] [Bronze], of type and size required for valve.[Include zinc coating.]

2. Brackets:  Type, number, size, and fasteners required to mount actuator on valve.

Retain only hot-dip, galvanized steel below unless another material is required.

3. Chain:  [Hot-dip, galvanized steel] [Brass] [Stainless steel], of size required to fit sprocket rim.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine piping system for compliance with requirements for installation tolerances and other conditions affecting performance.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

B. Examine valve interior for cleanliness, freedom from foreign matter, and corrosion.  Remove special packing materials, such as blocks, used to prevent disc movement during shipping and handling.

C. Operate valves in positions from fully open to fully closed.  Examine guides and seats made accessible by such operations.

D. Examine threads on valve and mating pipe for form and cleanliness.

E. Examine mating flange faces for conditions that might cause leakage.  Check bolting for proper size, length, and material.  Verify that gasket is of proper size, that its material composition is suitable for service, and that it is free from defects and damage.

F. Do not attempt to repair defective valves; replace with new valves.

3.2 VALVE APPLICATIONS

Data in this Article will be incorporated into piping Sections when they are updated.  Delete applications below if they are covered in corresponding piping Sections.

A. Refer to piping Sections for specific valve applications.  If valve applications are not indicated, use the following:

1. Shutoff Service:  Ball, butterfly[, or gate] [, gate, or plug] valves.

2. Throttling Service:  Angle, ball, butterfly, or globe valves.

3. Pump Discharge:  Spring-loaded, lift-disc or wafer check valves.

4. Pressure Instruments:  Needle valves.

B. If valves with specified SWP classes or CWP ratings are not available, the same types of valves with higher SWP class or CWP ratings may be substituted.

This Section is arranged to provide copper-alloy valves in NPS 2 (DN 50) and smaller and ferrous-alloy valves in NPS 2-1/2 (DN 65) and larger.  Edit sizes for copper- and ferrous-alloy valves to suit Project.  Many types of copper-alloy valves are made in at least NPS 4 (DN 100).  Many ferrous-alloy valves are made in NPS 2 (DN 50) and larger.

Caution:  Verify that valve classes and pressure and temperature ratings are adequate for system fluid.  Repeat each category listing if necessary and add required pressure range for each listing.  Indicate different pressure systems on Drawings.

Valves in categories below are recommended.  Delete valve types not required and add required types from Part 2 articles.

C. Chilled-Water Piping:  Use the following types of valves:

1. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

2. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

Single-flange or flanged butterfly valves in subparagraph below are required for dead-end service.

3. Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [Flangeless] [Single-flange] [Flanged], [1035-kPa (150-psig)] [1207-kPa (175-psig)] [1380-kPa (200-psig)] [1725-kPa (250-psig)] [2070-kPa (300-psig)] CWP rating, ferrous alloy, with [EPDM] <Insert other> liner.

Single-flange, high-pressure butterfly valves in subparagraph below are required for dead-end service.

4. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class  [150] [300].

5. Grooved-End, Ductile-Iron Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

6. Lift Check Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], [horizontal] [or] [vertical], bronze.

7. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

8. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron.

9. Grooved-End, Ductile-Iron, Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

10. Wafer Check Valves, DN 65 (NPS 2-1/2) and Larger:  [Single] [Dual]-plate, [wafer] [wafer-lug] [double-flanged], Class  [125 or 150] [250 or 300] ferrous alloy.

11. Spring-Loaded, Lift-Disc Check Valves, DN 50 (NPS 2) and Smaller:  Type IV, Class  [125 minimum] [150] [200].

12. Spring-Loaded, Lift-Disc Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [I or II] [II] [III], Class  [125] [250], cast iron.

13. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [2] [3], Class  [125] [150] [200], bronze.

14. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

15. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

16. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

17. Plug Valves, DN 50 (NPS 2) and Larger:  Class  [125 or 150] [250 or 300], [lubricated] [nonlubricated]-type, cast iron.

18. Resilient-Seated, Eccentric Plug Valves, DN 80 (NPS 3) and Larger:  1207-kPa (175-psig) CWP rating, cast iron.

Delete low-pressure, compressed-air piping applications below if compressed-air valves are covered in Division 15 Section "Compressed-Air Piping."

D. Low-Pressure, Compressed-Air Piping:  Use the following types of valves:

1. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

2. Equipment-Isolation Ball Valves, DN 50 (NPS 2) and Smaller:  Safety-exhaust, bronze.

3. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

4. Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [Flangeless] [Single-flange] [Flanged], [1035-kPa (150-psig)] [1207-kPa (175-psig)] [1380-kPa (200-psig)] [1725-kPa (250-psig)] [2070-kPa (300-psig)] CWP rating, ferrous alloy, with [NBR] <Insert other> liner.

5. Grooved-End, Ductile-Iron Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

6. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class  [150] [300].

7. Lift Check Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], [horizontal] [or] [vertical], bronze.

8. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

9. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron.

10. Grooved-End, Ductile-Iron, Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

Caution:  Verify that check valves selected from first three subparagraphs below are suitable for low-pressure, compressed-air piping applications.

11. Wafer Check Valves, DN 65 (NPS 2-1/2) and Larger:  [Single] [Dual]-plate, [wafer] [wafer-lug] [double-flanged], Class  [125 or 150] [250 or 300] ferrous alloy.

12. Spring-Loaded, Lift-Disc Check Valves, DN 50 (NPS 2) and Smaller:  Type IV, Class  [125 minimum] [150].

13. Spring-Loaded, Lift-Disc Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [I or II] [II] [III], Class  [125] [250], cast iron.

14. Gate Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

15. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

16. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

17. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

Delete medium-pressure, compressed-air piping applications below if compressed-air valves are covered in Division 15 Section "Compressed-Air Piping."

E. Medium-Pressure, Compressed-Air Piping:  Use the following types of valves:

1. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

2. Equipment-Isolation Ball Valves, DN 50 (NPS 2) and Smaller:  Safety-exhaust, bronze.

3. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

4. Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [Flangeless] [Single-flange] [Flanged], [1035-kPa (150-psig)] [1207-kPa (175-psig)] [1380-kPa (200-psig)] [1725-kPa (250-psig)] [2070-kPa (300-psig)] CWP rating, ferrous alloy, with [NBR] <Insert other> liner.

5. Grooved-End, Ductile-Iron Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

6. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class  [150] [300].

7. Lift Check Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], [horizontal] [or] [vertical], bronze.

8. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

9. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron.

10. Grooved-End, Ductile-Iron, Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

Caution:  Verify that check valves selected from first three subparagraphs below are suitable for medium-pressure, compressed-air piping applications.

11. Wafer Check Valves, DN 65 (NPS 2-1/2) and Larger:  [Single] [Dual]-plate, [wafer] [wafer-lug] [double-flanged], Class  [125 or 150] [250 or 300], ferrous alloy.

12. Spring-Loaded, Lift-Disc Check Valves, DN 50 (NPS 2) and Smaller:  Type IV, Class  [125 minimum] [150].

13. Spring-Loaded, Lift-Disc Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [I or II] [II] [III], Class  [125] [250], cast iron.

14. Gate Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

15. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

16. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

17. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

F. Condenser Water Piping:  Use the following types of valves:

1. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

2. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

Single-flange or flanged butterfly valves in subparagraph below are required for dead-end service.

3. Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [Flangeless] [Single-flange] [Flanged], [1035-kPa (150-psig)] [1207-kPa (175-psig)] [1380-kPa (200-psig)] [1725-kPa (250-psig)] [2070-kPa (300-psig)] CWP rating, ferrous alloy, with [EPDM] <Insert other> liner.

Single-flange, high-pressure butterfly valves in subparagraph below are required for dead-end service.

4. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class  [150] [300].

5. Grooved-End, Ductile-Iron Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

6. Lift Check Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], [horizontal] [or] [vertical], bronze.

7. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

8. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron.

9. Grooved-End, Ductile-Iron, Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

10. Wafer Check Valves, DN 65 (NPS 2-1/2) and Larger:  [Single] [Dual]-plate, [wafer] [wafer-lug] [double-flanged], Class  [125 or 150] [250 or 300], ferrous alloy.

11. Spring-Loaded, Lift-Disc Check Valves, DN 50 (NPS 2) and Smaller:  Type IV, Class  [125 minimum] [150] [200].

12. Spring-Loaded, Lift-Disc Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [I or II] [II] [III], Class  [125] [250], cast iron.

13. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [2] [3], Class  [125] [150] [200], bronze.

14. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

15. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

16. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

17. Plug Valves, DN 50 (NPS 2) and Larger:  Class  [125 or 150] [250 or 300], [lubricated] [nonlubricated]-type, cast iron.

Verify that eccentric plug valves are suitable for fluid temperature; delete subparagraph below if not suitable.

18. Resilient-Seated, Eccentric Plug Valves, DN 80 (NPS 3) and Larger:  1207-kPa (175-psig) CWP rating, cast iron.

G. Domestic Water Piping:  Use the following types of valves:

1. Angle Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

2. Angle Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], cast iron.

3. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

4. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

5. Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [Flangeless] [Single-flange] [Flanged], [1035-kPa (150-psig)] [1207-kPa (175-psig)] [1380-kPa (200-psig)] [1725-kPa (250-psig)] [2070-kPa (300-psig)] CWP rating, ferrous alloy, with EPDM liner.

6. Grooved-End, Ductile-Iron Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

7. Lift Check Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], [horizontal] [or] [vertical], bronze.

8. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

9. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron.

10. Grooved-End, Ductile-Iron, Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

11. Wafer Check Valves, DN 65 (NPS 2-1/2) and Larger:  [Single] [Dual]-plate, [wafer] [wafer-lug] [double-flanged], Class  [125 or 150] [250 or 300], ferrous alloy.

12. Spring-Loaded, Lift-Disc Check Valves, DN 50 (NPS 2) and Smaller:  Type IV, Class  [125 minimum] [150] [200].

13. Spring-Loaded, Lift-Disc Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [I or II] [II] [III], Class  [125] [250], cast iron.

14. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [1] [2], Class  [125] [150] [200], bronze.

15. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

16. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

17. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

18. Plug Valves, DN 50 (NPS 2) and Larger:  Class  [125 or 150] [250 or 300], [lubricated-type with FDA-approved-material sealant] [nonlubricated-type], cast iron.

19. Resilient-Seated, Eccentric Plug Valves, DN 80 (NPS 3) and Larger:  1207-kPa (175-psig) CWP rating, cast iron.

H. Heating Water Piping:  Use the following types of valves:

1. Angle Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

2. Angle Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], cast iron.

3. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

4. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

5. Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [Flangeless] [Single-flange] [Flanged], [1035-kPa (150-psig)] [1207-kPa (175-psig)] [1380-kPa (200-psig)] [1725-kPa (250-psig)] [2070-kPa (300-psig)] CWP rating, ferrous alloy, with [EPDM] <Insert other> liner.

6. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class  [150] [300].

7. Grooved-End, Ductile-Iron Butterfly Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

8. Lift Check Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], [horizontal] [vertical], bronze.

9. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

10. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron.

11. Grooved-End, Ductile-Iron, Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  [1207-kPa (175-psig)] [2070-kPa (300-psig)] CWP rating.

Verify that wafer check valves selected from subparagraph below are suitable for fluid temperature; delete below if not suitable.

12. Wafer Check Valves, DN 65 (NPS 2-1/2) and Larger:  [Single] [Dual]-plate, [wafer] [wafer-lug] [double-flanged], Class  [125 or 150] [250 or 300], ferrous alloy.

13. Spring-Loaded, Lift-Disc Check Valves, DN 50 (NPS 2) and Smaller:  Type IV, Class  [125 minimum] [150] [200].

14. Spring-Loaded, Lift-Disc Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [I or II] [II] [III], Class  [125] [250], cast iron.

15. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [2] [3], Class  [125] [150] [200], bronze.

16. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

17. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

18. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

19. Plug Valves, DN 50 (NPS 2) and Larger:  Class  [125 or 150] [250 or 300], [lubricated] [nonlubricated]-type, cast iron.

Verify that eccentric plug valves are suitable for fluid temperature; delete subparagraph below if not suitable.

20. Resilient-Seated, Eccentric Plug Valves, DN 80 (NPS 3) and Larger:  1207-kPa (175-psig) CWP rating, cast iron.

I. [Sanitary Waste] [and] [Storm Drainage] Piping:  Use the following types of valves:

1. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

2. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class 150, ferrous alloy.

3. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type  [3] [4], Class  [125] [150], bronze.

4. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [or] [II], Class 125, gray iron.

5. Grooved-End, Ductile-Iron, Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  1207-kPa (175-psig) minimum CWP rating.

6. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [1] [2], Class  [125] [150], bronze.

7. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class 125, [NRS] [OS&Y], bronze-mounted cast iron.

8. Globe Valves, DN 50 (NPS 2) and Smaller:  Type  [1] [2], Class  [125] [150], bronze.

9. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class 125, cast iron.

10. Plug Valves, DN 50 (NPS 2) and Larger:  Class 125 or 150, [lubricated] [nonlubricated]-type, cast iron.

J. Low-Pressure Steam Piping:  Use the following types of valves:

1. Angle Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150], bronze.

2. Angle Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class 125, cast iron.

3. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

4. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class 150, ferrous alloy.

5. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class 150.

6. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150], bronze.

7. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class 125, gray iron.

8. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [2] [3], Class  [125] [150], bronze.

9. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class 125, [NRS] [OS&Y], bronze-mounted cast iron.

10. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150], bronze.

11. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class 125, bronze-mounted cast iron.

K. High-Pressure Steam Piping:  Use the following types of valves:

1. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

2. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

3. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class  [150] [300].

4. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

5. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron

6. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [2] [3], Class  [125] [150] [200], bronze.

7. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

8. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 1, Class  [125] [150] [200], bronze.

9. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

L. Steam Condensate Piping:  Use the following types of valves:

1. Ball Valves, DN 50 (NPS 2) and Smaller:  [One] [Two] [Three]-piece, [2760-kPa (400-psig)] [4140-kPa (600-psig)] <Insert other> CWP rating, copper alloy.

2. Ball Valves, DN 65 (NPS 2-1/2) and Larger:  Class  [150] [300], ferrous alloy.

3. High-Pressure Butterfly Valves, DN 80 (NPS 3) and Larger:  [Flangeless] [Single-flange], Class  [150] [300].

4. Swing Check Valves, DN 50 (NPS 2) and Smaller:  Type 4, Class  [125] [150] [200], bronze.

5. Swing Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type II, Class  [125] [250], gray iron.

6. Spring-Loaded, Lift-Disc Check Valves, DN 50 (NPS 2) and Smaller:  Type IV, Class  [125 minimum] [150] [200].

7. Spring-Loaded, Lift-Disc Check Valves, DN 65 (NPS 2-1/2) and Larger:  Type  [I] [I or II] [II] [III], Class  [125] [250], cast iron.

8. Gate Valves, DN 50 (NPS 2) and Smaller:  Type  [2] [3], Class  [125] [150] [200], bronze.

9. Gate Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], [NRS] [OS&Y], bronze-mounted cast iron.

10. Globe Valves, DN 50 (NPS 2) and Smaller:  Type 2, Class  [125] [150] [200], bronze.

11. Globe Valves, DN 65 (NPS 2-1/2) and Larger:  Type I, Class  [125] [250], bronze-mounted cast iron.

12. Plug Valves, DN 50 (NPS 2) and Larger:  Class  [125 or 150] [250 or 300], [lubricated] [nonlubricated]-type, cast iron.

M. Select valves, except wafer and flangeless types, with the following end connections:

1. For Copper Tubing, DN 50 (NPS 2) and Smaller:  Solder-joint or threaded ends, except provide valves with threaded ends for [condenser water,] heating hot water, steam, and steam condensate services.

2. For Copper Tubing, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Flanged [or threaded] ends.

3. For Copper Tubing, DN 125 (NPS 5) and Larger:  Flanged ends.

4. For Steel Piping, DN 50 (NPS 2) and Smaller:  Threaded ends.

5. For Steel Piping, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Flanged [or threaded] ends.

6. For Steel Piping, DN 125 (NPS 5) and Larger:  Flanged ends.

7. For Grooved-End, [copper tubing] [and] [steel piping]:  Valve ends may be grooved.  Do not use for steam or steam condensate piping.

N. Instrumentation – pressure gages and sensing lines.

1. Needle valves, stainless, brass or bronze as required.

3.3 VALVE INSTALLATION

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.

C. Locate valves for easy access and provide separate support where necessary.

D. Install valves in horizontal piping with stem at or above center of pipe.

E. Install valves in position to allow full stem movement.

Delete or edit first paragraph below to suit Project.

F. Install chainwheel operators on valves [DN 100 (NPS 4)] <Insert other> and larger when valve is more than [2400 mm (96 inches)] <Insert other> above floor.  Extend chains to [1520 mm (60 inches)] <Insert other> above finished floor elevation.

G. Install gear drive operators on valves [DN 100 (NPS 4)] <Insert other> and larger.  Furnish chain operator on gear drives when valve is more than [96 inches (2400 mm)]  <Insert other> above finished floor.

H. Install check valves for proper direction of flow and as follows:

Edit check valve installation requirements to suit Project.  Delete check valves not required.

1. Swing Check Valves:  In horizontal position with hinge pin level.

2. Dual-Plate Check Valves:  In horizontal or vertical position, with flow direction up, between flanges.

3. Lift Check Valves:  With stem upright and plumb.

3.4 JOINT CONSTRUCTION

A. Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic piping joint construction.

B. Grooved Joints:  Assemble joints with keyed coupling housing, gasket, lubricant, and bolts according to coupling and fitting manufacturer's written instructions.

C. Soldered Joints:  Use ASTM B 813, water-flushable, lead-free flux; ASTM B 32, lead-free-alloy solder; and ASTM B 828 procedure, unless otherwise indicated.

3.5 ADJUSTING

A. Adjust or replace valve packing after piping systems have been tested and put into service but before final adjusting and balancing.  Replace valves if persistent leaking occurs.

END OF SECTION 15110

VALVES
15110 - 37

