Copyright 2001 AIA
MASTERSPEC
06/01 (GSA 03/05)

Copyright 2001, The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15122 – METERS AND GAGES

PART 1 -  GENERAL

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete notes to editor before submission.

1.2 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.3 SUMMARY

A. This Section includes the following meters and gages for mechanical systems:

Adjust list below to suit Project.

1. Thermometers.

2. Gages.

3. Test plugs.

4. Flowmeters.

5. Thermal-energy meters.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Water Distribution" for domestic and fire-protection water service meters outside the building.

2. Division 2 Section "Natural Gas Distribution" for gas meters outside the building.

3. Division 13 Section "[Electric-Drive, Centrifugal Fire Pumps] [Diesel-Drive, Centrifugal Fire Pumps] [Electric-Drive, Vertical-Turbine Fire Pumps] [Diesel-Drive, Vertical-Turbine Fire Pumps]" for fire-pump flowmeter systems.

4. Division 15 Section "Domestic Water Piping" for domestic and fire-protection water service meters inside the building.

5. Division 15 Section "Steam and Condensate Piping" for steam and condensate meters.

6. Division 15 Section "Fuel Gas Piping" for gas meters inside the building.

1.4 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. CR:  Chlorosulfonated polyethylene synthetic rubber.

B. EPDM:  Ethylene-propylene-diene terpolymer rubber.

1.5 SUBMITTALS

A. Product Data:  For each type of product indicated; include performance curves.

B. Shop Drawings:  Schedule for [thermometers] [gages] [flowmeters] [and] [thermal-energy meters] indicating manufacturer's number, scale range, and location for each.

C. Product Certificates:  For each type of [thermometer] [gage] [flowmeter] [and] [thermal-energy meter], signed by product manufacturer.

D. Operation and Maintenance Data:  For [flowmeters] [and] [thermal-energy meters] to include in emergency, operation, and maintenance manuals.

PART 2 -  PRODUCTS

2.2 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.  

2.3 METAL-CASE, LIQUID-IN-GLASS THERMOMETERS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Palmer - Wahl Instruments Inc.

2. Trerice, H. O. Co.

3. Weiss Instruments, Inc.

4. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

5. <Insert manufacturer's name.>

B. Case:  [Die-cast aluminum] [Die-cast aluminum or brass] [Brass] [Chrome-plated brass], [178 mm (7 inches)] [229 mm (9 inches)] <Insert other> long.

C. Tube:  Red or blue reading, [mercury] [mercury or organic-liquid] [organic-liquid] filled, with magnifying lens.

D. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

E. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

F. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, straight type] [Rigid, angle type].

G. Stem:  Copper-plated steel, aluminum, or brass for thermowell installation and of length to suit installation.

H. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.4 PLASTIC-CASE, LIQUID-IN-GLASS THERMOMETERS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Ernst Gage Co.

2. Eugene Ernst Products Co.

3. Marsh Bellofram.

4. Miljoco Corp.

5. Trerice, H. O. Co.

6. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

7. Winters Instruments.

8. <Insert manufacturer's name.>

B. Case:  Plastic, [178 mm (7 inches)] [229 mm (9 inches)] <Insert other> long.

C. Tube:  Red or blue reading, mercury or organic-liquid filled, with magnifying lens.

D. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

E. Window:  Glass or plastic.

F. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, straight type] [Rigid, angle type].

G. Stem:  Metal, for thermowell installation and of length to suit installation.

H. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.5 DUCT-TYPE, LIQUID-IN-GLASS THERMOMETERS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Miljoco Corp.

2. Palmer - Wahl Instruments Inc.

3. Trerice, H. O. Co.

4. Weiss Instruments, Inc.

5. <Insert manufacturer's name.>

B. Case:  [Die-cast aluminum] [Metal or plastic], [178 mm (7 inches)] <Insert other> long.

C. Tube:  Red or blue reading, mercury or organic filled, with magnifying lens.

D. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

E. Window:  [Glass or plastic] <Insert other>.

F. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, angle type].

G. Stem:  Metal, for installation in mounting bracket and of length to suit installation.

H. Mounting Bracket:  Flanged fitting for attachment to duct and made to hold thermometer stem.

I. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.
This type thermometer should only be used on equipment and ductwork that is not subject to vibration or pulsations and where only approximate temperature readings are required.  Use liquid glass when more accurate readings are required.
2.6 DIRECT-MOUNTING, VAPOR-ACTUATED DIAL THERMOMETERS
A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

2. KOBOLD Instruments, Inc.

3. Marsh Bellofram.

4. Trerice, H. O. Co.

5. Weiss Instruments, Inc.

6. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

7. <Insert manufacturer's name.>

B. Case:  [Dry] [Liquid-filled] type, [drawn steel or cast aluminum] [metal or plastic] [plastic], [114-mm (4-1/2-inch)] [127-mm (5-inch)] [152-mm (6-inch)] <Insert other> diameter.

C. Element:  Bourdon tube or other type of pressure element.

D. Movement:  Mechanical, connecting element and pointer.

E. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

F. Pointer:  Red[ or other dark-color] metal.

G. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

H. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

I. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, bottom type] [Rigid, back type].

J. Thermal System:  Liquid- or mercury-filled bulb in copper-plated steel, aluminum, or brass stem for thermowell installation and of length to suit installation.

K. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

This type of thermometer should only be used when local, approximate temperature readings are required.  Use DDC control system with remote readout panels when more accurate readings are required.
2.7 REMOTE-MOUNTING, VAPOR-ACTUATED DIAL THERMOMETERS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Marsh Bellofram.

4. Miljoco Corp.

5. Palmer - Wahl Instruments Inc.

6. REO TEMP Instrument Corporation.

7. Tel-Tru Manufacturing Company.

8. Trerice, H. O. Co.

9. Weiss Instruments, Inc.

10. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

11. Winters Instruments.

12. <Insert manufacturer's name.>

B. Case:  Dry type, [drawn steel or cast aluminum] <Insert other>, [114-mm (4-1/2-inch)] [152-mm (6-inch)] <Insert other> diameter with [holes] <Insert other> for panel mounting.

C. Element:  Bourdon tube or other type of pressure element.

D. Movement:  Mechanical, connecting element and pointer.

E. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

F. Pointer:  Red[ or other dark-color] metal.

G. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

H. Ring:  [Metal] [Brass] [Stainless steel].

I. Connector:  [Bottom] [Back] union type.

J. Thermal System:  Liquid- or mercury-filled bulb in copper-plated steel, aluminum, or brass stem for thermowell installation and of length to suit installation.

K. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

This type of thermometer should only be used when local, approximate temperature readings are required.  Use the DDC control system with remote readout panels when more accurate readings are required.
2.8 THERMOWELLS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Ernst Gage Co.

4. Marsh Bellofram.

5. Miljoco Corp.

6. NANMAC Corporation.

7. Noshok, Inc.

8. Palmer - Wahl Instruments Inc.

9. REO TEMP Instrument Corporation.

10. Tel-Tru Manufacturing Company.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

B. Description:  [Bronze or brass] [Stainless steel] [Bronze, brass or stainless steel] pressure-tight, socket-type metal fitting made for insertion into piping and of type, diameter, and length required to hold thermometer.

2.9 PRESSURE GAGES

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Ernst Gage Co.

4. Eugene Ernst Products Co.

5. KOBOLD Instruments, Inc.

6. Marsh Bellofram.

7. Miljoco Corp.

8. Noshok, Inc.

9. Palmer - Wahl Instruments Inc.

10. REO TEMP Instrument Corporation.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

B. Direct-Mounting, Dial-Type Pressure Gages:  Indicating-dial type complying with ASME B40.100.

1. Case:  [Dry] [Liquid-filled] type, [drawn steel or cast aluminum] [metal or plastic] [plastic], [114-mm (4-1/2-inch)] [152-mm (6-inch)] <Insert other> diameter.

2. Pressure-Element Assembly:  Bourdon tube, unless otherwise indicated.

3. Pressure Connection:  Brass, DN 8 (NPS 1/4), bottom-outlet type unless back-outlet type is indicated.

4. Movement:  Mechanical, with link to pressure element and connection to pointer.

5. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

6. Pointer:  Red[ or other dark-color] metal.

7. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

8. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

9. Accuracy:  Grade [A, plus or minus 1 percent of middle half] [B, plus or minus 2 percent of middle half] [C, plus or minus 3 percent of middle half] [D, plus or minus 5 percent of whole] scale.

10. Vacuum-Pressure Range:  100 kPa of vacuum to 103 kPa of pressure (30-in. Hg of vacuum to 15 psig of pressure).

11. Range for Fluids under Pressure:  Two times operating pressure.

C. Remote-Mounting, Dial-Type Pressure Gages:  ASME B40.100, indicating-dial type.

1. Case:  Dry type, [drawn steel or cast aluminum] <Insert other>, [114-mm (4-1/2-inch)] [152-mm (6-inch)] <Insert other> diameter with [holes] <Insert other> for panel mounting.

2. Pressure-Element Assembly:  Bourdon tube, unless otherwise indicated.

3. Pressure Connection:  Brass, DN 8 (NPS 1/4), bottom-outlet type unless back-outlet type is indicated.

4. Movement:  Mechanical, with link to pressure element and connection to pointer.

5. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

6. Pointer:  Red[ or other dark-color] metal.

7. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

8. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

9. Accuracy:  Grade [A, plus or minus 1 percent of middle half] [B, plus or minus 2 percent of middle half] [C, plus or minus 3 percent of middle half] [D, plus or minus 5 percent of whole] scale.

10. Vacuum-Pressure Range:  100 kPa of vacuum to 103 kPa of pressure (30-in. Hg of vacuum to 15 psig of pressure).

11. Range for Fluids under Pressure:  Two times operating pressure.

D. Pressure-Gage Fittings:

1. Valves:  DN 8 (NPS 1/4) brass or stainless-steel needle type.

2. Syphons:  DN 8 (NPS 1/4) coil of brass tubing with threaded ends.

3. Snubbers:  ASME B40.5, DN 8 (NPS 1/4) brass bushing with corrosion-resistant, porous-metal disc of material suitable for system fluid and working pressure.

2.10 TEST PLUGS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Flow Design, Inc.

2. MG Piping Products Co.

3. National Meter, Inc.

4. Peterson Equipment Co., Inc.

5. Sisco Manufacturing Co.

6. Trerice, H. O. Co.

7. Watts Industries, Inc.; Water Products Div.

8. <Insert manufacturer's name.>

B. Description:  Corrosion-resistant brass or stainless-steel body with core inserts and gasketed and threaded cap, with extended stem for units to be installed in insulated piping.

C. Minimum Pressure and Temperature Rating:  [3450 kPa at 93 deg C (500 psig at 200 deg F)] <Insert other>.

D. Core Inserts:  One or two self-sealing rubber valves.

1. Insert material for air, water, oil, or gas service at minus 7 to plus 93 deg C (20 to 200 deg F) shall be CR.

2. Insert material for air or water service at minus 35 to plus 136 deg C (minus 30 to plus 275 deg F) shall be EPDM.

Retain paragraph and subparagraphs below if required.

E. Test Kit:  Furnish [one] <Insert other> test kit(s) containing one pressure gage and adaptor, [one] [two] thermometer(s), and carrying case.  Pressure gage, adapter probes, and thermometer sensing elements shall be of diameter to fit test plugs and of length to project into piping.

1. Pressure Gage:  Small bourdon-tube insertion type with [51- to 76-mm- (2- to 3-inch-)] <Insert other> diameter dial and probe.  Dial range shall be [0 to 1380 kPa (0 to 200 psig)] <Insert other>.

2. Pressure Probe:  Pressure probe shall have minimum DN4 (NPS 1/8) connection for use with large face pressure gage or a pressure transducer or other pressure measuring instrument.
3. Low-Range Thermometer:  Small bimetallic insertion type with [25- to 51-mm- (1- to 2-inch-)] <Insert other> diameter dial and tapered-end sensing element.  Dial ranges shall be [minus 4 to plus 52 deg C (25 to 125 deg F)] <Insert other>.

Retain subparagraph above or first subparagraph below if only one thermometer is required.

4. High-Range Thermometer:  Small bimetallic insertion type with [25- to 51-mm- (1- to 2-inch-)] <Insert other> diameter dial and tapered-end sensing element.  Dial ranges shall be [minus 18 to plus 104 deg C (0 to 220 deg F)] <Insert other>.

5. Carrying case shall have formed instrument padding.

2.11 WAFER-ORIFICE FLOWMETERS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. ABB, Inc.; ABB Instrumentation.

2. Armstrong Pumps, Inc.

3. Badger Meter, Inc.; Industrial Div.

4. Bell & Gossett; ITT Industries.

5. Meriam Instruments Div.; Scott Fetzer Co.

6. <Insert manufacturer's name.>

B. Description:  Differential-pressure-design orifice insert for installation between pipe flanges; with calibrated flow-measuring element, separate flowmeter, hoses or tubing, valves, fittings, and conversion chart compatible with flow-measuring element, flowmeter, and system fluid.

C. Construction:  Cast-iron body, brass valves with integral check valves and caps, and calibrated nameplate.

D. Pressure Rating:  [2070 kPa (300 psig)] <Insert other>.

E. Temperature Rating:  [121 deg C (250 deg F)] <Insert other>.

F. Range:  Flow range of flow-measuring element and flowmeter shall cover operating range of equipment or system served.

Retain one of first two paragraphs and associated subparagraphs below.

G. Permanent Indicators:  Suitable for wall or bracket mounting, calibrated for connected flowmeter element, and having 150-mm- (6-inch-) diameter, or equivalent, dial with fittings and copper tubing for connecting to flowmeter element.

1. Scale:  Liters per second (Gallons per minute).

2. Accuracy:  Plus or minus 1 percent between 20 and 80 percent of range.

H. Portable Indicators:  Differential-pressure type calibrated for connected flowmeter element and having two 3.7-m (12-foot) hoses in carrying case.

1. Scale:  Liters per second (Gallons per minute).

2. Accuracy:  Plus or minus 2 percent between 20 and 80 percent of range.

I. Remote Indicator: Differential – pressure transmitter calibrated for flowmeter element.

J. Operating Instructions:  Include complete instructions with each flowmeter.

2.12 VENTURI FLOWMETERS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Armstrong Pumps, Inc.

2. Badger Meter, Inc.; Industrial Div.

3. Bailey-Fischer & Porter Co.

4. Flow Design, Inc.

5. Gerand Engineering Co.

6. Hyspan Precision Products, Inc.

7. Leeds & Northrup.

8. McCrometer, Inc.

9. Preso Meters Corporation.

10. Victaulic Co. of America.

11. <Insert manufacturer's name.>

B. Description:  Differential-pressure design for installation in piping; with calibrated flow-measuring element, separate flowmeter, hoses or tubing, valves, fittings, and conversion chart compatible with flow-measuring element, flowmeter, and system fluid.

C. Construction:  Bronze, brass, or factory-primed steel; with brass fittings and attached tag with flow conversion data.

D. Pressure Rating:  [1725 kPa (250 psig)] <Insert other>.

E. Temperature Rating:  [121 deg C (250 deg F)] <Insert other>.

F. End Connections for DN 50 (NPS 2) and Smaller:  Threaded.

G. End Connections for DN 65 (NPS 2-1/2) and Larger:  Flanged or welded.

H. Range:  Flow range of flow-measuring element and flowmeter shall cover operating range of equipment or system served.

Retain one of first two paragraphs and associated subparagraphs below.

I. Permanent Indicators:  Suitable for wall or bracket mounting, calibrated for connected flowmeter element, and having 150-mm- (6-inch-) diameter, or equivalent, dial with fittings and copper tubing for connecting to flowmeter element.

1. Scale:  Liters per second (Gallons per minute).

2. Accuracy:  Plus or minus 1 percent between 20 and 80 percent of range.

J. Portable Indicators:  Differential-pressure type calibrated for connected flowmeter element and having two 3.7-m (12-foot) hoses in carrying case.

1. Scale:  Liters per second (Gallons per minute).

2. Accuracy:  Plus or minus 2 percent between 20 and 80 percent of range.

K. Remote Indicator: Differential – pressure transmitter calibrated for flowmeter element.

L. Operating Instructions:  Include complete instructions with each flowmeter.

2.13 TURBINE FLOWMETERS

Turbine flowmeters can be used with a transmitter to send signals to a remote meter terminal.

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Badger Meter, Inc.; Industrial Div.

2. Bailey-Fischer & Porter Co.

3. Data Industrial Corp.

4. Engineering Measurements Company.

5. ERDCO Engineering Corp.

6. Fisher, George Inc.

7. Hoffer Flow Controls, Inc.

8. ISTEC Corporation.

9. Midwest Instruments & Controls Corp.

10. ONICON Incorporated.

11. SeaMetrics Inc.

12. Sponsler Company, Inc.

13. Thermo Measurement Ltd.

14. Venture Measurement.

15. <Insert manufacturer's name.>

B. Description:  Insertion type for inserting turbine into piping and measuring flow directly in liters per second (gallons per minute).

C. Construction:  Bronze or stainless-steel body; with plastic turbine or impeller and integral direct-reading scale.

D. Pressure Rating:  [1035 kPa (150 psig)] <Insert other> minimum.

E. Temperature Rating:  [82 deg C (180 deg F)] <Insert other> minimum.

F. Display:  Visual instantaneous rate of flow[, with register to indicate total volume in liters (gallons)].

G. Accuracy:  Plus or minus 2-1/2 percent.

2.14 VORTEX-SHEDDING FLOWMETERS

Vortex-shedding flowmeters can be used with a transmitter to send signals to a remote meter terminal.

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Bailey-Fischer & Porter Co.

2. Engineering Measurements Company.

3. ISTEC Corporation.

4. MCO/Eastech, Inc.

5. Schlumberger Limited; Measurement Div.

6. Venture Measurement.

7. <Insert manufacturer's name.>

B. Description:  Inline type for installing between pipe flanges and measuring flow directly in liters per second (gallons per minute).

C. Construction:  Stainless-steel body; with integral transmitter and direct-reading scale.

D. Pressure Rating:  [6900 kPa (1000 psig)] <Insert other> minimum.

E. Temperature Rating:  [260 deg C (500 deg F)] <Insert other> minimum.

F. Display:  Visual instantaneous rate of flow[, with register to indicate total volume in liters (gallons)].

G. Integral Transformer:  For low-voltage power operation.

H. Accuracy:  Plus or minus 7/10 percent for liquids and 1-1/4 percent for gases.

2.15 PITOT-TUBE FLOWMETERS

Pitot-tube flowmeters can be used with a transmitter to send signals to a remote meter terminal.

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Dieterich Standard Inc.

2. Meriam Instruments Div.; Scott Fetzer Co.

3. Preso Meters Corporation.

4. Taco, Inc.

5. Veris, Inc.

6. <Insert manufacturer's name.>

B. Description:  Insertion-type, differential-pressure design for inserting probe into piping and measuring flow directly in liters per second (gallons per minute).

C. Construction:  Stainless-steel probe of length to span inside of pipe; with integral transmitter and direct-reading scale.

D. Pressure Rating:  [1035 kPa (150 psig)] <Insert other> minimum.

E. Temperature Rating:  [121 deg C (250 deg F)] <Insert other> minimum.

F. Display:  Visual instantaneous rate of flow[, with register to indicate total volume in liters (gallons)].

G. Integral Transformer:  For low-voltage power connection.

H. Accuracy:  Plus or minus 1 percent for liquids and gases.

2.16 FLOW INDICATORS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Brooks Instrument Div.; Emerson Electric Co.

2. Dwyer Instruments, Inc.

3. Ernst Gage Co.

4. Eugene Ernst Products Co.

5. McCrometer, Inc.

6. OPW Engineered Systems; Dover Corp.

7. Penberthy, Inc.

8. <Insert manufacturer's name.>

B. Description:  Instrument for installation in piping systems for visual verification of flow.

C. Construction:  Bronze or stainless-steel body; with sight glass and [plastic pelton-wheel] <Insert other> indicator, and threaded or flanged ends.

D. Pressure Rating:  [860 kPa (125 psig)] <Insert other>.

E. Temperature Rating:  [93 deg C (200 deg F)] <Insert other>.

F. End Connections for DN 50 (NPS 2) and Smaller:  Threaded.

G. End Connections for DN 65 (NPS 2-1/2) and Larger:  Flanged.

2.17 INSERTION-TURBINE, THERMAL-ENERGY METER SYSTEMS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Data Industrial Corp.

2. ONICON Incorporated.

3. Thermo Measurement Ltd.

4. <Insert manufacturer's name.>

B. Description:  Flow sensor,[ strainer,] two temperature sensors, transmitter, meter, and connecting wiring.

C. Flow Sensor:  Insertion-type turbine or paddle-wheel element with corrosion-resistant-metal body and transmitter.

1. Pressure Rating:  [860 kPa (125 psig)] <Insert other>.

2. Temperature Range:  [5 to 121 deg C (40 to 250 deg F)] <Insert other>.

D. Meter:  Solid-state integrating type[ with integral battery pack].

1. Data Output:  Six-digit electromechanical counter with readout in kilowatts per hour or joules (British thermal units).

2. Accuracy:  Plus or minus [1] <Insert other> percent.

3. Battery Pack:  Five-year lithium battery.

E. Strainer:  Full size of main line piping.

2.18 INLINE-TURBINE, THERMAL-ENERGY METER SYSTEMS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Engineering Measurements Company.

2. Hoffer Flow Controls, Inc.

3. ISTEC Corporation.

4. Thermo Measurement Ltd.

5. Venture Measurement.

6. <Insert manufacturer's name.>

B. Description:  Flow sensor,[ strainer,] two temperature sensors, transmitter, meter, and connecting wiring.

C. Flow Sensor:  Turbine-type water meter with corrosion-resistant-metal body and transmitter.

1. Pressure Rating:  [1035-kPa (150-psig)] <Insert other> minimum working-pressure rating.

2. Temperature Range:  [5 to 121 deg C (40 to 250 deg F)] <Insert other>.

D. Meter:  Solid-state integrating type[ with integral battery pack].

1. Data Output:  Six-digit electromechanical counter with readout in kilowatts per hour or joules (British thermal units).

2. Accuracy:  Plus or minus [1] <Insert other> percent.

3. Battery Pack:  Five-year lithium battery.

E. Strainer:  Full size of main line piping.

2.19 ULTRASONIC, THERMAL-ENERGY METER SYSTEMS

A. Available Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Controlotron Corporation.

2. Engineering Measurements Company.

3. Mesa Laboratories, Inc.; Nusonics Div.

4. <Insert manufacturer's name.>

B. Description:  Flow sensor, two temperature sensors, transmitter, meter, and connecting wiring.

C. Flow Sensor:  Strap-on or integral ultrasonic type with transmitter.

D. Meter:  Solid-state integrating type[ with integral battery pack].

1. Data Output:  Six-digit electromechanical counter with readout in kilowatts per hour or joules (British thermal units).

2. Accuracy:  Plus or minus [1] <Insert other> percent.

3. Battery Pack:  Five-year lithium battery.

E. Strainer:  Full size of main line piping.

PART 3 -  EXECUTION

Refer to Section 5.20 in PBS-P-100, Revised March 2003.

The preferred instrument is liquid-in-glass thermometers.  Suggested use of this type is when the temperature is being monitored by DDC Sensors.
3.2 THERMOMETER APPLICATIONS

A. Install liquid-in-glass thermometers in the following locations:

Edit or delete sixteen subparagraphs below to suit Project.

1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each boiler.

3. Inlet and outlet of each heat exchanger.

4. Inlet and outlet of each heating water generator.

5. Inlet and outlet of each side of each heat recovery unit.

6. Inlet and outlet of each thermal storage tank.

7. Inlet and outlet of each evaporator on each chiller.

8. Inlet and outlet of each condenser on each chiller.

9. Inlet and outlet of each cooling tower.

10. Inlet and outlet of each evaporative condenser.

11. Inlet and outlet of each dry cooler.

12. In each outside and return air duct on each air handling unit.

13. In each mixed air plenum on each air handling unit.

14. Inlet and outlet of each heating and cooling coil on the water side and air side.

15. In each suction and discharge of each pump.

16. Inlet and outlet of each domestic water heater.

B. Install direct-mounting, vapor-actuated dial thermometers in the following locations:

Edit or delete sixteen subparagraphs below to suit Project.
1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each boiler.

3. Inlet and outlet of each heat exchanger.

4. Inlet and outlet of each heating water generator.

5. Inlet and outlet of each side of each heat recovery unit.

6. Inlet and outlet of each thermal storage tank.

7. Inlet and outlet of each evaporator on each chiller.

8. Inlet and outlet of each condenser on each chiller.

9. Inlet and outlet of each cooling tower.

10. Inlet and outlet of each evaporative condenser.

11. Inlet and outlet of each dry cooler.

12. In each outside and return air duct on each air handling unit.

13. In each mixed air plenum on each air handling unit.

14. Inlet and outlet of each heating and cooling coil on the water side and air side.

15. In each suction and discharge of each pump.

16. Inlet and outlet of each domestic water heater.

C. Install remote-mounting, vapor-actuated dial thermometers in the following locations:

Edit or delete sixteen subparagraphs below to suit Project.
1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each boiler.

3. Inlet and outlet of each heat exchanger.

4. Inlet and outlet of each heating water generator.

5. Inlet and outlet of each side of each heat recovery unit.

6. Inlet and outlet of each thermal storage tank.

7. Inlet and outlet of each evaporator on each chiller.

8. Inlet and outlet of each condenser on each chiller.

9. Inlet and outlet of each cooling tower.

10. Inlet and outlet of each evaporative condenser.

11. Inlet and outlet of each dry cooler.

12. In each outside and return air duct on each air handling unit.

13. In each mixed air plenum on each air handling unit.

14. Inlet and outlet of each heating and cooling coil on the water side and air side.

15. In each suction and discharge of each pump.

16. Inlet and outlet of each domestic water heater.

D. Install bimetallic-actuated dial thermometers in the following locations:

Edit or delete sixteen subparagraphs below to suit Project.

1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each boiler.

3. Inlet and outlet of each heat exchanger.

4. Inlet and outlet of each heating water generator.

5. Inlet and outlet of each side of each heat recovery unit.

6. Inlet and outlet of each thermal storage tank.

7. Inlet and outlet of each evaporator on each chiller.

8. Inlet and outlet of each condenser on each chiller.

9. Inlet and outlet of each cooling tower.

10. Inlet and outlet of each evaporative condenser.

11. Inlet and outlet of each dry cooler.

12. In each outside and return air duct on each air handling unit.

13. In each mixed air plenum on each air handling unit.

14. Inlet and outlet of each heating and cooling coil on the water side and air side.

15. In each suction and discharge of each pump.

16. Inlet and outlet of each domestic water heater.

E. Provide the following temperature ranges for thermometers:

Other temperature ranges and units with both Fahrenheit and Celsius scales are available.

1. Domestic Hot Water:  [Minus 1 to plus 82 deg C, with 1-degree scale divisions (30 to 180 deg F, with 2-degree scale divisions)] [Minus 1 to plus 115 deg C, with 1-degree scale divisions (30 to 240 deg F, with 2-degree scale divisions)] <Insert other>.

2. Domestic Cold Water:  [Minus 18 to plus 38 deg C, with 1-degree scale divisions (0 to 100 deg F, with 2-degree scale divisions)] [Minus 1 to plus 55 deg C, with 1-degree scale divisions (30 to 130 deg F, with 2-degree scale divisions)] <Insert other>.

3. Heating Hot Water:  [Minus 1 to plus 115 deg C, with 1-degree scale divisions (30 to 240 deg F, with 2-degree scale divisions)] [10 to 205 deg C, with 2-degree scale divisions (50 to 400 deg F, with 5-degree scale divisions)] <Insert other>.

4. Condenser Water:  [Minus 18 to plus 71 deg C, with 1-degree scale divisions (0 to 160 deg F, with 2-degree scale divisions)] [Minus 1 to plus 115 deg C, with 1-degree scale divisions (30 to 240 deg F, with 2-degree scale divisions)] <Insert other>.

5. Chilled Water:  [Minus 18 to plus 38 deg C, with 1-degree scale divisions (0 to 100 deg F, with 2-degree scale divisions)] [Minus 18 to plus 71 deg C, with 1-degree scale divisions (0 to 160 deg F, with 2-degree scale divisions)] <Insert other>.

6. Steam and Condensate:  [Minus 1 to plus 150 deg C, with 2-degree scale divisions (30 to 300 deg F, with 5-degree scale divisions)] [10 to 205 deg C, with 3-degree scale divisions (50 to 400 deg F, with 5-degree scale divisions)] <Insert other>.

7. Air Ducts:  [Minus 40 to plus 43 deg C, with 2-degree scale divisions (Minus 40 to plus 110 deg F, with 2-degree scale divisions)] [Minus 1 to plus 115 deg C, with 1-degree scale divisions (30 to 240 deg F, with 2-degree scale divisions)] [10 to 205 deg C, with 3-degree scale divisions (50 to 400 deg F, with 5-degree scale divisions)] <Insert other>.

3.3 GAGE APPLICATIONS

A. Install dry-case type pressure gages in the following locations:

Edit or delete ten subparagraphs below to suit Project.

1. Inlet and outlet of each boiler.

2. Inlet and outlet of each heat exchanger.

3. Inlet and outlet of each heating water generator.

4. Inlet and outlet of each side of each heat recovery unit.

5. Inlet and outlet of each evaporator on each chiller.

6. Inlet and outlet of each condenser on each chiller.

7. Inlet and outlet of each evaporative condenser.

8. Inlet and outlet of each dry cooler.

9. Inlet and outlet of each heating and cooling coil on the water side.

10. In each suction and discharge of each pump.

B. Install liquid-filled-case-type pressure gages in the following locations:
Edit or delete ten subparagraphs below to suit Project.

1. Inlet and outlet of each boiler.

2. Inlet and outlet of each heat exchanger.

3. Inlet and outlet of each heating water generator.

4. Inlet and outlet of each side of each heat recovery unit.

5. Inlet and outlet of each evaporator on each chiller.

6. Inlet and outlet of each condenser on each chiller.

7. Inlet and outlet of each evaporative condenser.

8. Inlet and outlet of each dry cooler.

9. Inlet and outlet of each heating and cooling coil on the water side.

10. In each suction and discharge of each pump.
C. Install differential static pressure gages in the following locations:

1. Each set of filters in each air handling unit. 

2. At each differential pressure transmitter.

3.4 INSTALLATIONS

A. Install direct-mounting thermometers and adjust vertical and tilted positions.

B. Install remote-mounting dial thermometers on panel, with tubing connecting panel and thermometer bulb supported to prevent kinks.  Use minimum tubing length.

C. Install thermowells with socket extending [a minimum of 51 mm (2 inches) into fluid] [one-third of diameter of pipe] [to center of pipe] and in vertical position in piping tees where thermometers are indicated and where flows to coils are 0.63 L/s (10 gpm) or less.
D. Duct Thermometer Support Flanges:  Install in wall of duct where duct thermometers are indicated.  Attach to duct with screws.

E. Install direct-mounting pressure gages in piping tees with pressure gage located on pipe at most readable position.

F. Install remote-mounting pressure gages on panel.

G. Install needle-valve and snubber fitting in piping for each pressure gage for fluids (except steam).

H. Install needle-valve and syphon fitting in piping for each pressure gage for steam.

I. Install test plugs in tees in piping.

J. Install flow indicators, in accessible positions for easy viewing, in piping systems.

K. Assemble and install connections, tubing, and accessories between flow-measuring elements and flowmeters as prescribed by manufacturer's written instructions.

L. Install flowmeter elements in accessible positions in piping systems.

M. Install differential-pressure-type flowmeter elements with at least minimum straight lengths of pipe upstream and downstream from element as prescribed by manufacturer's written instructions.

N. Install wafer-orifice flowmeter elements between pipe flanges.

O. Install permanent indicators on walls or brackets in accessible and readable positions.

P. Install connection fittings for attachment to portable indicators in accessible locations.

Q. Install flowmeters at discharge of hydronic system pumps and at inlet of hydronic air coils.

R. Assemble components and install thermal-energy meters.

S. Mount meters on wall if accessible; if not, provide brackets to support meters.

3.5 CONNECTIONS

A. Install meters and gages adjacent to machines and equipment to allow service and maintenance for meters, gages, machines, and equipment.

B. Connect flowmeter-system elements to meters.

C. Connect flowmeter transmitters to meters.

D. Connect thermal-energy-meter transmitters to meters.

E. Ground equipment according to Division 16 Section "Grounding and Bonding."

F. Connect wiring according to Division 16 Section "Conductors and Cables."

3.6 ADJUSTING

A. Calibrate meters according to manufacturer's written instructions, after installation.

B. Adjust faces of meters and gages to proper angle for best visibility.

END OF SECTION 15122

PAGE  
METERS AND GAGES
15122 - 14

