Copyright 1998 AIA
GSA VERSION MASTERSPEC
6/98 (GSA 03/05)

Copyright 1998, The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15181 - HYDRONIC PIPING
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes piping, special-duty valves, and hydronic specialties for hot-water heating, chilled-water cooling, diesel and natural gas engine cooling, and condenser water systems; makeup water for these systems; blowdown drain lines; and condensate drain piping from air handling equipment
B. Related Sections include the following:

List below only those sections that specify products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 7 Section "Through-Penetration Firestop Systems" for materials and methods for sealing pipe penetrations through fire and smoke barriers.

2. Division 7 Section "Joint Sealants" for materials and methods for sealing pipe penetrations through exterior walls.

3. Division 15 Section "Basic Mechanical Materials and Methods" for general piping materials and installation requirements.

4. Division 15 Section "Hangers and Supports" for pipe supports, product descriptions, and installation requirements.  Hanger and support spacing is specified in this Section.

5. Division 15 Section "Valves" for general-duty gate, globe, ball, butterfly, and check valves.

6. Division 15 Section "Meters and Gages" for thermometers, flow meters, and pressure gages.

Retain first subparagraph below if Specification in Division 15 Section "Basic Mechanical Materials and Methods" is insufficient for this Project.

7. Division 15 Section "Mechanical Identification" for labeling and identifying hydronic piping.

8. Division 15 Section "Hydronic Pumps" for pumps, motors, and accessories for hydronic piping.

9. Division 15 Section "HVAC Instrumentation and Controls" for temperature-control valves and sensors.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. DN:  Dimension Nominal

B. DWV:  Drainage, Waste and Vent

C. NPS:  Nominal Pipe Size

1.4 SUBMITTALS

A. Product Data:  For each type of special-duty valve indicated.  Include flow and pressure drop curves based on manufacturer's testing for diverting fittings, calibrated balancing valves, and automatic flow-control valves.  For expansion tanks, air separators and purgers, flexible connectors, and expansion joints.

B. Shop Drawings:  Detail fabrication of pipe anchors, hangers, special pipe support assemblies, alignment guides, expansion joints and loops, and their attachment to the building structure.  Detail location of anchors, alignment guides, and expansion joints and loops.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding Certificates:  Copies of certificates for welding procedures and personnel.

D. Field Test Reports:  Written reports of tests specified in Part 3 of this Section.  Include the following:

1. Test procedures used.

2. Test results that comply with requirements.

3. Failed test results and corrective action taken to achieve requirements.

E. Maintenance Data:  For hydronic specialties and special-duty valves to include in maintenance manuals specified in Division 1.

Delete below if chemical treatment is specified in Division 15 Section "HVAC Water Treatment."

F. Water Analysis:  Submit a copy of the water analysis to illustrate water quality available at Project site.

1.5 QUALITY ASSURANCE

Delete paragraph below if no welding is required on this project.  Retain "Welding Certificates" Paragraph in "Submittals" Article if below is retained.

A. Welding:  Qualify processes and operators according to the ASME Boiler and Pressure Vessel Code:  Section IX, "Welding and Brazing Qualifications."

B. ASME Compliance:  Comply with ASME B31.9, "Building Services Piping," for materials, products, and installation.  Safety valves and pressure vessels shall bear the appropriate ASME label.  Fabricate and stamp air separators and expansion tanks to comply with the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

1.6 COORDINATION

Edit paragraphs below to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of hydronic piping and piping support system components with other construction, including light fixtures, HVAC equipment, fire-suppression-system components, and partition assemblies.

B. Coordinate piping installation with roof curbs, equipment supports, and roof penetrations.  Roof specialties are specified in Division 7 Sections.

C. Coordinate pipe fitting pressure classes with products specified in related Sections.

D. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into base.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Sections.

E. Coordinate installation of pipe sleeves for penetrations through foundation walls, exterior walls and floor assemblies.  Coordinate with requirements for firestopping specified in Division 7 Section "Through-Penetration Firestop Systems" for fire and smoke wall and floor assemblies.

1.7 EXTRA MATERIALS

Delete paragraph below for complex projects requiring several types of chemical-treatment systems that are specified in Division 15 Section "HVAC Water Treatment."

Revise below to suit Project.

A. Water Treatment Chemicals:  Furnish sufficient chemicals for initial system startup and for preventive maintenance for one year from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:  

1. Integrated Reinforced Branch Welding Fittings:

a. Bonney Forge.

b. <Insert manufacturer’s name>.
2. Grooved Mechanical-Joint Fittings and Couplings:

a. Central Sprinkler Company; Central Grooved Piping Products.

b. Grinnell Corporation.

c. Victaulic Company of America.

3. Calibrated Balancing Valves:

a. Armstrong Pumps, Inc.

b. Flow Design, Inc.

c. Gerand Engineering Company.

d. Griswold Controls.

e. ITT Bell & Gossett; ITT Fluid Technology Corp.

f. Taco, Inc.

4. Pressure-Reducing Valves:

a. Amtrol, Inc.

b. Armstrong Pumps, Inc.

c. Conbraco Industries, Inc.

d. ITT Bell & Gossett; ITT Fluid Technology Corp.

e. Spence Engineering Company, Inc.

f. Watts Industries, Inc.; Watts Regulators.

5. Safety Valves:

a. Amtrol, Inc.

b. Armstrong Pumps, Inc.

c. Conbraco Industries, Inc.

d. ITT McDonnell & Miller Div.; ITT Fluid Technology Corp.

e. Kunkle Valve Division.

f. Spence Engineering Company, Inc.

6. Automatic Flow-Control Valves:

a. Flow Design, Inc.

b. Griswold Controls.

7. Expansion Tanks:

a. Amtrol, Inc.

b. Armstrong Pumps, Inc.

c. ITT Bell & Gossett; ITT Fluid Technology Corp.

d. Taco, Inc.

8. Air Separators and Air Purgers:

a. Amtrol, Inc.

b. Armstrong Pumps, Inc.

c. ITT Bell & Gossett; ITT Fluid Technology Corp.

d. Taco, Inc.

2.2 PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for discussion on this Section's organization and on the most efficient way to edit this Section.

A. General:  Refer to Part 3 "Piping Applications" Article for applications of pipe and fitting materials. 

Coordinate three articles below with "Piping Applications" Article in Part 3.  Delete materials not used.  The articles include examples of materials listed in the 1996 ASHRAE HANDBOOK--"HVAC Systems and Equipment," Chapter 40, "Pipes, Tubes, and Fittings."

2.3 COPPER TUBE AND FITTINGS

Types M and C in paragraph below have the thinnest wall thicknesses and are not included in the 1996 ASHRAE HANDBOOK--"HVAC Systems and Equipment."

Type K (Type A) drawn-temper is used for underground installations when the laying lengths exceed available coil lengths and joints are required below grade.  Also Type U(Type A) is used when extra well thickness is necessary for corrosion or pressure considerations.

A. Drawn-Temper Copper Tubing:  ASTM B 88M, Type B (ASTM B 88, Type L), ASTM B 88M Type C (ASTM B 88, Type M) ASTM B 88M, Type A (ASTM B 88, Type K).
Type K (Type A) soft temper is used for underground installations.  If deleted here, also edit Part 3.

B. Annealed-Temper Copper Tubing:  ASTM B 88M, Type A (ASTM B 88, Type K).

Type DWV tubing in paragraph below is available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200) and may be used for condensate drains.  NPS 2-1/2 and NPS 3-1/2 (DN 65 and DN 90) are not available.  Wall thicknesses are thinner than ASTM B 88, Type M (ASTM B 88M, Type C).  DWV tubing is intended for nonpressure applications.

C. DWV Copper Tubing:  ASTM B 306, Type DWV.

D. Wrought-Copper Fittings:  ASME B16.22.

E. Wrought-Copper Unions:  ASME B16.22.

See Evaluations for discussions on solder and brazing materials.

F. Solder Filler Metals:  ASTM B 32, 95-5 tin antimony.

G. Brazing Filler Metals:  AWS A5.8, Classification BAg-1 (silver).

2.4 STEEL PIPE AND FITTINGS

Minimum steel pipe size recommended for hydronic piping is NPS 3/4 (DN 20).

Type E is available in as small a size as NPS ⅛ (DN 3) and as is preferable to Type F which needs tends to have a rougher interior.

Steel Pipe, DN 50 (NPS 2) and Smaller:  ASTM A 53, Type S (seamless) or Type F (furnace-butt welded), Grade B, Schedule 40, black steel, plain ends.

A. Steel Pipe, DN 65 through DN 300 (NPS 2-1/2 through NPS 12):  ASTM A 53, Type E (electric-resistance welded), Grade B, Schedule 40, black steel, plain ends.

B. Steel Pipe, DN 350 through DN 450 (NPS 14 through NPS 18):  ASTM A 53, Type E (electric-resistance welded) or Type S (seamless), Grade B, Schedule 30, black steel, plain ends.

C. Steel Pipe, DN 500 (NPS 20):  ASTM A 53, Type E (electric-resistance welded) or Type S (seamless), Grade B, Schedule 20, black steel, plain ends.

D. Steel Pipe Nipples:  ASTM A 733, made of ASTM A 53, Schedule 40, black steel; seamless for DN 50 (NPS 2) and smaller and electric-resistance welded for DN 65 (NPS 2-1/2) and larger.

Coordinate flange class with products in other parts of this Section and in related Sections to correlate face size and bolt patterns.

Cast iron threaded fittings tends to be brittle.  Use cast iron only in systems that have low pressure and/or thermal stresses.
E. Cast-Iron Threaded Fittings:  ASME B16.4; Classes 125 and 250.

F. Malleable-Iron Threaded Fittings:  ASME B16.3, Classes 150 and 300.

G. Malleable-Iron Unions:  ASME B16.39; Classes 150, 250, and 300.

H. Cast-Iron Pipe Flanges and Flanged Fittings:  ASME B16.1, Classes 25, 125, and 250; raised ground face, and bolt holes spot faced.

I. Wrought-Steel Fittings:  ASTM A 234/A 234M, wall thickness to match adjoining pipe.

Flanges and fittings below are available in several classes, materials, facings, and end connections.  Coordinate with Project requirements.

J. Wrought Cast- and Forged-Steel Flanges and Flanged Fittings:  ASME B16.5, including bolts, nuts, and gaskets of the following material group, end connections, and facings:

K. Integrally Reinforced Branch Welding Fittings:  These fittings commonly referred to as weld-o-lets, thread-o-lets and half-couplings shall conform to the same material specifications are the pipe to which they are welded.  They shall also conform to MSS-SP-97 and either ASME B31.1, ASME B31.3 and/or ASME B31.9.  These fittings shall only be used when the branch connection is two nominal pipe sizes smaller than the main.

1. Material Group:  1.1.

2. End Connections:  Butt welding.

3. Facings:  Raised face.

Delete type F if smooth interior is required.

L. Grooved Mechanical-Joint Fittings:  ASTM A 536, Grade 65-45-12 ductile iron; ASTM A 47M (ASTM A 47), Grade 32510 malleable iron; ASTM A 53, Type F, E or S, Grade B fabricated steel; or ASTM A 106, Grade B steel fittings with grooves or shoulders designed to accept grooved end couplings.

M. Grooved Mechanical-Joint Couplings:  Ductile- or malleable-iron housing and synthetic rubber gasket of central cavity pressure-responsive design; with nuts, bolts, locking pin, locking toggle, or lugs to secure grooved pipe and fittings.

N. Welding Materials:  Comply with Section II, Part C, of the ASME Boiler and Pressure Vessel Code for welding materials appropriate for wall thickness and for chemical analysis of pipe being welded.

O. Gasket Material:  Thickness, material, and type suitable for fluid to be handled; and design temperatures and pressures.

Edit paragraph below to suit project.

P. acceptable Nominal Pipe Sizes:  Nominal pipe sizes are restricted to those below: DN 15 (NPS ½) is the smallest size allowable.    

DN 15 (NPS ½)


DN 65 (NPS 2-½)

DN 350 (NPS 14)
DN 25 (NPS 1)


DN 80 (NPS 3)


DN 400 (NPS 16)
DN 32 (NPS 1¼)


DN 100 (NPS 4)

DN 450 (NPS 18)
DN 40 (NPS 1½)


DN125 (NPS 5)


DN 500 (NPS 20)
DN 50 (NPS 2)


DN150 (NPS 6)


DN 600 (NPS 24)






DN 200 (NPS 8)

DN 750 (NPS 30)






DN 250 (NPS 10)

DN 900 (NPS 36)






DN 300 (NPS 12)

DN1200 (NPS 48) 
2.5 PLASTIC PIPE AND FITTINGS

A. PVC Plastic Pipe:  ASTM D 1785, Schedules 40 and 80, bell and spigot end.
B. PVC Plastic Pipe Fittings:  Spigot type pipe fittings, ASTM D 2466 for Schedule 40 pipe; ASTM D 2467 for Schedule 80 pipe.

2.6 VALVES

A. Gate, globe, check, ball, and butterfly valves are specified in Division 15 Section "Valves."

B. Refer to Part 3 "Valve Applications" Article for applications of each valve.

C. Calibrated Balancing Valves, DN 50 (NPS 2) and Smaller:  Bronze body, ball type, 860-kPa (125-psig) working pressure, 121 deg C (250 deg F) maximum operating temperature, and having threaded ends.  Valves shall have calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, and be equipped with a memory stop to retain set position.

D. Calibrated Balancing Valves, DN 65 (NPS 2-1/2) and Larger:  Cast-iron or steel body, ball type, 860-kPa (125-psig) working pressure, 121 deg C (250 deg F) maximum operating temperature, and having flanged or grooved connections.  Valves shall have calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, and be equipped with a memory stop to retain set position.

E. Pressure-Reducing Valves:  Diaphragm-operated, bronze or brass body with low inlet pressure check valve, inlet strainer removable without system shutdown, and noncorrosive corrosion resistant valve seat and stem.  Select valve size, capacity, and operating pressure to suit system.  Valve shall be factory set at operating pressure and have capability for field adjustment.

F. Safety Valves:  Diaphragm-operated, bronze or brass body with brass and rubber, wetted, internal working parts; shall suit system pressure and heat capacity and shall comply with the ASME Boiler and Pressure Vessel Code, Section IV.

Strainers should be installed upstream of these valves, as with any control valve.  This type valve will become clogged if one appropriate strainer is not installed.  Consider inconvenience of installing new internals if flow valves change.

G. Automatic Flow-Control Valves:  Gray-iron body, factory set to maintain constant flow with plus or minus 5 percent over system pressure fluctuations, and equipped with a readout kit including flow meter, probes, hoses, flow charts, and carrying case.  Each valve shall have an identification tag attached by chain, and be factory marked with the zone identification, valve number, and flow rate.  Valve shall be line size and one of the following designs:

1. Gray-iron or brass body, designed for 1206 kPa (175 psig) at 93 deg C (200 deg F) with stainless-steel piston and spring.

2. Brass or ferrous-metal body, designed for 2068 kPa (300 psig) at 121 deg C (250 deg F) with corrosion-resistant, tamperproof, self-cleaning, piston-spring assembly easily removable for inspection or replacement.

3. Combination assemblies, including bronze ball valve and brass alloy control valve, with stainless-steel piston and spring, fitted with pressure and temperature test valves, and designed for 2067 kPa (300 psig) at 121 deg C (250 deg F).

2.7 HYDRONIC SPECIALTIES

Automatic air vents may cause damage to ceilings and other finished surfaces.  Air vents aid in system filling.  Air removal after initial startup is accomplished by air separator or boiler dip-tube.  Manual air vents may be a better solution.

A. Manual Air Vent:  Bronze body and nonferrous internal parts; 1035-kPa (150-psig) working pressure; 107 deg C (225 deg F) operating temperature; manually operated with screwdriver or thumbscrew; with DN 6 (NPS 1/8) discharge connection and DN 15 (NPS 1/2) inlet connection.

B. Automatic Air Vent:  Designed to vent automatically with float principle; bronze body and nonferrous internal parts; 1035-kPa (150-psig) working pressure; 116 deg C (240 deg F) operating temperature; with DN 8 (NPS 1/4) discharge connection and DN 15 (NPS 1/2) inlet connection.

Select one of two paragraphs and associated subparagraphs below according to system capacity and space availability.  Bladder-type tanks and diaphragm-type tanks can be mounted anywhere on the floor.

C. Expansion Tanks:  Welded carbon steel, rated for 860-kPa (125-psig) working pressure and 191 deg C (375 deg F) minimum operating temperature, with taps in bottom of tank for tank fitting and taps in end of tank for gage glass.  Tanks shall be factory tested with taps fabricated and labeled according to the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.  Include the following fittings and accessories:

1. Air-Control Tank Fitting:  Cast-iron body, copper-plated tube, brass vent tube plug, and stainless-steel ball check, 379-L (100-gal.) unit only; sized for compression-tank diameter.  Design tank fittings for 860-kPa (125-psig) working pressure and 121 deg C (250 deg F) minimum operating temperature.

2. Tank Drain Fitting:  Brass body, nonferrous internal parts; 860-kPa (125-psig) working pressure and 116 deg C (240 deg F) maximum minimum operating temperature; designed to admit air to compression tank, drain water, and close off system.

3. Gage Glass:  Full height with dual manual shutoff valves, 20-mm- (3/4-inch-) diameter gage glass, and slotted-metal glass guard.

D. Expansion Tanks:  Welded carbon steel, rated for 860-kPa (125-psig) working pressure and 191 deg C (375 deg F) minimum operating temperature.  Separate air charge from system water to maintain design expansion capacity by a flexible [diaphragm] [bladder] securely sealed into tank.  Include drain fitting and taps for pressure gage and air-charging fitting.  Support vertical tanks with steel legs or base; support horizontal tanks with steel saddles.  Factory fabricate and test tank with taps and supports installed and labeled according to the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Select one of three paragraphs below according to system capacity.

Insure that proper selection of air separators, purgers has been documented.  Selecting line separators may not provide desired performance.  Generally tangential air separators require a minimum of 7 kPa or (1 psig) to function correctly.
E. Tangential-Type Air Separators:  Welded black steel; ASME constructed and labeled for 860-kPa (125-psig) minimum working pressure and 191 deg C (375 deg F) minimum operating temperature; perforated stainless-steel air collector tube designed to direct released air into expansion tank; tangential inlet and outlet connections; threaded connections for DN 50 (NPS 2) and smaller; flanged connections for DN 65 (NPS 2-1/2) and larger; threaded blowdown connection.  Provide units in sizes for full-system flow capacity.

F. In-Line Air Separators:  One-piece cast iron with an integral weir designed to decelerate system flow to maximize air separation at a working pressure up to 1206 kPa (175 psig) and liquid temperature up to 149 deg C (300 deg F).

G. Air Purgers:  Cast-iron body with internal baffles that slow the water velocity to separate the air from solution and divert it to the vent for quick removal.  Maximum working pressure of 1035 kPa (150 psig) and temperature of 121 deg C (250 deg F).

Delete paragraph below for complex projects requiring several types of chemical-treatment systems that are specified in Division 15 Section "HVAC Water Treatment."

H. Bypass Chemical Feeder:  Welded steel construction; 860-kPa (125-psig) working pressure; 19‑L (5-gal.) capacity; with fill funnel and inlet, outlet, and drain valves.

1. Chemicals:  Specially formulated, based on analysis of makeup water, to prevent accumulation of scale and corrosion in piping and connected equipment.

Fitting in paragraph below is used where a single pipe acts as both supply and return, such as a branch supply line at a convector or finned-tube radiation.  These fittings are available in NPS 3/4 to NPS 2 (DN 20 to DN 50).

I. Diverting Fittings:  860-kPa (125-psig) working pressure; 121 deg C (250 deg F) maximum operating temperature; cast-iron body with threaded ends, or wrought copper with soldered ends.  Indicate flow direction on fitting.

For each type strainer select from the following lists, the materials, perforations and options required for this project.  Note that all materials, perforations and options on all combinations may not be available or may not be available for all sizes and configurations.

J. Y-Pattern Strainers:  860-kPa (125-psig) working pressure; cast-iron body (ASTM A 126, Class B), flanged ends for DN 65 (NPS 2-1/2) and larger, threaded connections for DN 50 (NPS 2) and smaller, bolted cover, perforated stainless-steel basket, and bottom drain connection.

1. Baskets: [ Carbon steel ][ Stainless steel, Type[ 304][ 316]][ Brass][ Monel alloy][ Wedge wire]
2. Perforations:  [3-mm (0.125)] [3-mm (0.125)] [3-mm (0.125)][20 mesh] [40 mesh] [60 mesh] <Insert number here>
3. Service Bonnets: [with lifting lugs] [ mechanical davits] [ hydraulic davits][ quick opening closures].

4. Accessories:

a. Drain connection.

b. Vent connection.

c. Magnetic plugs or inserts.

d. Differential gauge[ and switch].

On large systems or on critical systems, dual basket strainers may be required.  Paragraphs below to specify dual strainers if required.

K. Basket Strainers:  860-kPa (125-psig) working pressure; high-tensile cast-iron body (ASTM A 126, Class B), flanged-end connections, bolted cover, perforated stainless-steel basket, and bottom drain connection.

1. Baskets: [ Carbon steel ][ Stainless steel, Type[ 304][ 316]][ Brass] [ Monel alloy] [ Wedge wire]
2. Perforations:  [3-mm (0.125)] [3-mm (0.125)] [3-mm (0.125)][20 mesh] [40 mesh] [60 mesh] <Insert number here>
3. Service Bonnets: [with lifting lugs] [ mechanical davits] [ hydraulic davits][ quick opening closures].

4. Configuration: [Duplex][ Simplex].

5. Accessories:

a. Drain connection.

b. Vent connection.

c. Magnetic plugs or inserts.

d. Differential gauge[ and switch].

L. T-Pattern Strainers:  5170-kPa (750-psig) working pressure; ductile-iron or malleable-iron body, grooved-end connections, stainless-steel basket with 57 percent free area; removable access coupling and end cap for strainer maintenance.

1. Baskets: [ Carbon steel ][ Stainless steel, Type[ 304][ 316]][ Brass] [ Monel alloy] [ Wedge wire]
2. Perforations:  [3-mm (0.125)] [3-mm (0.125)] [3-mm (0.125)][20 mesh] [40 mesh] [60 mesh] <Insert number here>
3. Service Bonnets: [with lifting lugs][ mechanical davits][ hydraulic davits][ quick opening closures].

4. Configuration: [Duplex][ Simplex].

5. Accessories:

a. Drain connection.

b. Vent connection.

c. Magnetic plugs or inserts.

d. Differential gauge[ and switch].

Retain first paragraph below for small pipe sizes.  Allow sufficient length for installation.  Where space is limited and for larger piping applications, consider using flexible joints and spherical connectors.

Combinations of grooved mechanical-joint couplings and short nipples may also be used.  Refer to Victaulic Company of America's technical information.

M. Flexible Connectors:  Stainless-steel bellows with woven, flexible, bronze, wire-reinforcing protective jacket; 1035-kPa (150-psig) minimum working pressure and 121 deg C (250 deg F) minimum operating temperature.  Connectors shall have flanged- or threaded-end connections to match equipment connected and shall be capable of 20-mm (3/4-inch) misalignment.

N. Spherical, Rubber, Flexible Connectors:  Fiber-reinforced rubber body with steel flanges drilled to align with Classes 150 and 300 steel flanges; minimum operating temperatures up to 121 deg C (250 deg F) and pressures up to 1035 kPa (150 psig).

Specify slip type expansion joints only when space does not permit use of loops or bellows type.  Also, insure that the system will typically cycle, i.e., heat and cool regularly to keep slip joint operational.

O. Packed, Slip, Expansion Joints:  1035-kPa (150-psig) minimum working pressure, steel pipe fitting consisting of telescoping body and slip-pipe sections, packing ring, packing, limit rods, flanged ends, and chrome-plated finish on slip-pipe telescoping section.

PART 3 -  EXECUTION

3.1 PIPING APPLICATIONS

Coordinate applications below with materials specified in Part 2 of this Section.  Pipe sizes at which joining methods change are between NPS 2 and NPS 2-1/2 (DN 50 and DN 65).  Adjust this change point to suit personal preference.

Materials and joining methods for applications below are as listed in the 1996 ASHRAE HANDBOOK-- "HVAC Systems and Equipment," Chapter 42, "Pipes, Tubes, and Fittings."  See Editing Instruction No. 2 in the Evaluations for discussion on selecting piping materials.

Soldered joints for pipes larger than NPS 2 (DN 50) may not meet system pressures.

A. Hot and Chilled Water, DN 50 (NPS 2) and Smaller:  Aboveground, use Type B (Type L) drawn-temper copper tubing with soldered joints or Schedule  [40] [30] [20] steel pipe with threaded joints.  Belowground or within slabs, use Type A (Type K) annealed-temper copper tubing with brazed joints.  Use the fewest possible joints belowground and within floor slabs.

B. Hot and Chilled Water, DN 65 (NPS 2-1/2) and Larger:  Aboveground Schedule  [40] [30] [20] steel pipe with [welded and flanged joints] [or] [grooved mechanical-joint couplings].

Retain paragraph below when project is limited to NPS 2 (DN 50) and smaller to allow copper tubing.

C. Condenser Water, DN 50 (NPS 2) and Smaller:  Aboveground, use Type B (Type L) drawn-temper copper tubing with soldered joints or Schedule  [40] [30] [20] steel pipe with threaded joints.  Belowground or within slabs, use Type A (Type K) annealed-temper copper tubing with brazed joints.

Select from four options in paragraph below for all sizes of plastic pipe and for aboveground and belowground.  Use Schedule 80 for higher pressures.  Use CPVC for higher temperatures.  See Evaluations.

Use of plastic pipe is recommended only for belowground use.

D. Condenser Water, Belowground:  Schedule  [40] [80], [PVC] pipe with bell and spigot, push-on gasketed joints.

Retain first paragraph below for mechanical-joint steel pipe, all sizes.

E. Condenser Water DN 65 (NPS 2-1/2) and larger, Aboveground:  Schedule  [40] [30] [20] steel pipe with [welded and flanged joints] [or] [grooved mechanical-joint couplings].

F. Diesel Engine Cooling Water:  For DN 50 (NPS 2) and smaller, use Schedule  [40] [30] [20] steel pipe with threaded joints; for DN 65 (NPS 2-1/2) and larger, use Schedule  [40] [30] [20] steel pipe with welded joints.

G. Dry Cooler Piping:  For DN 50 (NPS 2) and smaller, use Schedule  [40] [30] [20] steel pipe with threaded joints; for DN 65 (NPS 2-1/2) and larger, use Schedule  [40] [30] [20] steel pipe with welded joints.

H. Condensate Drain Lines:  Type B (Type L) drawn-temper copper tubing with soldered joints.
I. Make-up Water Lines:  Type B (Type L) drawn-temper copper tubing with soldered joints or Schedule 40, PVC pipe with solvent-welded joints.

3.2 VALVE APPLICATIONS

A. General-Duty Valve Applications:  Unless otherwise indicated, use the following valve types:

1. Shutoff Duty:  Gate, ball, and butterfly valves.

2. Throttling Duty:  Globe, ball, and butterfly valves.

B. Install shutoff duty valves at each branch connection to supply mains, at supply connection to each piece of equipment, unless only one piece of equipment is connected in the branch line.  Install throttling duty valves at each branch connection to return mains, at return connections to each piece of equipment, and elsewhere as indicated.

C. Install calibrated balancing valves in the return water line of each heating or cooling element and elsewhere as required to facilitate system balancing.

D. Install check valves at each pump discharge and elsewhere as required to control flow direction.

E. Install safety valves on hot-water generators, refrigerant evaporators and condensers, and elsewhere as required by the ASME Boiler and Pressure Vessel Code.  Install safety-valve discharge piping, without valves, to floor drain.  Comply with the ASME Boiler and Pressure Vessel Code, Section VIII, Division 1, for installation requirements.

F. Install pressure-reducing valves on hydronic system make up water piping and elsewhere as required to regulate system pressure.

3.3 PIPING INSTALLATIONS

A. Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic piping installation requirements.

B. Install groups of pipes parallel to each other, spaced to permit welding, applying insulation and servicing of valves.

C. Install drains, consisting of a tee fitting, DN 20 (NPS 3/4) ball valve, and short DN 20 (NPS 3/4) threaded nipple with cap, at low points in piping system mains and elsewhere as required for system drainage.

D. Install piping at a uniform grade of 0.2 percent upward in direction of flow.

E. Reduce pipe sizes using eccentric reducer fitting installed with level side up.

F. Unless otherwise indicated, install branch connections to mains using tee fittings in main pipe, with the takeoff coming out the bottom of the main pipe.  For up-feed risers, install the takeoff coming out the top of the main pipe.

G. When branch lines are two nominal pipe sizes smaller than the main, integrally reinforced branch welding fitting may be used.  Follow the manufacturers written instructions regarding welding procedures, weld passes and cutting holes in the main to form the branch.

H. Field mitering of pipe to form elbows, tees or any other pipe fitting is not acceptable.

I. Install strainers on supply side of each control valve, pressure-reducing valve, solenoid valve, in-line pump, and elsewhere as indicated.  Install DN 20 (NPS 3/4) nipple and ball valve in blowdown connection of strainers DN 50 (NPS 2) and larger.  Match size of strainer blowoff connection for strainers smaller than DN 50 (NPS 2).

J. Anchor piping for proper direction of expansion and contraction.

3.4 BRANCH LINES

A. All branches from mains shall be made with factory fittings. Mitering of pipe will not be permitted.

B. All branches in steel pipe shall be made with tees.  When the branch line is two nominal pipe sizes smaller, branch line connections may be made utilizing welded branch line fitting such as weld-o-lets or thread-o-lets or an approved substitution.

C. All branches in copper lines shall be made with tees, except when the branch line is two nominal pipe sizes smaller; then the branch connection may be made using Tee-drill or an approved substitution.

Delete this paragraph in its entirety when the Section “Hangers and Supports” is included in the specifications.

3.5 HANGERS AND SUPPORTS

Piping support must account for expansion and contraction, vibration, and dead load of piping and its contents, and seismic bracing requirements.  Insure that proper building and piping attachment devices are specified, when this paragraph is retained.
A. Install the following pipe attachments:

1. Adjustable steel clevis hangers for individual horizontal piping less than 6 m (20 feet) long.

2. Adjustable roller hangers and spring hangers for individual horizontal piping 6 m (20 feet) or longer.

3. Pipe Roller:  MSS SP-58, Type 44 for multiple horizontal piping 6 m (20 feet) or longer, supported on a trapeze.

4. Spring hangers to support vertical runs.

5. On plastic pipe, install pads or cushions on bearing surfaces to prevent hanger from scratching pipe.

Verify actual supported loads for hanger sizes and spacing.  Consult structural engineer.  Spacing and sizes below are from the 1996 ASHRAE HANDBOOK--"HVAC Systems and Equipment."

B. Install hangers for steel piping with the following maximum spacing and minimum rod sizes:

1. DN 20 (NPS 3/4):  Maximum span, 2.1 m (7 feet); minimum rod size, 6.4 mm (1/4 inch).

2. DN 25 (NPS 1):  Maximum span, 2.1 m (7 feet); minimum rod size, 6.4 mm (1/4 inch).

3. DN 40 (NPS 1-1/2):  Maximum span, 2.7 m (9 feet); minimum rod size, 10 mm (3/8 inch).

4. DN 50 (NPS 2):  Maximum span, 3 m (10 feet); minimum rod size, 10 mm (3/8 inch).

5. DN 65 (NPS 2-1/2):  Maximum span, 3.4 m (11 feet); minimum rod size, 10 mm (3/8 inch).

6. DN 80 (NPS 3):  Maximum span, 3.7 m (12 feet); minimum rod size, 10 mm (3/8 inch).

7. DN 100 (NPS 4):  Maximum span, 4.3 m (14 feet); minimum rod size, 13 mm (1/2 inch).

8. DN 150 (NPS 6):  Maximum span, 5.2 m (17 feet); minimum rod size, 13 mm (1/2 inch).

9. DN 200 (NPS 8):  Maximum span, 5.8 m (19 feet); minimum rod size, 16 mm (5/8 inch).

10. DN 250 (NPS 10):  Maximum span, 6.1 m (20 feet); minimum rod size, 19 mm (3/4 inch).

11. DN 300 (NPS 12):  Maximum span, 7 m (23 feet); minimum rod size, 22 mm (7/8 inch).

12. DN 350 (NPS 14):  Maximum span, 7.6 m (25 feet); minimum rod size, 25 mm (1 inch).

13. DN 400 (NPS 16):  Maximum span, 8.2 m (27 feet); minimum rod size, 25 mm (1 inch).

14. DN 450 (NPS 18):  Maximum span, 8.5 m (28 feet); minimum rod size, 32 mm (1-1/4 inches).

15. DN 500 (NPS 20):  Maximum span, 9.1 m (30 feet); minimum rod size, 32 mm (1-1/4 inches).

C. Install hangers for drawn-temper copper piping with the following maximum spacing and minimum rod sizes:

1. DN 20 (NPS 3/4):  Maximum span, 1.5 m (5 feet); minimum rod size, 6.4 mm (1/4 inch).

2. DN 25 (NPS 1):  Maximum span, 1.8 m (6 feet); minimum rod size, 6.4 mm (1/4 inch).

3. DN 40 (NPS 1-1/2):  Maximum span, 2.4 m (8 feet); minimum rod size, 10 mm (3/8 inch).

4. DN 50 (NPS 2):  Maximum span, 2.4 m (8 feet); minimum rod size, 10 mm (3/8 inch).

5. DN 65 (NPS 2-1/2):  Maximum span, 2.7 m (9 feet); minimum rod size, 10 mm (3/8 inch).

6. DN 80 (NPS 3):  Maximum span, 3 m (10 feet); minimum rod size, 10 mm (3/8 inch).

D. Plastic Piping Hanger Spacing:  Space hangers according to pipe manufacturer's written instructions for service conditions.  Avoid point loading.  Space and install hangers with the fewest practical rigid anchor points.

E. Support vertical runs at roof, at each floor, and at 3-m (10-foot) intervals between floors.

3.6 PIPE JOINT CONSTRUCTION

A. Refer to Division 15 Section "Basic Mechanical Materials and Methods" for joint construction requirements for soldered and brazed joints in copper tubing; threaded, welded, and flanged joints in steel piping; and push-on joints for PVC piping.

3.7 HYDRONIC SPECIALTIES INSTALLATION

A. Install manual air vents at high points in piping, at heat-transfer coils, and elsewhere as required for system air venting.

Automatic air vents may cause damage to ceilings and other finished surfaces.  Air vents aid in system filling.  Air removal after initial startup is accomplished by air separator or boiler dip-tube.  Manual air vents may be a better solution.

B. Install automatic air vents in mechanical equipment rooms only at high points of system piping, at heat-transfer coils, and elsewhere as required for system air venting.

Select one of three paragraphs below according to air separator specified in Part 2.

C. Install dip-tube fittings in boiler outlet.  Install piping to expansion tank with a 2 percent upward slope toward tank.  Connect boiler-outlet piping.

D. Install in-line air separators in pump suction lines.  Install piping to compression tank with a 2 percent upward slope toward tank.  Install drain valve on units DN 50 (NPS 2) and larger.

E. Install combination air separator and strainer in pump suction lines.  Install piping to compression tank with a 2 percent upward slope toward tank.  Install blowdown piping with gate valve; extend to nearest drain.

Delete paragraph below if Division 15 Section "HVAC Water Treatment" is used.  Coordinate location of an equipment drain near feeder locations.

F. Install bypass chemical feeders in each hydronic system where indicated, in upright position with top of funnel not more than 1200 mm (48 inches) above floor.  Install feeder in bypass line, off main, using globe valves on each side of feeder and in the main between bypass connections.  Pipe drain, with ball valve, to nearest equipment drain.

Select one of two paragraphs and associated subparagraph below.

G. Install expansion tanks above air separator.  Install gage glass and cocks on end of tank.  Install tank fitting in tank bottom and charge tank.  Use manual vent for initial fill to establish proper water level in tank.

1. Support tank from floor or structure above with sufficient strength to carry weight of tank, piping connections, and fittings, plus weight of a full tank of water.  Do not overload building components and structural members.

H. Install expansion tanks on floor.  Vent and purge air from hydronic system, and ensure tank is properly charged with air to suit system design requirements.

3.8 TERMINAL EQUIPMENT CONNECTIONS

A. Size for supply and return piping connections shall be, at a minimum, the same size as the equipment connections, install the runouts the size indicated on the plans.
B. Install control valves in accessible locations close to connected equipment.  Install control valves in hot lines at a 30 degree angle minimum. Support the actuator when valves are not installed with the actuator in a vertical position.
C. Install bypass piping with globe valve around control valve.  If multiple, parallel control valves are installed, only one bypass is required.

D. Install ports for pressure and temperature gages at coil inlet connections.

3.9 CHEMICAL TREATMENT

Delete this Article if Division 15 Section "HVAC Water Treatment" is used.

Delete first paragraph and subparagraphs below if water analysis has been or will be conducted by Owner.

A. Perform an analysis of supply water to determine the type and quantities of chemical treatment needed to keep system free of scale, corrosion, and fouling, and to sustain the following water characteristics:

1. Closed hydronic systems, including [hot-water heating] [chilled water] [dual-temperature water] [and] [glycol cooling], shall have the following water qualities:

a. Hardness:  0.00

b. Iron content: 0.00

c. Dissolved solids: 1500 to 1750 ppm

d. Silica: 610 ppm or less

e. pH:  Maintain a value 10.5 or higher.

Retain first subparagraph below for systems that do not contain glycol.

f. Chemical Oxygen Demand:  Maintain a maximum value of [100] <Insert number> ppm.

g. Microbiological Limits:

1) Total Aerobic Plate Count:  Maintain a maximum value of [1000] <Insert number> organisms/ml.

2) Total Anaerobic Plate Count:  Maintain a maximum value of [100] <Insert number> organisms/ml.

3) Nitrate Reducers:  Maintain a maximum value of [100] <Insert number> organisms/ml.

4) Sulfate Reducers:  Maintain a maximum value of [0] <Insert number> organisms/ml.

5) Iron Bacteria:  Maintain a maximum value of [0] <Insert number> organisms/ml.

h. <Insert other requirements if necessary.>

B. Open hydronic systems, including [condenser] [fluid-cooler spray] water, shall have the following water qualities:

1. pH:  Maintain a value within [8.0 to 9.1] <Insert range>.

2. "P" Alkalinity:  Maintain a maximum value of [100] <Insert number> ppm.

3. Chemical Oxygen Demand:  Maintain a maximum value of [100] <Insert number> ppm.

4. Soluble Copper:  Maintain a maximum value of [0.20] <Insert number> ppm.

5. TDS:  Maintain a maximum value of [10] <Insert number> ppm.

6. Ammonia:  Maintain a maximum value of [20] <Insert number> ppm.

7. Free "OH" Alkalinity:  Maintain a maximum value of [0] <Insert number> ppm

8. Microbiological Limits:

a. Total Aerobic Plate Count:  Maintain a maximum value of [10,000] <Insert number> organisms/ml.

b. Total Anaerobic Plate Count:  Maintain a maximum value of [1000] <Insert number> organisms/ml.

c. Nitrate Reducers:  Maintain a maximum value of [100] <Insert number> organisms/ml.

d. Sulfate Reducers:  Maintain a maximum value of [0] <Insert number> organisms/ml.

e. Iron Bacteria:  Maintain a maximum value of [0] <Insert number> organisms/ml.

9. Polymer Testable:  Maintain a minimum value within [10 to 40] <Insert range>.

10. <Insert other requirements if necessary.>

C. Fill system and perform initial chemical treatment.

3.10 FIELD QUALITY CONTROL

A. Prepare hydronic piping according to ASME B31.9 and as follows:

1. Leave joints, including welds, uninsulated and exposed for examination during test.

2. Provide temporary restraints for expansion joints that cannot sustain reactions due to test pressure.  If temporary restraints are impractical, isolate expansion joints from testing.

3. Flush system with clean water.  Clean strainers.

4. Isolate equipment from piping.  If a valve is used to isolate equipment, its closure shall be capable of sealing against test pressure without damage to valve.  Install blinds in flanged joints to isolate equipment.

5. Install safety valve, set at a pressure no more than one-third higher than test pressure, to protect against damage by expanding liquid or other source of overpressure during test.

Procedures below are paraphrased from ASME B31.9.

B. Perform the following tests on hydronic piping:

1. Use ambient temperature water as a testing medium unless there is risk of damage due to freezing.  Another liquid that is safe for workers and compatible with piping may be used.

2. While filling system, use vents installed at high points of system to release trapped air.  Use drains installed at low points for complete draining of liquid.

3. Check expansion tanks to determine that they are not air bound and that system is full of water.

4. Subject piping system to hydrostatic test pressure that is not less than 1.5 times the design pressure.  Test pressure shall not exceed maximum pressure for any vessel, pump, valve, or other component in system under test.  Verify that stress due to pressure at bottom of vertical runs does not exceed either 90 percent of specified minimum yield strength or 1.7 times "SE" value in Appendix A of ASME B31.9, "Building Services Piping."

5. After hydrostatic test pressure has been applied for at least 10 minutes, examine piping, joints, and connections for leakage.  Eliminate leaks by tightening, repairing, or replacing components, and repeat hydrostatic test until there are no leaks.

6. Prepare written report of testing.

3.11 ADJUSTING

A. Mark calibrated nameplates of pump discharge valves after hydronic system balancing has been completed, to permanently indicate final balanced position.

B. Perform these adjustments before operating the system:

1. Open valves to fully open position.  Close coil bypass valves.

2. Check pump for proper direction of rotation.

3. Set automatic fill valves for required system pressure.

4. Check air vents at high points of system and determine if all are installed and operating freely (automatic type), or bleed air completely (manual type).

5. Set temperature controls so all coils are calling for full flow.

6. Check operation of automatic bypass valves.

7. Check and set operating temperatures of boilers, chillers, and cooling towers to design requirements.

8. Lubricate motors and bearings.

3.12 CLEANING

A. Flush hydronic piping systems with clean water.  Remove and clean or replace strainer screens.  After cleaning and flushing hydronic piping systems, but before balancing, remove disposable fine-mesh strainers in pump suction diffusers.

END OF SECTION 15181
HYDRONIC PIPING
15181 - 1

