Copyright 2002 AIA
GSA VERSION MASTERSPEC
03/02 (R 09/03) (GSA 03/05)

Copyright 2002 (09/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15671 - CONDENSING UNITS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes [air-] [and] [water-]cooled condensing units.

1.3 SUBMITTALS

A. Product Data:  For each condensing unit, include rated capacities, operating characteristics, furnished specialties, and accessories.  Include equipment dimensions, weights and structural loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain paragraph and subparagraphs below if condensing units are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify condensing units' compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Shop Drawings:  Signed and sealed by a qualified professional engineer.

1. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

2. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.

3. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Structural members to which condensing units will be attached.

2. Liquid and vapor pipe sizes.

3. Refrigerant specialties.

4. Piping including connections, oil traps, and double risers.

5. Evaporators.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

D. Manufacturer Seismic Qualification Certification:  Submit certification that condensing units, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For condensing units to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

Retain paragraph and subparagraph below if HCFC-free refrigerants are required for LEED Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

H. LEED Submittals:

1. Credit EA 4:  Manufacturers' product data for refrigerants, including printed statement that refrigerants are free of HCFCs.

1.4 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of condensing units and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Fabricate and label refrigeration system according to ASHRAE 15, "Safety Code for Mechanical Refrigeration."

Retain subparagraph below to comply with LEED Credit EA 4.

1. Units shall be designed to operate with HCFC-free refrigerants.

Retain first paragraph below only for water-cooled condensing units 135,000 Btu/h (39 500 W) and larger.

D. ASME Compliance:  Fabricate and label water-cooled condensing units to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

C. Coordinate location of piping and electrical rough-ins.

1.6 WARRANTY

Warranties vary among manufacturers from covering the whole unit up to 4 years, to only the compressor for 5 to 10 years, or the condenser coil only for 5 years.  Extended special warranties are limited to units in the 1- to 5-ton (3.5- to 17.6-kW) range, and then are usually restricted to residential applications.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of condensing units that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Compressor failure.

b. Condenser coil leak.

Verify available warranties and insert number below.

2. Warranty Period:  [Four] [Five] [10] <Insert number> years from date of Substantial Completion.

3. Warranty Period:  [Four] <Insert number> years from date of Substantial Completion.

4. Warranty Period (Compressor Only):  [Five] [10] <Insert number> years from date of Substantial Completion.

5. Warranty Period (Condenser Coil Only):  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to manufacturers specified.
2.2 CONDENSING UNITS, AIR COOLED, 3.5 TO 17.6 kW (1 TO 5 TONS)
A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Carrier Corporation; Carrier Air Conditioning Div.

2. Lennox Industries Inc.

3. Rheem Manufacturing Air Conditioning Div.

4. Trane Co. (The); Worldwide Applied Systems Group.

5. Weatherking Air Conditioning Div.

6. York International Corp.

7. <Insert manufacturer's name.>

B. Description:  Factory assembled and tested, consisting of compressor, condenser coil, fan, motors, refrigerant reservoir, and operating controls.

C. Compressor:  Scroll, hermetically sealed, with rubber vibration isolators.

1. Motor:  [Single] [Two] speed, and includes thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

Two-speed compressor below is not available from all manufacturers.

2. Two-Speed Compressor:  Include manual-reset, high-pressure switch and automatic-reset, low-pressure switch.

Accumulator below is available only on 4- and 5-ton (14- and 17.6-kW) units.

3. Accumulator:  Suction tube.

Retain HCFC-free refrigerant for new HVAC&R systems if required to comply with LEED Credit EA 4.

4. Refrigerant Charge:  [R-407C] [R-410A] <Insert type>.

D. Condenser Coil:  Seamless copper-tube, aluminum-fin coil; circuited for integral liquid subcooler, with removable drain pan and brass service valves with service ports.

E. Condenser Fan:  Direct-drive, aluminum propeller fan; with permanently lubricated, totally enclosed fan motor with thermal-overload protection[ and ball bearings].

F. Accessories:

Edit list of accessories below to suit Project.  Not all accessories are available from all manufacturers.

1. Coastal Filter:  Mesh screen to protect condenser coil from salt damage.

2. Crankcase heater.

3. Cycle Protector:  Automatic-reset timer to prevent rapid compressor cycling.

4. [Electronic programmable thermostat] [Low-voltage thermostat and subbase] to control condensing unit and evaporator fan.

5. Evaporator Freeze Thermostat:  Temperature-actuated switch that stops unit when evaporator reaches freezing temperature.

6. Filter-dryer.

7. High-Pressure Switch:  Automatic-reset switch cycles compressor off on high refrigerant pressure.

8. Liquid-line solenoid.

9. Low Ambient Controller:  Cycles condenser fan to permit operation down to minus 18 deg C (0 deg F)[ with time-delay relay to bypass low-pressure switch].

Select subparagraph above or first subparagraph below if required.

10. Low Ambient Controller:  Controls condenser fan speed to permit operation down to minus 29 deg C (minus 20 deg F)[ with time-delay relay to bypass low-pressure switch].

11. Low-Pressure Switch:  Automatic-reset switch cycles compressor off on low refrigerant pressure.

12. PE mounting base to provide a permanent foundation.

13. Precharged and insulated suction and liquid tubing.

14. Sound Hood:  Wraps around sound attenuation cover for compressor.

15. Thermostatic expansion valve.

16. Time-Delay Relay:  Continues operation of evaporator fan after compressor shuts off.

17. <Insert accessories.>

G. Unit Casing:  Galvanized steel, finished with baked enamel; with removable panels for access to controls, weep holes for water drainage, and mounting holes in base.  Mount service valves, fittings, and gage ports on exterior of casing.

2.3 CONDENSING UNITS, AIR COOLED, 21 TO 422 kW (6 TO 120 TONS)
A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Carrier Corporation; Carrier Air Conditioning Div.

2. Continental Products.

3. Engineered Air.

4. Lennox Industries Inc.

5. McQuay International.

6. Rheem Manufacturing Air Conditioning Div.

7. Trane Co. (The); Worldwide Applied Systems Group.

8. York International Corp.

9. <Insert manufacturer's name.>

B. Description:  Factory assembled and tested, air cooled; consisting of casing, compressors, condenser coils, condenser fans and motors, and unit controls.

C. Compressor:  Hermetic or semihermetic compressor designed for service with crankcase sight glass, crankcase heater, and backseating service access valves on suction and discharge ports.

1. Capacity Control:  [Cylinder unloading] [Hot-gas bypass].

Retain HCFC-free refrigerant for new HVAC&R systems if required to comply with LEED Credit EA 4.

2. Refrigerant Charge:  [R-407C] [R-410A] [HFC-134a] <Insert type>.

D. Minimum Efficiency:  For units greater than 39.6 kW (134,000 Btu/hr):  

1. EER: 
10.1

2. IPLV:
11.2

E. Condenser Coil:  Seamless copper-tube, aluminum-fin coil, including subcooling circuit and backseating liquid-line service access valve.  Factory pressure test coils, then dehydrate by drawing a vacuum and fill with a holding charge of nitrogen or refrigerant.

F. Condenser Fans:  Propeller-type vertical discharge; either directly or belt driven.  Include the following:

1. Permanently lubricated ball-bearing motors.

2. Separate motor for each fan.

3. Dynamically and statically balanced fan assemblies.

G. Operating and safety controls include the following:

1. Manual-reset, high-pressure cutout switches.

2. Automatic-reset, low-pressure cutout switches.

3. Low oil pressure cutout switch.

4. Compressor-winding thermostat cutout switch.

5. Three-leg, compressor-overload protection.

6. Control transformer.

7. Magnetic contactors for compressor and condenser fan motors.

8. Timer to prevent excessive compressor cycling.

H. Accessories:

Edit list of accessories below to suit Project.  Not all accessories are available from all manufacturers.

1. [Electronic programmable thermostat] [Low-voltage thermostat and subbase] to control condensing unit and evaporator fan.

2. Low Ambient Controller:  Cycles condenser fan to permit operation down to minus 18 deg C (0 deg F)[ with time-delay relay to bypass low-pressure switch].

Select subparagraph above or first subparagraph below if required.

3. Low Ambient Controller:  Controls condenser fan speed to permit operation down to minus 29 deg C (minus 20 deg F)[ with time-delay relay to bypass low-pressure switch].

4. Gage Panel:  Package with refrigerant circuit suction and discharge gages.

5. Hot-gas bypass kit.

6. Part-winding-start timing relay, circuit breakers, and contactors.

7. <Insert accessories.>

I. Unit Casings:  Designed for outdoor installation with weather protection for components and controls and with removable panels for required access to compressors, controls, condenser fans, motors, and drives.  Additional features include the following:

1. Steel, galvanized or zinc coated, for exposed casing surfaces; treated and finished with manufacturer's standard paint coating.

2. Perimeter base rail with forklift slots and lifting holes to facilitate rigging.

3. Gasketed control panel door.

4. Nonfused disconnect switch, factory mounted and wired, for single external electrical power connection.

Accessories below are optional.  All are not available from all manufacturers.

5. Condenser coil [hail guard] [grille] to protect coil from physical damage.

2.4 CONDENSING UNITS, WATER COOLED

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Carrier Corporation; Carrier Air Conditioning Div.

2. McQuay International.

3. Trane Co. (The); Worldwide Applied Systems Group.

4. York International Corp.

5. <Insert manufacturer's name.>

B. Description:  Factory assembled and tested, water cooled; consisting of compressors, water-cooled condensers, bases, and unit controls.

C. Compressor:  Hermetic or serviceable hermetic type; with oil pump, operating oil charge, and suction and discharge shutoff valves.  Factory mounted on base using spring isolators.  Include the following:

1. Thermally protected compressor motor.

2. Crankcase heater.

3. Capacity control using cylinder unloading, suction pressure controlled and discharge pressure operated, designed for unloaded start.

Retain HCFC-free refrigerant for new HVAC&R systems if required to comply with LEED Credit EA 4.

4. Refrigerant Charge:  [R-407C] [R-410A] [HFC-134a] <Insert type>.

D. Minimum Efficiency:  For units greater than 39.6 kW (134,000 Btu/hr):  

1. EER: 
13.1

2. IPLV:
13.1

E. Condenser:  Single-pass, tube-in-tube coaxial type; with seamless, integral-finned, copper tube and steel outer shell with water-regulating valve.

Retain paragraph above or first paragraph and subparagraph below.

F. Condenser:  Multipass, shell-and-tube type; with replaceable, seamless, integral-finned copper tubes; positive-liquid subcooling circuit; pressure relief device; liquid-level test cock; purge connection; liquid-line shutoff valve; and angle valve for connection of water-regulating valve.

Retain subparagraph below only if ASME stamp is required.

1. Unit Construction:  ASME stamped for refrigerant-side working pressure of 2650 kPa (385 psig) and water-side working pressure of 1720 kPa (250 psig).

G. Accessories include the following:

Edit list of accessories below to suit Project.  Not all accessories are available from all manufacturers.

1. Discharge-line muffler.

2. Gage panel containing gages for suction, discharge, and oil pressure.

3. Electric solenoid cylinder unloaders.

4. Pump-down relay package.

5. Crankcase cover plates with equalizer connections.

H. Controls:  Factory-mounted and -wired panel with the following:

1. Timer to prevent short cycling.

2. High- and low-refrigerant-pressure safety controls.

3. Power- and control-circuit terminal blocks.

4. Compressor motor starter.

5. Control-circuit on-off switch.

6. Control-circuit fuse.

2.5 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add paragraphs below to suit Project.

A. General requirements for motors are specified in Division 15 Section "Motors."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

2.6 CONTROLS

1. Factory-installed, native [ASHRAE 135 BACnet] [LonWorks compatible] microprocessor controls specified by Division 15 Section, "Building Automation System" and “Temperature Controls.”
2.7 SOURCE QUALITY CONTROL

Retain first option in first paragraph below for units smaller than 135,000 Btu/h (39 500 W) and second option for units 135,000 Btu/h (39 500 W) and larger.

A. Verification of Performance:  Rate condensing units according to ARI 365.

ASHRAE/IESNA 90.1 establishes minimum coefficient of performance for air- and water-cooled units.   LEED Prerequisite EA 2 requires minimum efficiency equal to requirements of ASHRAE/IESNA 90.1.  LEED Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1.

1. Coefficient of Performance:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1, "Energy Efficient Design of Buildings except Low-Rise Residential Buildings."

2. Energy-Efficiency Ratio:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1, "Energy Efficient Design of Buildings except Low-Rise Residential Buildings."

B. Test and inspect shell and tube condensers according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

C. Testing Requirements:  Factory test sound-power-level ratings according to ARI 270.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of condensing units.

B. Examine roughing-in for refrigerant piping systems to verify actual locations of piping connections before equipment installation.

C. Examine walls, floors, and roofs for suitable conditions where condensing units will be installed.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install units level and plumb, firmly anchored in locations indicated; maintain manufacturer's recommended clearances.

Retain first two paragraphs and associated subparagraphs below for condensing units mounted on grade.

B. Install condensing units on concrete base.  Concrete base is specified in Division 15 Section "Basic Mechanical Materials and Methods," and concrete materials and installation requirements are specified in Division 3.

Retain paragraph and subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.  Delete if retaining vibration isolation equipment bases.

C. Concrete Bases:

1. Install dowel rods to connect concrete base to concrete slab.  Unless otherwise indicated, install dowel rods on 450-mm (18-inch) centers around full perimeter of the base.

2. For equipment supported on structural slab, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Install anchor bolts according to anchor-bolt manufacturer's written instructions.

Retain paragraph below and delete two paragraphs and associated subparagraphs above if units are installed on roof.

D. Install roof-mounting units on equipment supports specified in Division 7.

Retain one of first two paragraphs below.  Coordinate with Drawings and Division 15 Section "Mechanical Vibration and Seismic Controls."  Retain first paragraph for equipment supported on slabs-on-grade.  Delete both paragraphs if vibration and seismic controls are scheduled on Drawings.

E. Vibration Isolation:  Mount condensing units on rubber pads with a minimum deflection of [6.35 mm (1/4 inch)] <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

Based on supporting structure and seismic requirements, insert amount of required deflection in first paragraph below.

F. Vibration Isolation:  Mount condensing units on restrained spring isolators with a minimum deflection of <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

G. Maintain manufacturer's recommended clearances for service and maintenance.

H. Loose Components:  Install electrical components, devices, and accessories that are not factory mounted.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Connect precharged refrigerant tubing to unit's quick-connect fittings.  Install tubing so it does not interfere with access to unit.  Install furnished accessories.

Select paragraph above for units using precharged tubing or paragraph below for assembled systems.

D. Connect refrigerant piping to air-cooled condensing units; maintain required access to unit.  Install furnished field-mounted accessories.  Refrigerant piping and specialties are specified in Division 15 Section "Refrigerant Piping."

Retain paragraph above for air-cooled condensing units and first paragraph below for water-cooled condensing units.

E. Connect refrigerant and condenser-water piping to water-cooled condensing units.  Maintain clear tube removal space.  Refrigerant piping and specialties are specified in Division 15 Section "Refrigerant Piping" and condenser-water piping and specialties are specified in Division 15 Section "[Domestic Water Piping] [Hydronic Piping]."

F. Ground equipment according to Division 16 Section "Grounding and Bonding."

G. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. Perform electrical test and visual and mechanical inspection.

2. Leak Test:  After installation, charge systems with refrigerant and oil and test for leaks.  Repair leaks, replace lost refrigerant and oil, and retest until no leaks exist.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper operation, product capability, and compliance with requirements.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

5. Verify proper airflow over coils.

B. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

C. Remove and replace malfunctioning condensing units and retest as specified above.

3.5 STARTUP SERVICE

A. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Inspect for physical damage to unit casing.

2. Verify that access doors move freely and are weathertight.

3. Clean units and inspect for construction debris.

4. Verify that all bolts and screws are tight.

5. Adjust vibration isolation and flexible connections.

6. Verify that controls are connected and operational.

B. Lubricate bearings on fans.

C. Verify that fan wheel is rotating in the correct direction and is not vibrating or binding.

Retain first paragraph below for units with belt-driven condenser fans.

D. Adjust fan belts to proper alignment and tension.

E. Start unit according to manufacturer's written instructions and complete manufacturer's startup checklist.

F. Measure and record airflow over coils.

G. Verify proper operation of condenser capacity control device.

H. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

Retain option in paragraph below for units with belt-driven condenser fans.

I. After startup and performance test, lubricate bearings[ and adjust belt tension].

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain condensing units.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15671
CONDENSING UNITS
15671 - 12

