Copyright 2000 AIA
GSA VERSION MASTERSPEC
3/00 (R 09/03) (GSA 03/05)

Copyright 2000 (09/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15734 - COMPUTER-ROOM AIR-CONDITIONING UNITS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed. 
 Delete notes to editor before submission.
PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following types of computer-room air-conditioning units:

Adjust list below to suit Project.

P100 design guidelines: (1) Use self-contained units up to 280 kW (80 tons); (2) Size units for 50% redundancy, e.g. two units each sized for 75% of the load or three units sized for 50% of the load; (3) For critical computer rooms, as determined by GSA’s Office of the Chief of Information Technology, a minimum of three units shall be used; For large computer rooms, 500 sq. m. (5,000 sq. ft.) or larger, use computer room units in combination with air-handling units.
1. Floor-mounting units
2. Ceiling-mounting units.

1.3 DEFINITIONS

A. MERV: Minimum Efficiency Reporting Value
1.4 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

C. Manufacturer Seismic Qualification Certification:  Submit certification that computer-room air-conditioning units, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specifiied [and the unit will be fully operational after the seismic event]."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For computer-room air-conditioning units to include in emergency, operation, and maintenance manuals.

F. Warranties:  Special warranties specified in this Section.

Retain paragraph and subparagraph below if HCFC-free refrigerants are required for LEED Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

G. LEED Submittals:

1. Credit EA 4:  Manufacturers' product data for refrigerants, including printed statement that refrigerants are free of HCFCs.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Fabricate and label refrigeration system to comply with ASHRAE 15, "Safety Code for Mechanical Refrigeration."

C. Energy-Efficiency Ratio:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1, "Energy Efficient Design of Buildings except Low-Rise Residential Buildings."

D. Coefficient of Performance:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1, "Energy Efficient Design of New Buildings except Low-Rise Residential Buildings."

E. ANSI/ARI Compliance: ANSI/ARI 340/360, “Commercial and Industrial Unitary Air-Conditioning and Heat Pump Equipment.”  

F. EIA/TIA Standard 569 Compliance: For equipment in communication and telephone frame rooms.

G. ASME Compliance:  Fabricate and label water-cooled condenser shell to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, "Pressure Vessels," Division 1.

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerant.  R-407C and R-410A are HCFC-free refrigerants.  R-22 seems still seems to be the staple of the industry, but the number of products utilizing these new refrigerants is growing.  Ensure the specified refrigerant allows competition between unit manufacturers.

H. Units shall be designed to operate with HCFC-free refrigerants.

1.6 COORDINATION

Edit first paragraph below to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of computer-room air-conditioning units and suspension system with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

B. Coordinate installation of computer-room air-conditioning units with computer-room access flooring Installer.

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of computer-room air-conditioning units that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

B. Warranty Period for Compressors:  Manufacturer's standard, but not less than [five] [10] <Insert number> years from date of Substantial Completion.

C. Warranty Period for Humidifiers:  Manufacturer's standard, but not less than [three] <Insert number> years from date of Substantial Completion.

D. Warranty Period for Control Boards:  Manufacturer's standard, but not less than [three] <Insert number> years from date of Substantial Completion.

1.8 EXTRA MATERIALS

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Fan Belts:  [One set] [<Insert number> sets] for each belt-drive fan.

2. Filters:  [One set] [<Insert number> sets] of filters for each unit.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where subparagraph titles below introduce lists, the following requirements apply for product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.  
2.2 FLOOR-MOUNTING UNITS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Compu-Aire, Inc.

2. Data Aire Inc.

3. Liebert Corporation.

4. Stulz Air Technology Systems, Inc.
5. <Insert manufacturer's name.>

B. Description and Assembly:  Packaged, factory assembled, prewired, and prepiped; consisting of cabinet, fans, filters, humidifier, and controls.

Select configuration from options in subparagraph below.

1. Assembly: [ Downflow][ Upflow] air delivery, in [draw] [blow]-through configuration.

C. Efficiencies:

1. Capacities 19  to 40 kW (65,000 to 135,000 Btuh):  Minimum EER 10.3

2. Capacities 40 to 70 kW (135,000 to 240,000 Btuh):  Minimum EER 9.7

3. Capacities 70 to 223 kW (240,000 to 760,000 Btuh):  Minimum EER 9.5, minimum IPLV 9.7

D. Cabinet and Frame:  Welded steel, suitably braced for rigidity, supporting compressors and other mechanical equipment and fittings; with floor stand with adjustable legs and vibration isolation pads.

1. Doors and Access Panels:  Galvanized steel with polyurethane gaskets, hinges, and concealed fastening devices.

2. Insulation:  Thermally and acoustically insulate cabinet interior with 25-mm- (1-inch-) thick duct liner.

3. Finish of Exterior Surfaces:  Baked-on, textured vinyl enamel, color [as selected from manufacturer's standard colors] [to match computer equipment].

4. Floor Stand:  Welded tubular steel, <Insert required height> high.

5. Top discharge plenum[ with turning vanes].

E. Evaporator Fan:  Double inlet, forward curved, centrifugal, and statically and dynamically balanced.

Select fan drive from options in first subparagraph below.

1. Drive:  [V-belt drive with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor] [Direct].

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  These characteristics, such as “Noise rating of quiet” used below, have meaning within NEMA standards upon which motor designs are based.  If different characteristics are required, add paragraphs below to suit Project.

2. Motor:  Comply with requirements in Division 15 Section "Motors."

a. Noise Rating:  Quiet.

Select compressor type from first three options in first paragraph below.  Retain or delete fourth option with any of the three compressor options.

F. Compressors:  [Hermetic reciprocating;] [Hermetic scroll;] with[ oil strainer, internal motor overload protection,] resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

1. Refrigeration Circuits:  [Two, ][Quantity to match number of compressors, ]each with hot-gas mufflers, thermal-expansion valve with external equalizer, liquid-line solenoid valve, liquid-line filter-dryer, sight glass with moisture indicator, service shutoff valves, charging valves, accumulator sized for liquid seal under light load, and charge of refrigerant.

Restrictions on hot gas bypass capacity come from Table 6.5.9 of ASHRAE 62-2004.

2. Hot gas bypass: 

a. Units 26 to 70 kW (7.5 to 20 tons):  Maximum 50% bypass.

b. Units over 70 kW (20 tons):  Maximum 25% bypass.

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerant.  R-407C and R-410A are HCFC-free refrigerants.  R-22 seems still seems to be the staple of the industry, but the number of products utilizing these new refrigerants is growing.  Insure the specified refrigerant allows competition between unit manufacturers.  Consider the following requirement carefully.
3. Refrigerant: [R-22] [R-407C] [R-410A] <Insert other available type>.

G. Evaporator Coil:  Alternate-row or split-face-circuit, direct-expansion coil of seamless copper tubes expanded into aluminum fins.  Mount coil assembly over stainless-steel drain pan[ having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

Select water-regulating valve type from options in paragraph below; two way is standard, three way is optional.

H. Water-Cooled Condenser:  [Coaxial tube-in-tube type] [Plate type] with liquid-line stop valve and head-pressure-actuated, [two] [three]-way, water-regulating valve.  Terminate water connections outside cabinet.

Retain paragraph above or first paragraph below.

I. Air-Cooled Condenser:  Corrosion-resistant cabinet, copper-tube aluminum-fin coils arranged for two circuits, multiple direct-drive propeller fans with permanently lubricated ball bearings, and single-phase motors with internal overload protection, integral electric control panel, and disconnect switch.  Control capacity by cycling fans.

J. Chilled-Water Coil:  Seamless copper tubes expanded into aluminum fins with modulating control valve.  Mount coil assembly over stainless-steel drain pan[ having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

K. Glycol Cooling Coil:  Seamless copper tubes expanded into aluminum fins with three-way control valve.

L. Electric-Resistance Heating Coil:  Enclosed finned-tube electric elements arranged for minimum of three stages, with primary and secondary thermal switches, manual-reset overload protection, and branch-circuit overcurrent protection.

M. Refrigerant Reheat Coil:  Hot-gas refrigerant coil of seamless copper tubes expanded into aluminum fins with three-way solenoid valve on first-stage refrigerant circuit.

N. Hot-Water Reheat Coil:  Seamless copper tubes expanded into aluminum fins with two-way modulating control valve and strainer.

LEED Credit EQ 3.1 requires minimum MERV-13 filters.  Verify availability of MERV-13 filters with unit manufacturers.  Units 5 tons and less typically do not have the power to overcome static pressure of MERV 13 filters.
O. Filter:  Pleated, lofted, nonwoven, reinforced cotton fabric; supported and bonded to welded-wire grid; enclosed in cardboard frame[ with 50-mm- (2-inch-) thick, disposable, glass-fiber prefilter].

1. Nominal Thickness:  [50 mm (2 inches)] [100 mm (4 inches)].

2. Dust-Spot Efficiency:  [30] [65] percent.

Select ASHRAE 52.1 efficiency above or ASHRAE 52.2 below.

3. Efficiency: MERV [8] [13]
4. Weight Arrestance:  90 to 92 percent.

5. Initial Resistance at 2.54-m/s (500-FPM) Face Velocity:  75 Pa (0.30-inch wg).

6. Recommended Final Resistance:  250 Pa (1-inch wg).

Retain one of three humidifiers below.  Infrared humidifiers are used by a limited number of manufacturers.  
P. Infrared Humidifier:  High-intensity quartz lamps mounted above stainless-steel evaporator pan, serviceable without disconnecting water, drain, or electrical connections; prepiped and using condensate water from cooling coils with stainless-steel or brass float-valve mechanism; located in bypass airstream; with flush-cycle timer and solenoid drain valve.

Q. Electrode Steam Humidifier:  Self-contained, microprocessor-controlled unit with disposable, polypropylene-plastic cylinders and having field-adjustable steel electrodes and stainless-steel steam dispersion tube.

1. Plumbing Components and Valve Bodies:  Plastic, linked by flexible rubber hosing, with water fill with air gap and solenoid valve incorporating built-in strainer, pressure-reducing and flow-regulating orifice, and drain with integral air gap on drain.

2. Control:  Fully modulating to provide gradual 0 to 100 percent capacity with field-adjustable maximum capacity; with high-water probe.

3. Drain Cycle:  Field-adjustable drain duration and drain interval.

R. Ultrasonic Humidifier:  Self-contained, operating on piezoelectric nebulization principle.
Roof-installed dry coolers comply with P-100 when there is sufficient access via freight elevator or staircase.

S. Remote Glycol Drycooler:  Corrosion-resistant cabinet, copper-tube aluminum-fin coil, multiple direct-drive propeller fans with fan guards, and single-phase motors with internal overload protection, integral electric control panel, and disconnect switch.  Control capacity by cycling fans.

T. Glycol Pump Package:  Weatherproof and vented enclosure. of Eenameled, galvanized steel on structural base frame containing two centrifugal pumps with mechanical seals; electrical-control cabinet with starters, disconnect switch, lead-lag switch, automatic switchover, and alarm light.

1. Piping:  Interconnecting piping, from suction to discharge, with shutoff valves, flow switches, check valves in pump discharge, unions, and pressurized expansion tank with air purge vent and system-charging connection.

2. Motor: TEFC[, outdoor-duty rated].

Select NEMA 3R for outdoor installations.

U. Integral Electrical Controls:  Unit-mounted electrical enclosure with piano-hinged door, grounding lug, combination [NEMA 3R ]magnetic starters with overload relays, circuit breakers and cover interlock, and fusible control-circuit transformer.

Paragraph below describes an optional accessory.  Standard unit does not come with disconnect switch.  Coordinate with Division 16 Sections.

V. Disconnect Switch:  Nonautomatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

Paragraph and subparagraphs below are representative of standard electronic controls.

W. Electronic-Control System:  Solid state, with start button, stop button, temporary loss of power indicator, manual-reset circuit breakers, temperature control, humidity control, and monitor panel.

1. Monitor Panel:  Backlighted, with no visible indicator lights until operating function is activated; indicators include cooling, humidification, loss of airflow, change filters, high temperature, low temperature, high humidity, low humidity, high head pressure (each compressor), and low suction pressure (each compressor).

2. Temperature- and Humidity-Control Modules:  Solid state, plug-in; with adjustable set point, push-to-test calibration check button, and built-in visual indicators to show mode of operation.

3. Location:  Behind hinged door in front of unit; isolated from conditioned airstream to allow service while system is operating.

X. Accessories:

a. Condensate pump.

b. Firestat.

c. Water detector.

d. Smoke detector.

e. Compressor sound jacket.

Paragraph and subparagraphs below are representative of optional microprocessor controls.

Y. Microprocessor-Control System:  
1. Factory-installed, [native ASHRAE 135, BACnet,] [LonWorks compatible] microprocessor controls specified by Division 15 Section, "Building Automation System" and “Temperature Controls”.

2. In-room display and monitoring device[ equipment][ wall] mounted.
3. Continuously monitors operation of process cooling system; continuously displays room temperature and room relative humidity; sounds alarm on system malfunction and simultaneously displays problem.  If more than one malfunction occurs, system displays fault in sequence with room temperature and continues to display fault when malfunction is cleared until system is reset.

4. Malfunctions:

a. Power Loss.

b. Loss of Airflow.

c. Clogged Air Filter.

d. High Room Temperature.

e. Low Room Temperature.

f. High Humidity.

g. Low Humidity.

h. Smoke/Fire.

i. Water-under-Floor.

j. Supply Fan Overload.

k. Compressor No. 1--Overload.

l. Compressor No. 1--Low Pressure.

m. Compressor No. 1--High Pressure.

n. Compressor No. 2--Overload.

o. Compressor No. 2--Low Pressure.

p. Compressor No. 2--High Pressure.

5. LED Display:

a. Control Power On.

b. Humidifying.

c. Dehumidifying.

d. Compressor No. 1 Operating.

e. Compressor No. 2 Operating.

f. Heat Operating.

g. Economy Cooling.

6. Push buttons shall stop and start process cooling system, silence audible alarm, test LED indicators, and display room relative humidity.

7. Remote Signaling:  Provide terminals for remote signaling of system status and alarms.

LEED Credit EA 5 requires continuous metering equipment for monitoring building energy consumption performance over time.  Retain subparagraph and associated subparagraphs below if required to comply with the requirements for this credit.  Verify availability of control features with unit manufacturers.

8. Additional Monitoring:

a. Monitor cooling load.

b. Monitor economizer cycles.

c. Monitor air distribution static pressure and ventilation air volumes.
d. Smoke detector.
e. Firestat.
Z. Maintain the following conditions in computer and communications-telephone frame rooms between 150 mm and 2 meters (6 inches and 6 feet) above floor:

1. Summer humidity:  (45 to 60% RH plus or minus 5%).

2. Winter humidity:  30% RH plus or minus 5%)

2.3 CEILING-MOUNTING UNITS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Compu-Aire, Inc.

2. Data Aire Inc.

3. Liebert Corporation.

4. Stulz Air Technology Systems, Inc.

5. <Insert manufacturer's name.>

B. Description:  Self-contained, factory assembled, prewired, and prepiped; consisting of cabinet, fan, filters, and controls; for horizontal ceiling mounting to fit 610-by-1220-mm (24-by-48-inch) T-bar ceiling opening.

C. Minimum efficiencies:

1. Capacities 19  to 40 kW (65,000 to 135,000 Btuh):  EER 10.3

2. Capacities 40 to 70 kW (135,000 to 240,000 Btuh):  EER 9.7

3. Capacities 70 to 223 kW (240,000 to 760,000 Btuh):  EER 9.5, IPLV 9.7

D. Cabinet:  Galvanized steel with baked-enamel finish, insulated with 15-mm- (1/2-inch-) thick duct liner.

E. Evaporator Fan:  Forward curved, centrifugal, and directly driven by two-speed motor.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add paragraphs below to suit Project.

1. Motor:  Comply with requirements in Division 15 Section "Motors."

a. Noise Rating:  Quiet.

F. Compressor:  Hermetic, with resilient suspension system, oil strainer, and internal motor overload protection.

1. Refrigeration Circuit:  Low-pressure switch, manual-reset high-pressure switch, thermal-expansion valve with external equalizer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerant.  R-407C and R-410A are HCFC-free refrigerants.  R-22 seems still seems to be the staple of the industry, but the number of products utilizing these new refrigerants is growing.  Ensure the specified refrigerant allows competition between manufacturers.  Consider the following requirement carefully.
2. Refrigerant:  [R-22] [R-407C] [R-410A] <Insert other available type>.

G. Evaporator Coil:  Direct-expansion cooling coil of seamless copper tubes expanded into aluminum fins.  Mount coil assembly over stainless-steel drain pan[ having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

H. Water-Cooled Condenser:  [Coaxial, counterflow, tube-in-tube] [Brazed-plate] type with liquid-line stop valve and head-pressure-actuated, water-regulating valve.

Retain paragraph above or first paragraph below.

I. Air-Cooled Condenser:  Integral copper-tube aluminum-fin coil with [propeller] [centrifugal] fan, direct driven.

Subparagraph below may be retained with either of last two paragraphs above.

1. Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

J. Chilled-Water Coil:  Seamless copper tubes expanded into aluminum fins with modulating control valve.  Mount coil assembly over stainless-steel drain pan[ having a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir].

K. Electric-Resistance Heating Coil:  Finned-tube electric elements with contactor, dehumidification relay, and high-temperature-limit switch.

LEED Credit EQ 3.1 requires minimum MERV-13 filters.  Verify availability of MERV-13 filters with unit manufacturers.

L. Filter:
1. Thickness:  25-mm- (1-inch-) thick, disposable, glass-fiber media.

2. Efficiency: MERV 13
Retain one of two humidifiers below or delete both.  Humidifiers are optional on this type of equipment.

M. Atomizing Humidifier:  Centrifugal atomizer with stainless-steel pan, demister pad, and solenoid valve.

N. Electrode Steam Humidifier:  Self-contained, microprocessor-controlled unit with disposable, polypropylene-plastic cylinders and having field-adjustable steel electrodes and stainless-steel steam dispersion tube.

1. Plumbing Components and Valve Bodies:  Plastic, linked by flexible rubber hosing, with water fill with air gap and solenoid valve incorporating built-in strainer, pressure-reducing and flow-regulating orifice, and drain with integral air gap on drain.

2. Control:  Fully modulating to provide gradual 0 to 100 percent capacity with field-adjustable maximum capacity; with high-water probe.

3. Drain Cycle:  Field-adjustable drain duration and drain interval.

O. Ultrasonic Humidifier:  Self-contained, operating on piezoelectric nebulization principle.

P. Control System:  
1. Programmable thermostat.

2. Factory-installed, [native ASHRAE 135, BACnet,] [LonWorks compatible] microprocessor controls specified by Division 15 Section, "Building Automation System" and “Temperature Controls”.

LEED Credit EA 5 requires continuous metering equipment for monitoring building energy consumption performance over time.  Retain subparagraph and associated subparagraphs below if required to comply with the requirements for this credit.  Verify availability of control features with unit manufacturers.

3. Continuously monitors operation of process cooling system; continuously displays room temperature and room relative humidity; sounds alarm on system malfunction and simultaneously displays problem.  If more than one malfunction occurs, system displays fault in sequence with room temperature and continues to display fault when malfunction is cleared until system is reset.

4. Additional Monitoring:

a. Monitor cooling load.

b. Monitor economizer cycles.

c. Monitor air distribution static pressure and ventilation air volumes.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install computer-room air-conditioning units level and plumb, maintaining manufacturer's recommended clearances.[ Install according to ARI Guideline B.]

Retain paragraph below if components are roof mounted.

B. Curb Support:  Install and secure roof-mounting units on curbs and coordinate roof penetrations and flashing with roof construction.[ Secure units to curb support with anchor bolts.]

Select paragraph above or below for appropriate mounting method and edit to suit Project.  Anchor bolts may be required for seismic restraint.

C. Install suspended components level.  Coordinate wall penetrations and flashing with wall construction.[ Secure units to structural support with anchor bolts.]

Select one of three paragraphs below for remotely mounted equipment.

D. Install air-cooled condenser on rubber-in-shear vibration isolators.

E. Install remote glycol cooler on rubber-in-shear vibration isolators.

F. Install glycol pump package on rubber-in-shear vibration isolators.

Retain paragraph below for projects in seismic areas.

G. Install floor-mounting units on bases designed to withstand, without damage to equipment, seismic forces required by code.

Retain below for suspended units; delete if vibration and seismic controls are scheduled on Drawings.

H. Support suspended units from structure using threaded steel rods and [elastomeric hanger] [spring hanger] [spring hanger, with vertical-limit stop,] having [25-mm (1-inch) deflection] <Insert deflection>.  Vibration-control devices and installation requirements are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Water and Drainage Connections:  Comply with applicable requirements in Division 15 Section "Domestic Water Piping."  Provide adequate connections for water-cooled units, condensate drain, and humidifier flushing system.

Retain paragraph below for units with hot-water coils.

D. Hot-Water Heating Piping:  Comply with applicable requirements in Division 15 Section "Hydronic Piping."  Provide shutoff valves in inlet and outlet piping to reheat coils.

E. Condenser-Water Piping:  Comply with applicable requirements in Division 15 Section "Hydronic Piping."  Provide shutoff valves in water inlet and outlet piping on water-cooled units.

F. Refrigerant Piping:  Comply with applicable requirements in Division 15 Section "Refrigerant Piping."  Provide shutoff valves and piping.

G. Glycol Pump Package Piping: Interconnecting piping, from suction to discharge, with shutoff valves, flow switches, check valves in pump discharge, unions, and pressurized expansion tank with air purge vent and system-charging connection.

H. Electrical System Connections:  Comply with applicable requirements in Division 16 Sections for power wiring, switches, and motor controls.

I. Ground equipment according to Division 16 Section "Grounding and Bonding."

J. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with paragraph above.  Edit to suit Project.

1. Inspect for and remove shipping bolts, blocks, and tie-down straps.

2. After installing computer-room air-conditioning units and after electrical circuitry has been energized, test for compliance with requirements.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3.4 STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

B. Verify that computer-room air-conditioning units are installed and connected according to manufacturer's written instructions and the Contract Documents.

C. Verify that electrical wiring installation complies with manufacturer's submittal and installation requirements in Division 16 Sections.

D. Complete installation and startup checks according to manufacturer's written instructions.

E. After startup service and performance test, change filters and flush humidifier.

3.5 ADJUSTING

A. Adjust initial temperature[ and humidity] set points.

B. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to two visits to site outside normal occupancy hours for this purpose, without additional cost.

3.6 DEMONSTRATION

Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain computer-room air-conditioning units.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15734
COMPUTER-ROOM AIR-CONDITIONING UNITS
15734 - 7

