Copyright 2002 AIA
GSA VERSION MASTERSPEC
06/02 (09/03) (GSA 03/05)

Copyright 2002 (09/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15736 - SELF-CONTAINED AIR-CONDITIONING UNITS (15 TONS AND SMALLER)
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

Select one of three condensers in first paragraph below or edit to suit Project.

A. This Section includes packaged air-conditioning units with refrigerant compressors and controls, intended for indoor installations, with [water] [externally mounted air] [integral air]-cooled condensers.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Mechanical Vibration and Seismic Controls" for isolation pads, spring isolators, and seismic restraints.

2. Division 15 Section "Building Automation System" for control devices not packaged with units.

3. Division 15 Section "Sequence of Operation" for control sequences affecting operation of units.

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, furnished specialties, and accessories for each type of product indicated.

B. Shop Drawings:  Diagram power, signal, and control wiring.

C. Samples for Initial Selection:  For units with factory-applied color finishes.

D. Operation and Maintenance Data:  For self-contained air-conditioning units to include in maintenance manuals specified in Division 1.

E. Warranties:  Special warranties specified in this Section.

Retain paragraph and subparagraph below if HCFC-free refrigerants are required for LEED Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

F. LEED Submittals:

1. Credit EA 4:  Manufacturers' product data for refrigerants, including printed statement that refrigerants are free of HCFCs.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Energy-Efficiency Ratio:  Equal to or greater than prescribed by ASHRAE 90.1, "Energy Efficient Design of Buildings except Low-Rise Residential Buildings."

C. Coefficient of Performance:  Equal to or greater than prescribed by ASHRAE 90.1, "Energy Efficient Design of Buildings except Low-Rise Residential Buildings."

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerant.  Coordinate paragraph below with requirements selected in Part 2 for refrigerants.

D. Units shall be designed to operate with HCFC-free refrigerants.

1.5 COORDINATION

A. Coordinate size and location of concrete bases for units.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete."

Retain paragraph below for units with remote-mounted air-cooled condensers.  
B. Coordinate size, location, and connection details with equipment supports, remote strikeout.
1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. General Warranty:  Special warranty specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

B. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of self-contained air-conditioning units that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period:  [Five] <Insert other number> years from date of Substantial Completion.

1.7 EXTRA MATERIALS

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise two subparagraphs below to suit Project.

1. Filters:  One set of filters for each unit.

2. Fan Belts:  One set of belts for each unit.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Water-Cooled, Self-Contained Air-Conditioning Units:

a. Carrier Air Conditioning; Div. of Carrier Corp.

b. Engineered Air.

c. Marshall Engineered Pruducts Co. (MEPCO).

d. McQuay International.

e. Trane Co. (The); North American Commercial Group.

f. USA Coil & Air Inc.

g. Whalen Co. (The).

h. <Insert manufacturer's name.>

2. Remote Air-Cooled, Self-Contained Air-Conditioning Units:

a. Carrier Air Conditioning; Div. of Carrier Corp.

b. Engineered Air.

c. McQuay International.

d. Trane Co. (The); North American Commercial Group.

e. USA Coil & Air Inc.

f. Whalen Co. (The).

g. <Insert manufacturer's name.>

3. Integral Air-Cooled, Self-Contained Air-Conditioning Units:

a. McQuay International.

b. Trane Co. (The); North American Commercial Group.

c. <Insert manufacturer's name.>

4. Integral Air-Cooled, Wall-Mount Air-Conditioning Units:

a. Bard Manufacturing Co.

b. Stulz Air Technology Systems, Inc.

c. <Insert manufacturer's name.>

2.2 PACKAGED UNITS

A. Description:  Self-contained, factory-assembled and -wired unit; consisting of cabinet, compressor, evaporator fan, evaporator coil, air filters, and controls; and fully charged with refrigerant and oil.

Select one of three condensers in subparagraph below.

1. Condenser:  [Integral water] [Integral air] [Remote air]-cooled condenser.

2. Performance efficiency for water-cooled units: 

a. Units less than 19 kW (65,000 Btuh):  12.1 EER

b. Units 19 kW through 40 kW (65,000 and 135,000 Btuh): 11.3 EER

c. Units 40 kW through  53 kW (135,000 through 180,000 Btuh): 10.8 EER

3. Performance efficiency for air-cooled units: 

a. Units less than 19 kW (65,000 Btuh):  10 SEER

b. Units 19 kW through 40 kW (65,000 and 135,000 Btuh): 10.1 EER

c. Units 40 kW through  53 kW (135,000 through 180,000 Btuh): 9.5 EER

B. Disconnect Switch:  Factory mounted [in control panel] [on equipment].

2.3 CABINET

A. Frame and Panels:  Structural-steel frame with galvanized-steel panels with baked-enamel finish in color selected by Architect, and with access doors or panels.

B. Insulation:  Minimum 13-mm- (1/2-inch-) thick, non-fibrous acoustic duct liner on cabinet interior and control panel.

C. Condensate Drain Pans:  Formed sections of Type 304 stainless steel sheet complying with requirements in ASHRAE 62.  Pans to extend minimum 305 mm (12 inches) past coil.  Fabricate pans with slopes in a minimum of two planes to collect condensate from cooling coils (including coil piping connections and return bends) and humidifiers when units are operating at maximum catalogued face velocity across cooling coil.

1. Double Wall Construction:  Fill space between walls with foam insulation and seal moisture tight.

2. Drain Connections:  Both ends of pan.

3. Units with stacked coils shall have an intermediate drain pan or drain trough to collect condensate from top coil.

4. Insulation:  Polystyrene or polyurethane insulation

5. Slope to drain

Select the option for units with draw through fan configurations.

6. Traps at each drain.  [Drain traps with depth and height differential between inlet and outlet equal or greater to the design static pressure plus 25.4 mm (1 inch w.g.)]  Include slab height in trap calculation.

Two paragraphs below are optional.

D. Discharge Plenum:  Cabinet extension with directional louvers.

E. Corrosion-Resistant Treatment:  Phenolic coating on unit interior and exterior.

2.4 EVAPORATOR FAN

A. Material:  Galvanized steel.

B. Configuration:  Double-width, double-inlet, forward-curved centrifugal fan; statically and dynamically balanced.

Select one of two drive types in first paragraph below.

C. Drive:  [Belt, with fan mounted on permanently lubricated bearings] [Direct, with fan and motor resiliently mounted].

D. Fan Sheaves:  Cast-iron or steel sheaves, dynamically balanced, bored to fit shafts and keyed.

E. Motor Sheave:  Variable and adjustable pitch selected so required rpm are obtained when set at midposition.

F. Rating:  As recommended by the manufacturer or a minimum of one and one-half times nameplate rating of motor.

G. Motors:  Multispeed, PSC type.

2.5 COMPRESSOR

A. Description:  Hermetically sealed, 3600 rpm maximum, and resiliently mounted with positive lubrication and internal motor protection.

Select one of two compressors in paragraph below.

B. Compressor Type:  [Reciprocating] [Scroll].

2.6 EVAPORATOR COIL

A. Direct-Expansion Coil:  Seamless copper tubes expanded into aluminum fins.

Subparagraph below is optional.

1. Corrosion-Resistant Treatment:  Phenolic coating applied with multiple dips and baked.

B. Refrigeration Circuit:  A separate circuit for each compressor, with externally equalized thermal-expansion valve, filter-dryer, and charging valves.

Select one of three condenser articles below.

2.7 WATER-COOLED CONDENSER

A. Description:  Copper tubes in copper tube or in steel shell with water-temperature-actuated, water-regulating valve.

2.8 REMOTE AIR-COOLED CONDENSER

A. Description:  Factory assembled and tested; consisting of condenser coil, fans and motors, and operating controls; suitable for roof mounting.

1. Condenser Coil:  Aluminum-fin copper tube with integral subcooler; leak tested to 2930 kPa (425 psig).

2. Condenser Fans:  Direct-drive propeller type with permanently lubricated motors with built-in thermal-overload protection.

3. Refrigerant Line Kits:  Annealed-copper suction and liquid lines that are factory cleaned, dried, pressurized, and sealed; insulated suction line; flared fittings at evaporator end, no fitting at condenser end; and service valves for both suction and liquid lines.

Select one of two subparagraphs below or delete both if not required.

4. Low Ambient Control:  Cycles fans to permit operation down to 7 deg C (45 deg F).

5. Low Ambient Control:  Cycles fans and modulates condenser fan damper assembly to permit operation down to minus 18 deg C (0 deg F).

Subparagraph below is optional.

6. Corrosion-Resistant Treatment:  Phenolic coating applied in multiple dips and baked.

2.9 INTEGRAL AIR-COOLED CONDENSER

A. Description:  Factory assembled and tested; consisting of condenser coil, fans and motors, and cabinet.

1. Condenser Coil:  Aluminum-fin copper tube with integral subcooler; leak tested to 2930 kPa (425 psig).

2. Condenser Fan:  Direct-drive propeller type with permanently lubricated motor with built-in thermal-overload protection.

3. Low Ambient Control:  Cycles fans to permit operation down to minus 18 deg C (0 deg F).

2.10 REFRIGERATION SYSTEM

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerant.

A. Description:  Factory assembled and tested, and charged with[ HCFC-free] refrigerant; consisting of piping and accessories connecting compressor, evaporator coil, and condenser coil, and including the following:

Retain first subparagraph below if required for heat-pump units only.

1. Four-way reversing valve and suction line accumulator.

2. Expansion valve with replaceable thermostatic element.

3. Refrigerant dryer.

4. High-pressure switch.

5. Low-pressure switch.

6. Thermostat for coil freeze-up protection during low-ambient temperature operation or loss of air.

7. Low-ambient switch.

8. Brass service valves installed in discharge and liquid lines.

2.11 HEATING COIL

Delete this Article if unit does not include heating.  Select one heating coil type from first paragraph below.

A. Water Steam Coil:  Copper tube, with mechanically bonded copper fins spaced no closer than 2.5 mm (0.1 inch); leak tested to 2070 kPa (300 psig) underwater; and having a two-position control valve.

B. Electric Coil:  Helical, nickel-chrome, resistance-wire heating elements with refractory ceramic support bushings; automatic-reset thermal cutout; built-in magnetic contactors; manual-reset thermal cutout; airflow proving device; and one-time fuses in terminal box for overcurrent protection.

2.12 AIR FILTERS

Select and edit desired filters in this Article.  LEED Credit EQ 3.1 requires minimum MERV-13 filters.  Verify availability of MERV-13 filters with unit manufacturers.

A. Permanent Filters:  25-mm- (1-inch-) thick, cleanable panel filters.

Pleated filters in first paragraph below are not available in 1-inch (25-mm) thickness.

B. Disposable Filters:  [25-mm- (1-inch-)] [50-mm- (2-inch-)] thick, glass-fiber, [flat] [pleated] panel filters.

C. Extended-Surface, Disposable, Panel Filters:  [50-mm- (2-inch-)] [100-mm- (4-inch-)] thick,, dry, filters with fibrous media material formed into deep-V-shaped pleats and held by self-supporting wire grid holding frames, with nonflammable cardboard media and media-grid frame.

2.13 CONTROLS

A. Factory-installed, [native ASHRAE 135, BACnet,] [LonWorks compatible] microprocessor controls specified by Division 15 Section, "Building Automation System" and “Temperature Controls”.

B. Control Package:  Factory wired, including contactor, high- and low-pressure cutouts, internal-winding thermostat for compressor, control-circuit transformer, and noncycling reset relay.

C. Time-Delay Relay:  Five-minute delay to prevent compressor cycling.

Edit first paragraph and subparagraphs below to suit unit configuration.

D. Adjustable Thermostat:  [Unit mounted] [Remote] to control the following:

1. Supply fan.

2. Compressor.

3. Condenser.

4. Hot-water coil valve.

5. Steam coil valve.

6. Electric heater.

E. System Selector Switch:  [Heat-off-cool] [Off-heat-auto-cool].

F. Fan Control Switch:  Auto-on.

LEED Credit EA 5 requires continuous metering equipment for monitoring building energy consumption performance over time.  Retain paragraph and subparagraphs below if required to comply with the requirements for this credit.  Verify availability of control features with unit manufacturers.

G. Additional Monitoring:

1. Monitor constant and variable motor loads.

2. Monitor variable frequency drive operation.

3. Monitor economizer cycle.

4. Monitor cooling load.

5. Monitor air distribution static pressure and ventilation air volumes.

2.14 VENTILATION OPTIONS

Select from four paragraphs in this Article.

A. Barometric Outside-Air Damper:  Adjustable-blade damper allowing induction of up to 25 percent outside air when evaporator fan is running.

B. Motorized Outside-Air Damper:  Motorized, two-position blade damper allowing induction of up to 25 percent outside air; with spring-return, low-voltage damper motor.

C. Economizer:  Damper assembly allowing induction of up to 100 percent outside air to maintain a selected mixed-air temperature; and exhaust damper and spring-return, low-voltage, modulating damper motor with minimum position adjustment.

D. Energy-Recovery Ventilator:  Assembly of desiccant-coated, heat-recovery wheels and centrifugal exhaust fans to transfer approximately 67 percent of the difference between the sensible and latent heat of outside and exhaust air.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb.

B. Anchor units to structure.

Select one of two isolators in paragraph below; second is optional.

C. Isolation:  Mount cabinet and remote air-cooled condenser on [rubber-in-shear pads] [spring isolators] for mounting under base of unit.

Retain subparagraph below if spring isolators are selected in paragraph above.

1. Minimum Static Deflection:  [25 mm (1 inch)] <Insert static deflection to suit Project>.

Delete paragraph below if Project is not in a seismic zone.

D. Install seismic restraints.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to unit to allow service and maintenance.

C. Unless otherwise indicated, connect piping with unions and shutoff valves to allow units to be disconnected without draining piping.  Refer to piping system Sections for specific valve and specialty arrangements.

D. Ground equipment.

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

2. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning units and retest as specified above.

3.4 DEMONSTRATION

Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain units.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15736

SELF-CONTAINED AIR-CONDITIONING UNITS (15 TONS AND SMALLER)
15736 - 1

