Copyright 2003 AIA
GSA VERSION MASTERSPEC
12/03 (GSA 03/05)

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15775 - ELECTRIC HEATING CABLES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following electric heating cables:

1. Mineral insulated, series resistance.

2. Plastic insulated, series resistance.

3. Self-regulating, parallel resistance.

4. Constant wattage.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Radiant Heating and Cooling Units" for factory-fabricated electric heating panels for ceiling and wall applications.

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated.

1. Schedule heating capacity, length of cable, spacing, and electrical power requirement for each electric heating cable required.

B. Shop Drawings:  For electric heating cable.  Include plans, sections, details, and attachments to other work.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Ceiling suspension assembly members.

2. Method of attaching hangers to building structure.

3. Items installed in finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. Perimeter moldings.

g. <Insert item.>

Retain first paragraph below if Contractor is responsible for field quality-control testing.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For electric heating cables to include in operation and maintenance manuals.

F. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 COORDINATION

A. Coordinate layout and installation of electric heating cables and system components with other construction.

Retain subparagraph below for snow-melting cable in pavement or for radiant concrete floor heating cable.

1. Coordinate concrete, reinforcement, and formwork with requirements specified in Division 3.

Retain subparagraph below for roof-mounting heating cable.

2. Coordinate with roofing installer for installation and roof penetrations specified in Division 7 Sections.

Retain subparagraph below for freezer-frost-heave prevention.

3. Coordinate with freezer installer for cable placement in subsoil below insulation for freezer specified in Division 11 Section "Foodservice Equipment."

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period.

Verify available warranties for electric heating cable and insert number in subparagraph below.

1. Warranty Period:  [10] [15] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MINERAL-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain this Article for snow melting on pavement.

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Chromalox, Inc.; Wiegard Industrial Division; Emerson Electric Company.

2. Delta-Therm Corporation.

3. Easy Heat Inc.

4. Nelson Heat Trace.

5. Pyrotenax; a division of Tyco Thermal Controls.

6. Raychem; a division of Tyco Thermal Controls.

7. Trasor Corp.

8. Watts Radiant Inc.

9. <Insert manufacturer's name.>

B. Heating Element:  Single- or dual-conductor resistor wire.  Terminate with waterproof, factory-assembled nonheating leads with connectors at both ends.

C. Electrical Insulating Mineral:  Magnesium oxide.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

D. Cable Cover:  Copper/nickel alloy[ and high-density polyethylene outer jacket].

E. Maximum Operating Temperature:  [150 deg C (300 deg F)] <Insert temperature>.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

F. Capacities and Characteristics:

1. Maximum Heat Output:  [19.7 W/m (6 W/ft.)] [24.6 W/m (7.5 W/ft.)] <Insert heat output>.

2. Spacing:  <Insert mm (inches).>

Verify available voltages and heat-output ratings with specified manufacturer.

3. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

4. Phase:  <Insert value.>

5. Hertz:  <Insert value.>

6. Full-Load Amperes:  <Insert value.>

7. Minimum Circuit Ampacity:  <Insert value.>

8. Maximum Overcurrent Protection:  <Insert value.>

2.2 PLASTIC-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain this Article for ceiling and floor radiant heating, freezer-frost-heave prevention, pipe-mounting freeze protection, and snow and ice melting on pavement and roofs and in gutters and downspouts.  Some manufacturers limit use of this product to stone, ceramic tile, or concrete floors.

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Delta-Therm Corporation.

2. Easy Heat Inc.

3. NUHEAT.

4. Orbit Manufacturing.

5. Pyrotenax; a division of Tyco Thermal Controls.

6. Raychem; a division of Tyco Thermal Controls.

7. WarmlyYours.com Inc.

8. Watts Radiant Inc.

9. <Insert manufacturer's name.>

Retain first paragraph below if installing cable in radiant heating ceiling or floor.

B. Comply with UL 1673 and IEEE 515.1.

C. Heating Element:  Single- or dual-stranded resistor wire.  Terminate with waterproof, factory-assembled nonheating leads with connectors at both ends.

D. Electrical Insulating Jacket:  Minimum 0.10-mm (4.0-mil) Kapton with silicone jacket or Tefzel.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

E. Cable Cover:  Aluminum braid[ and silicone or Hylar outer jacket].

F. Maximum Operating Temperature:  [150 deg C (300 deg F)] <Insert temperature>.

Retain paragraph below for heating cables in factory-fabricated mats.  Indicate length and spacing of cables on Drawings.

G. Heating Cable Mats:  Factory-fabricated cable and fiberglass or plastic mesh with uniform [38-mm (1-1/2-inch)] [76-mm (3-inch)] <Insert dimension> cable spacing, in [457-mm (18-inch)] [914-mm (36-inch)] <Insert dimension> widths.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

H. Capacities and Characteristics:

1. Maximum Heat Output:  [19.7 W/m (6 W/ft.)] [24.6 W/m (7.5 W/ft.)] <Insert heat output>.

Retain subparagraph below for radiant panels.

2. Spacing:  <Insert mm (inches).>

Retain three subparagraphs below for freeze protection.

3. Piping Diameter:  <Insert DN (NPS).>

4. Number of Parallel Cables:  <Insert number.>

5. Spiral Wrap Pitch:  <Insert mm (inches).>

Verify available voltages and heat-output ratings with specified manufacturer.

6. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

7. Phase:  <Insert value.>

8. Hertz:  <Insert value.>

9. Full-Load Amperes:  <Insert value.>

10. Minimum Circuit Ampacity:  <Insert value.>

11. Maximum Overcurrent Protection:  <Insert value.>

2.3 SELF-REGULATING, PARALLEL-RESISTANCE HEATING CABLES

Retain this Article for ceiling and floor radiant heating, freezer-frost-heave prevention, pipe-mounting freeze protection, domestic hot-water-temperature maintenance, and snow and ice melting on pavement and roofs and in gutters and downspouts.

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. BH Thermal Corporation.

2. Chromalox, Inc.; Wiegard Industrial Division; Emerson Electric Company.

3. Delta-Therm Corporation.

4. Easy Heat Inc.

5. Nelson Heat Trace.

6. Pyrotenax; a division of Tyco Thermal Controls.

7. Raychem; a division of Tyco Thermal Controls.

8. Thermon Manufacturing Co.

9. Trasor Corp.

10. <Insert manufacturer's name.>

B. Heating Element:  Pair of parallel No. [16] [18] AWG, [tinned] [nickel-coated] stranded copper bus wires embedded in crosslinked conductive polymer core, which varies heat output in response to temperature along its length.  Terminate with waterproof, factory-assembled nonheating leads with connectors at one end, and seal the opposite end watertight.  Cable shall be capable of crossing over itself once without overheating.

C. Electrical Insulating Jacket:  Flame-retardant polyolefin.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

D. Cable Cover:  [Tinned-copper] [Stainless-steel] braid[, and polyolefin outer jacket with UV inhibitor].

E. Maximum Operating Temperature (Power On):  [65 deg C (150 deg F)] <Insert temperature>.

Verify temperature of circulated media in freeze-protected piping for paragraph below.

F. Maximum Exposure Temperature (Power Off):  [85 deg C (185 deg F)] <Insert temperature>.

G. Maximum Operating Temperature:  [150 deg C (300 deg F)] <Insert temperature>.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

H. Capacities and Characteristics:

1. Maximum Heat Output:  [9.8 W/m (3 W/ft.)] [16.4 W/m (5 W/ft.)] [26 W/m (8 W/ft.)] [32.8 W/m (10 W/ft.)] [39.4 W/m (12 W/ft.)] <Insert heat output>.

Retain subparagraph below for radiant panels.

2. Spacing:  <Insert mm (inches).>

Retain three subparagraphs below for freeze protection.

3. Piping Diameter:  <Insert DN (NPS).>

4. Number of Parallel Cables:  <Insert number.>

5. Spiral Wrap Pitch:  <Insert mm (inches).>

Verify available voltages and heat-output ratings with specified manufacturer.

6. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

7. Phase:  <Insert value.>

8. Hertz:  <Insert value.>

9. Full-Load Amperes:  <Insert value.>

10. Minimum Circuit Ampacity:  <Insert value.>

11. Maximum Overcurrent Protection:  <Insert value.>

2.4 CONSTANT-WATTAGE HEATING CABLES

Retain this Article for snow and ice melting on roofs and in gutters and downspouts.

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. BH Thermal Corporation.

2. Chromalox, Inc.; Wiegard Industrial Division; Emerson Electric Company.

3. Delta-Therm Corporation.

4. Easy Heat Inc.

5. Nelson Heat Trace.

6. Pyrotenax; a division of Tyco Thermal Controls.

7. Raychem; a division of Tyco Thermal Controls.

8. Thermon Manufacturing Co.

9. Trasor Corp.

10. <Insert manufacturer's name.>

B. Heating Element:  Pair of parallel No. [12] <Insert gage> AWG, [tinned] [nickel-coated] stranded copper bus wires with single-stranded resistor wire connected between bus wires.  Terminate with waterproof, factory-assembled nonheating leads with connectors at one end, and seal the opposite end watertight.

C. Electrical Insulating Jacket:  Flame-retardant fluoropolymer.

Outer jacket in first paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

D. Cable Cover:  [Tinned-copper] [Stainless-steel] braid[, and polyolefin outer jacket with UV inhibitor].

E. Maximum Operating Temperature (Power On):  [200 deg C (392 deg F)] <Insert temperature>.

If more than one electric heating cable configuration is required on Project, delete paragraph and subparagraphs below and schedule electric heating cable configurations on Drawings.

F. Capacities and Characteristics:

1. Maximum Heat Output:  [13.1 W/m (4 W/ft.)] [26 W/m (8 W/ft.)] [39.4 W/m (12 W/ft.)] <Insert heat output>.

Verify available voltages and heat-output ratings with specified manufacturer.

2. Volts:  [120] [208] [240] [277] [480] <Insert value> V.

3. Phase:  <Insert value.>

4. Hertz:  <Insert value.>

5. Full-Load Amperes:  <Insert value.>

6. Minimum Circuit Ampacity:  <Insert value.>

7. Maximum Overcurrent Protection:  <Insert value.>

2.5 CONTROLS

A. Refer to Division 15 Sections "Building Automation System" and "Sequence of Operation."

Retain paragraph above or applicable paragraphs and subparagraphs remaining in this Article for controls provided with electric heating cables.  Revise temperature ranges to suit Project.

B. Pipe-Mounting Thermostats for Freeze Protection:

1. Remote bulb unit with adjustable temperature range from [minus 1 to plus 10 deg C (30 to 50 deg F)] <Insert range>.

2. Snap action; open-on-rise, single-pole switch with minimum current rating adequate for connected cable.

3. Remote bulb on capillary, resistance temperature device, or thermistor for directly sensing pipe-wall temperature.

4. Corrosion-resistant, waterproof control enclosure.

Retain paragraph and subparagraphs below to operate electric heating cable for snow melting on pavement and roofs and in gutters.

C. Precipitation and Temperature Sensor for Snow Melting on Pavement and Roofs and in Gutters:

1. [[Native ASHRAE 135, BACnet] [LonWorks compatible] microprocessor controls specified by Division 15 Section, "Building Automation System" and “Temperature Controls”.]   [Automatic] control with manual on, automatic, and standby/reset switch.

2. Precipitation and temperature sensors shall sense the surface conditions of [pavement] [roof and gutters] and shall be programmed to energize the cable as follows:

Retain and edit desired features in first four subparagraphs below.  Verify available features with manufacturer.

a. Temperature Span:  [1 to 7 deg C (34 to 44 deg F)] <Insert range>.

b. Adjustable Delay Off Span:  [30 to 90] <Insert time> minutes.

c. Energize Cables:  Following [two] <Insert time>-minute delay if ambient temperature is below set point and precipitation is detected.

d. De-Energize Cables:  On detection of a dry surface plus time delay.

3. Corrosion-proof and waterproof enclosure suitable for outdoor mounting, for controls and precipitation and temperature sensors.

4. Minimum 30-A contactor to energize cable or close other contactors.

Consider pavement-mounting sensor for snow melting on pavement.  Freestanding sensor can be used for snow and ice melting on roofs and in gutters.

5. Precipitation sensor shall be [freestanding] [mounted in pavement].

6. Provide relay with contacts to indicate operational status, on or off, for interface with central HVAC control system workstation.

2.6 ACCESSORIES

A. Cable Installation Accessories:  Fiberglass tape, heat-conductive putty, cable ties, silicone end seals and splice kits, and installation clips all furnished by manufacturer, or as recommended in writing by manufacturer.

B. Warning Labels:  Refer to Division 15 Section "Mechanical Identification."

Retain paragraph above or paragraph and subparagraphs below.

C. Warning Tape:  Continuously printed "Electrical Tracing"; vinyl, at least 0.08 mm (3 mils) thick, and with pressure-sensitive, permanent, waterproof, self-adhesive back.

1. Width for Markers on Pipes with OD, Including Insulation, Less Than 150 mm (6 Inches):  19 mm (3/4 inch) minimum.

2. Width for Markers on Pipes with OD, Including Insulation, 150 mm (6 Inches) or Larger:  38 mm (1-1/2 inches) minimum.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine surfaces and substrates to receive electric heating cables for compliance with requirements for installation tolerances and other conditions affecting performance.

1. Ensure surfaces and pipes in contact with electric heating cables are free of burrs and sharp protrusions.

2. Ensure surfaces and substrates are level and plumb.

3. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATIONS

Applications in this Article are typical uses for each type of electric heating cable.  Consult manufacturers for other applications and for applications of other electric heating cables.

A. Install the following types of electric heating cable for the applications described:

1. Snow and Ice Melting on Pavement:  [Mineral-insulated, series-resistance] [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

2. Snow and Ice Melting on Roofs and in Gutters and Downspouts:  [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] [Constant-wattage] heating cable.

3. Freezer-Floor-Frost-Heave Prevention:  [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

3.3 INSTALLATION

A. Install electric heating cable or mats across expansion, construction, and control joints according to manufacturer's written recommendations using cable protection conduit and slack cable to allow movement without damage to cable.

B. Do not energize cables embedded in concrete or plaster until those assemblies are cured.

C. Electric Heating Cable Installation for Snow and Ice Melting on Pavement:

1. Install heating cable with heat-conductive fill materials such as asphalt or concrete, to ensure direct contact with finished radiant surfaces.

2. Install cables or mats after applying bituminous binder course to lower base; ensure that second bituminous binder course is applied to cables before pouring finish topping.

D. Electric Heating Cable Installation for Snow and Ice Melting on Roofs and in Gutters and Downspouts:  Install on roof and in gutters and downspouts with clips furnished by manufacturer that are compatible with roof, gutters, and downspouts.

E. Electric Heating Cable Installation for Freezer-Floor-Frost-Heave Prevention:  Install electric heating cable below insulation in subsoil.

F. Electric Heating Cable Installation for Freeze Protection for Piping:

1. Install electric heating cables after piping has been tested and before insulation is installed.

2. Install electric heating cables according to IEEE 515.1.

3. Install insulation over piping with electric cables according to Division 15 Section "Mechanical Insulation."

4. Install warning tape on piping insulation where piping is equipped with electric heating cables.

G. Set field-adjustable switches and circuit-breaker trip ranges.

H. Protect installed heating cables, including nonheating leads, from damage.

3.4 CONNECTIONS

A. Ground equipment according to Division 16 Section "Grounding and Bonding."

B. Connect wiring according to Division 16 Section "Conductors and Cables."

3.5 FIELD QUALITY CONTROL

A. Testing:  Perform tests after cable installation but before application of coverings such as insulation, wall or ceiling construction, or concrete.

1. Test cables for electrical continuity and insulation integrity before energizing.

2. Test cables to verify rating and power input.  Energize and measure voltage and current simultaneously.

Retain paragraph below for snow and ice melting on pavement, and freezer-frost-heave prevention.

B. Repeat tests for continuity, insulation resistance, and input power after applying finished surface on heating cables.

Retain first paragraph below for pipe-mounting freeze.
C. Repeat tests for continuity, insulation resistance, and input power after applying thermal insulation on pipe-mounting cables.

D. Remove and replace malfunctioning units and retest as specified above.

END OF SECTION 15775
ELECTRIC HEATING CABLES
15775 - 1

