Copyright 2000 AIA
GSA VERSION MASTERSPEC
9/00 (R 03/02)(GSA 03/05)

Copyright 2000 (R 03/02), The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15820 - DUCT ACCESSORIES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Backdraft dampers.

2. Relief dampers

3. Volume dampers, including balancing dampers

4. Motorized control dampers.

5. Fire dampers.

6. Ceiling fire dampers.

7. Smoke dampers.

8. Combination fire and smoke dampers.

9. Turning vanes.

10. Duct-mounting access doors.

11. Flexible connectors.

12. Flexible ducts.

13. Duct accessory hardware.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 13 Section "Fire Alarm" for duct-mounting fire and smoke detectors.

2. Division 15 Section “Noise Control Devices” for duct silencers.
3. Division 15 Section “Intake and Relief Ventilators” for louver penthouse, roof housings, and goosenecks.

4. Division 15 Section “Building Automation System” for electric and electronic damper actuators.

1.3 SUBMITTALS

A. Product Data:  For the following:

Edit list below to suit Project.

1. Backdraft dampers.

2. Relief dampers

3. Roof-mounted Air Outlets and Inlets

4. Volume dampers, including balancing dampers

5. Motorized control dampers.

6. Fire dampers.

7. Ceiling fire dampers.

8. Smoke dampers.

9. Combination fire and smoke dampers.

10. Turning vanes.

11. Duct-mounting access doors.

12. Flexible connectors.

13. Flexible ducts.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Special fittings.

2. Manual-volume damper installations.

3. Motorized-control damper installations.

4. Fire-damper, smoke-damper, and combination fire- and smoke-damper installations, including sleeves, duct-mounting access doors, and remote damper operators.

5. Security manbar installation.

Retain subparagraph below if equipment includes wiring.

6. Wiring Diagrams:  Power, signal, and control wiring.

Retain below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plans, drawn to scale and coordinating penetrations and ceiling-mounting items.  Show ceiling-mounting access panels and access doors required for access to duct accessories.

1.4 QUALITY ASSURANCE

A. Comply with NFPA 90A, "Installation of Air Conditioning and Ventilating Systems," and NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

B. Comply with AMCA 500-D, “Laboratory Methods of Testing Dampers for Rating”, and AMCA 500-L, “Laboratory Methods of Testing Louvers for Rating”

1.5 EXTRA MATERIALS

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise below to suit Project.

1. Fusible Links:  Furnish quantity equal to [10] <Insert number> percent of amount installed.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
2.2 SHEET METAL MATERIALS

See Evaluations for discussion on coatings.

A. Comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods, unless otherwise indicated.

B. Galvanized Sheet Steel:  Lock-forming quality; complying with ASTM A 653/A 653M and having [Z180 (G60)] [Z275 (G90)] coating designation; ducts shall have mill-phosphatized finish for surfaces exposed to view.

C. Stainless Steel:  ASTM A 480/A 480M.

D. Aluminum Sheets:  ASTM B 209M (ASTM B 209), alloy 3003, temper H14; with mill finish for concealed ducts and standard, 1-side bright finish for exposed ducts.

E. Extruded Aluminum:  ASTM B 221M (ASTM B 221), alloy 6063, temper T6.

F. Reinforcement Shapes and Plates:  Galvanized-steel reinforcement where installed on galvanized sheet metal ducts; compatible materials for aluminum and stainless-steel ducts.

G. Tie Rods:  Galvanized steel, 6-mm (1/4-inch) minimum diameter for lengths 900 mm (36 inches) or less; 10-mm (3/8-inch) minimum diameter for lengths longer than 900 mm (36 inches).

2.3 BACKDRAFT AND PRESSURE RELIEF  DAMPERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Air Balance, Inc.

2. American Warming and Ventilating.

3. CESCO Products.

4. Duro Dyne Corp.

5. Greenheck.

6. Penn Ventilation Company, Inc.

7. Prefco Products, Inc.

8. Ruskin Company.

9. Trox.

10. Vent Products Company, Inc.

11. <Insert manufacturer's name.>

Duplicate paragraphs below as required to specify all damper applications.

B. Outlet Dampers

1. Description:  Multiple-blade, parallel action gravity balanced, with[ center-pivoted] blades of maximum 150-mm (6-inch) width, with sealed edges, assembled in rattle-free manner with 90-degree stop, steel ball bearings, and axles; adjustment device to permit setting for varying differential static pressure.

2. Mounting: [Horizontal][Vertical][As indicated.]
3. Maximum face velocity:  [7 m/s (1500 fpm)] [7 m/s (2000 fpm)] [13 m/s (2500 fpm)].

4. Frame:  [1.3-mm- (0.052-inch-) thick, galvanized sheet steel] [1.6-mm- (0.063-inch-) thick extruded aluminum], with welded corners[ and mounting flange].

5. Blades:  [0.6-mm- (0.025-inch-) thick, roll-formed aluminum] [1.2-mm- (0.050-inch-) thick aluminum sheet] [1.68-mm- (0.070-inch-) thick aluminum sheet].

6. Blade Seals:  [Vinyl] [Neoprene].

7. Blade Axles:  [Nonferrous] [Galvanized steel] [Stainless steel].

8. Bearings:  [Synthetic ][Stainless steel ][Bronze].

9. Tie Bars and Brackets:  [Aluminum] [Galvanized steel].

10. Return Spring:  Adjustable tension.

11. Accessories:

a. Flange on [intake][ discharge][ intake and discharge].

b. <Insert accessories>

C. Inlet Dampers
1. Description:  Multiple-blade, gravity balanced, with[ center-pivoted] blades of maximum 150-mm (6-inch) width, with sealed edges, assembled in rattle-free manner with 90-degree stop, steel ball bearings, and axles; adjustment device to permit setting for varying differential static pressure.

2. Damper Design: [Parallel blade.][External inlet vane.]
3. Maximum face velocity:  [7 m/s (1500 fpm)] [7 m/s (2000 fpm)] [13 m/s (2500 fpm)] <Insert number>.

4. Maximum pressure differential:  [250 Pa (1-inch w.g.)] [750 Pa (2-inch w.g.)] [1000 Pa (4-inch w.g.)]<Insert number>.

5. Mounting: [Horizontal][Vertical][As indicated.]
6. Frame:  [1.3-mm- (0.052-inch-) thick, galvanized sheet steel] [1.6-mm- (0.063-inch-) thick extruded aluminum], with welded corners[ and mounting flange].

7. Blades:  [0.6-mm- (0.025-inch-) thick, roll-formed aluminum] [1.2-mm- (0.050-inch-) thick aluminum sheet] [1.68-mm- (0.070-inch-) thick aluminum sheet].

8. Blade Seals:  [Vinyl] [Neoprene].

9. Blade Axles:  [Nonferrous] [Galvanized steel] [Stainless steel].

10. Bearings:  [Synthetic ][Stainless steel ][Bronze].

11. Tie Bars and Brackets:  [Aluminum] [Galvanized steel].

12. Return Spring:  Adjustable tension.

13. Accessories:
a. Flange on [intake][ discharge][ intake and discharge].

b. <Insert accessories>

D. Barometric Relief Damper

1. Description:  Multiple-blade, parallel action gravity balanced, with eccentrically-pivoted blades of maximum 150-mm (6-inch) width, with sealed edges, assembled in rattle-free manner with 90-degree stop, steel ball bearings, and axles; adjustment device to permit setting for varying differential static pressure.

2. Mounting: [Horizontal][Vertical][As indicated.]
3. Maximum face velocity:  [7 m/s (1500 fpm)] [7 m/s (2000 fpm)] [13 m/s (2500 fpm)] <Insert number>.

4. Frame:  [1.3-mm- (0.052-inch-) thick, galvanized sheet steel] [1.6-mm- (0.063-inch-) thick extruded aluminum], with welded corners[ and mounting flange].

5. Blades:  [0.6-mm- (0.025-inch-) thick, roll-formed aluminum] [1.2-mm- (0.050-inch-) thick aluminum sheet].

6. Blade Seals:  [Vinyl] [Neoprene].

7. Blade Axles:  [Nonferrous] [Galvanized steel].

8. Bearings:  [Synthetic ][Stainless steel ][Bronze].

9. Tie Bars and Brackets:  [Aluminum] [Galvanized steel].

10. Return Spring:  Adjustable tension.

11. Accessories: 
a. Flange on intake.

b. <Insert accessories>

2.4 MANUAL VOLUME DAMPERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Air Balance, Inc.

2. American Warming and Ventilating.

3. Flexmaster U.S.A., Inc.

4. McGill AirFlow Corporation.

5. METALAIRE, Inc.

6. Nailor Industries Inc.

7. Penn Ventilation Company, Inc.

8. Ruskin Company.

9. Vent Products Company, Inc.

10. <Insert manufacturer's name.>

Show required air-volume-control devices on Drawings.  Identify each as standard, low-leakage, or high-performance volume-control damper.

B. General Description:  Factory fabricated, with required hardware and accessories.  Stiffen damper blades for stability.  Include locking device to hold single-blade dampers in a fixed position without vibration.  Friction locks not permitted.  Close duct penetrations for damper components to seal duct consistent with pressure class.

1. Pressure Classes of 750 Pa (3-Inch wg) or Higher:  End bearings or other seals for ducts with axels full length of damper blades and bearings at both ends of operating shaft.

C. Balancing Dampers:  Multiple- or single-blade, parallel- or opposed-blade design as indicated, standard leakage rating,[ with linkage outside air stream,] and suitable for horizontal or vertical applications.

Select steel blades for steel frames, aluminum blades for aluminum frames.  If retaining more than one, indicate location of each on Drawings.

1. Steel Frames:  Hat-shaped, [galvanized] [stainless] sheet steel channels, minimum of 1.62 mm (0.064 inch) thick, with mitered and welded corners; frames with flanges for attaching to walls and flangeless frames for installing in ducts.

2. Roll-Formed Steel Blades:  1.62-mm- (0.064-inch-) thick, [galvanized] [stainless] sheet steel.

3. Aluminum Frames:  Hat-shaped, 2.5-mm- (0.10-inch-) thick, aluminum sheet channels; frames with flanges for attaching to walls; and flangeless frames for installing in ducts.

4. Roll-Formed Aluminum Blades:  2.5-mm- (0.10-inch-) thick aluminum sheet.

5. Extruded-Aluminum Blades:  1.2-mm- (0.050-inch-) thick extruded aluminum.

6. Blade Axles:  [Galvanized steel] [Stainless steel] [Nonferrous].

7. Bearings:  [Oil-impregnated bronze] [Molded synthetic] [Stainless-steel sleeve].

8. Tie Bars and Brackets:  Aluminum.

D. Low-Leakage Volume Dampers:  [Multiple-][ or single-]blade, [parallel-][ or ][opposed-blade ]design, low-leakage rating,[ with linkage outside air stream,] and suitable for horizontal or vertical applications.

Select steel blades for steel frames, aluminum blades for aluminum frames.  If retaining more than one, indicate location of each on Drawings.  Damper blade should be a minimum of one thickness size heavier than the duct.

1. Steel Frames:  [Hat] [U] [Angle]-shaped, [galvanized] [stainless] sheet steel (50-mm-) (2-inch) wide channels, minimum of [1.62-mm- (0.063-inch-)][(3.175-mm-) (0.125-inch-)] thick, with mitered and welded corners; frames with flanges where indicated for attaching to walls and flangeless frames where indicated for installing in ducts.

2. Provide inside end bearings.

3. Provide locking quadrants with wing nuts.

4. Roll-Formed Steel Blades:  1.62-mm- (0.064-inch-) thick, [galvanized] [stainless] sheet steel.

5. Roll-Formed Aluminum Blades:  2.5-mm- (0.10-inch-) thick aluminum sheet.

6. Extruded-Aluminum Blades:  1.2-mm- (0.050-inch-) thick extruded aluminum.

7. Blade Quantity:

a. Single blades up to 300-mm- (12 inch) damper width.

b. Multi-blades for damper widths 300-mm- (12 inch) and larger.

8. Blade Axles:  [Galvanized steel] [Stainless steel].
9. Bearings:  [Oil-impregnated bronze] [Stainless-steel sleeve] thrust or ball.

10. Blade Seals:  [Vinyl] [Neoprene].

11. Jamb Seals:  Cambered [stainless steel] [aluminum].

12. Tie Bars and Brackets:  [Galvanized steel].
13. Extensions:  Locking-type damper operators shall have extensions where necessary  Operators shall indicate damper position.
E. Jackshaft:  25-mm- (1-inch-) diameter, galvanized-steel pipe rotating within pipe-bearing assembly mounted on supports at each mullion and at each end of multiple-damper assemblies.

1. Length and Number of Mountings:  Appropriate to connect linkage of each damper in multiple-damper assembly.

F. Damper Hardware:  Zinc-plated, die-cast core with dial and handle made of 2.4-mm- (3/32-inch-) thick zinc-plated steel, and a 19-mm (3/4-inch) hexagon locking nut.  Include center hole to suit damper operating-rod size.  Include elevated platform for insulated duct mounting.

2.5 MOTORIZED CONTROL DAMPERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Air Balance, Inc.

2. American Warming and Ventilating.

3. CESCO Products.

4. Duro Dyne Corp.

5. Greenheck.

6. McGill AirFlow Corporation.

7. METALAIRE, Inc.

8. Nailor Industries Inc.

9. Penn Ventilation Company, Inc.

10. Ruskin Company.

11. Vent Products Company, Inc.

12. <Insert manufacturer's name.>

B. General Description:  AMCA-rated, [parallel] [opposed]-blade design; minimum of 2.8-mm- (0.1084-inch-) thick, galvanized-steel frames with holes for duct mounting; minimum of 1.61-mm- (0.0635-inch-) thick, galvanized-steel damper blades with maximum blade width of 203 mm (8 inches).

1. Secure blades to 13-mm- (1/2-inch-) diameter, zinc-plated axles using zinc-plated hardware, with nylon blade bearings, blade-linkage hardware of zinc-plated steel and brass, ends sealed against spring-stainless-steel blade bearings, and thrust bearings at each end of every blade.

2. Operating Temperature Range:  From minus 40 to plus 93 deg C (minus 40 to plus 200 deg F).

Retain first option below for standard applications and second option for low-leakage applications.

3. Provide [closed-cell neoprene edging] [parallel- or opposed-blade design with inflatable seal blade edging, or replaceable rubber seals, rated for leakage at less than 51 L/s per sq. m (10 cfm per sq. ft.) of damper area, at differential pressure of 995 Pa (4-inch wg) when damper is being held by torque of 5.6 N x m (50 in. x lbf); when tested according to AMCA 500D].

2.6 FIRE DAMPERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Air Balance, Inc.

2. CESCO Products.

3. Greenheck.

4. McGill AirFlow Corporation.

5. METALAIRE, Inc.

6. Nailor Industries Inc.

7. Penn Ventilation Company, Inc.

8. Prefco Products, Inc.

9. Ruskin Company.

10. Vent Products Company, Inc.

11. Ward Industries, Inc.

12. <Insert manufacturer's name.>

Indicate damper designations on Drawings to match schedule.

B. Fire dampers shall be labeled according to UL 555.

C. Fire Rating:  [1-1/2] [3] hours.

Type 304, stainless-steel dampers are also available for corrosive atmospheres.

D. Frame:  [Curtain type with blades inside air stream] [Curtain type with blades outside air stream] [Multiple-blade type]; fabricated with roll-formed, 0.85-mm- (0.034-inch-) thick galvanized steel; with mitered and interlocking corners.

E. Mounting Sleeve:  Factory- or field-installed, galvanized sheet steel.

1. Minimum Thickness:  1.3 or 3.5 mm (0.052 or 0.138 inch) thick as indicated and of length to suit application.

2. Exceptions:  Omit sleeve where damper frame width permits direct attachment of perimeter mounting angles on each side of wall or floor, and thickness of damper frame complies with sleeve requirements.

F. Mounting Orientation:  Vertical or horizontal as indicated.

G. Blades:  Roll-formed, interlocking, 0.85-mm- (0.034-inch-) thick, galvanized sheet steel.  In place of interlocking blades, use full-length, 0.85-mm- (0.034-inch-) thick, galvanized-steel blade connectors.

Not all manufacturers use blade locks for horizontal units.

H. Horizontal Dampers:  Include blade lock and stainless-steel closure spring.

Retain one of two options below for temperature-rated links to suit application requirements.  Second option is standard.

I. Fusible Links:  Replaceable, [74 deg C (165 deg F)] [100 deg C (212 deg F)] rated.

2.7 CEILING FIRE DAMPERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Air Balance, Inc.

2. CESCO Products.

3. Greenheck.

4. McGill AirFlow Corporation.

5. METALAIRE, Inc.

6. Nailor Industries Inc.

7. Penn Ventilation Company, Inc.

8. Prefco Products, Inc.

9. Ruskin Company.

10. Vent Products Company, Inc.

11. Ward Industries, Inc.

12. <Insert manufacturer's name.>

B. General Description:  Labeled according to UL 555C; comply with construction details for tested floor- and roof-ceiling assemblies as indicated in UL's "Fire Resistance Directory."

C. Frame:  Galvanized sheet steel, round or rectangular, style to suit ceiling construction.

D. Blades:  Galvanized sheet steel with refractory insulation.

Retain one of three options below for temperature-rated links to suit application requirements.  Second option is standard.

E. Fusible Links:  Replaceable, [74 deg C (165 deg F)] [100 deg C (212 deg F)] [141 deg C (285 deg F)] rated.

2.8 [SMOKE] [COMBINATION FIRE AND SMOKE] DAMPERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Air Balance, Inc.

2. CESCO Products.

3. Greenheck.

4. Nailor Industries Inc.

5. Penn Ventilation Company, Inc.

6. Ruskin Company.

7. <Insert manufacturer's name.>

Available smoke and combination fire and smoke dampers include automatic-reopening types and types with electrothermal links that require link replacement after activation.  Manufacturers offer additional features for engineered smoke-control system dampers.

B. Smoke Dampers:  Labeled according to UL 555S.  

C. Combination Smoke and Fire Dampers:  Labeled according to UL 555S and UL 555 for 1-1/2-hour rating.

Retain one of two options in paragraph below for temperature-rated links to suit application requirements.  Second option is standard.

D. Fusible Links:  Replaceable, [74 deg C (165 deg F)] [100 deg C (212 deg F)] rated.

E. Frame and Blades:  1.62-mm- (0.064-inch-) thick, galvanized sheet steel.

F. Mounting Sleeve:  Factory-installed, 1.3-mm- (0.052-inch-) thick, galvanized sheet steel; length to suit wall or floor application.

Retain paragraph and subparagraphs below if damper actuators are part of smoke-damper assembly and are not specified in Division 15 Section "Building Automation System."

G. Damper Motors:  Modulating and two-position action.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add paragraphs below to suit Project.

1. Comply with requirements in Division 15 Section "Motors."

2. Permanent-Split-Capacitor or Shaded-Pole Motors:  With oil-immersed and sealed gear trains.

3. Spring-Return Motors:  Equip with an integral spiral-spring mechanism where indicated.  Enclose entire spring mechanism in a removable housing designed for service or adjustments.  Size for running torque rating of 17 N x m (150 in. x lbf) and breakaway torque rating of 17 N x m (150 in. x lbf).

4. Outdoor Motors and Motors in Outside-Air Intakes:  Equip with O-ring gaskets designed to make motors weatherproof.  Equip motors with internal heaters to permit normal operation at minus 40 deg C (minus 40 deg F).

5. Nonspring-Return Motors:  For dampers larger than 2.3 sq. m (25 sq. ft.), size motor for running torque rating of 17 N x m (150 in. x lbf) and breakaway torque rating of 34 N x m (300 in. x lbf).

6. Electrical Connection:  115 V, single phase, 60 Hz.

2.9 TURNING VANES

A. Fabricate to comply with SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for vanes and vane runners.  Vane runners shall automatically align vanes.

Retain first paragraph and subparagraphs below for manufactured turning vanes.  Delete for turning vanes fabricated by Installer.

B. Manufactured Turning Vanes:  Fabricate 38-mm- (1-1/2-inch-) wide, [single] [double]-vane, curved blades of galvanized sheet steel set 19 mm (3/4 inch) o.c.; support with bars perpendicular to blades set 50 mm (2 inches) o.c.; and set into vane runners suitable for duct mounting.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Ductmate Industries, Inc.

b. Duro Dyne Corp.

c. METALAIRE, Inc.

d. Ward Industries, Inc.

e. <Insert manufacturer's name.>

C. Acoustic Turning Vanes:  Fabricate airfoil-shaped aluminum extrusions with perforated faces and fibrous-glass fill.

2.10 REMOTE OPERATORS

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. Ventfabrics, Inc.

b. Young Regulator Co.

c. <Insert manufacturer's name.>

2. General Description: Cable system designed for remote manual damper adjustment.

3. Tubing: Brass
4. Cable: Stainless steel
5. Wall Box Mounting: [Recessed, 19 mm deep] [Recessed, 50 mm deep] [ Surface]
6. Cover Plate Material:  [Steel][ Stainless steel].

2.11 DUCT-MOUNTING ACCESS DOORS

A. General Description:  Fabricate doors airtight and suitable for duct pressure class.

B. Door:  Double wall, duct mounting, and rectangular; fabricated of galvanized sheet metal with  insulation fill..  Include vision panel where indicated.  Include piano hinge and cam latches.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. American Warming and Ventilating.

b. CESCO Products.

c. Ductmate Industries, Inc.

d. Flexmaster U.S.A., Inc.

e. Greenheck.

f. McGill AirFlow Corporation.

g. Nailor Industries Inc.

h. Ventfabrics, Inc.

i. Ward Industries, Inc.

j. <Insert manufacturer's name.>

2. Frame:  Galvanized sheet steel, with bend-over tabs and foam gaskets.

3. Provide number of hinges and locks as follows:

a. Less Than 300 mm (12 Inches) Square:  Secure with two sash locks.

b. Up to 450 mm (18 Inches) Square:  Two hinges and two sash locks.

c. Up to 600 by 1200 mm (24 by 48 Inches):  Three hinges and two compression latches[ with outside and inside handles].

d. Sizes 600 by 1200 mm (24 by 48 Inches) and Larger:  One additional hinge.

C. Pressure Relief Access Door:  Double wall and duct mounting; fabricated of galvanized sheet metal[ with insulation fill and thickness] for duct pressure class with insulation fill.  Include vision panel where indicated, latches, and retaining chain.

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
a. American Warming and Ventilating.

b. CESCO Products.

c. Ductmate Industries, Inc.

d. Greenheck.

e. KEES, Inc.

f. McGill AirFlow Corporation.

g. Nexus PDQ.

h. <Insert manufacturer's name.>

2. Frame:  Galvanized sheet steel, with bend-over tabs and foam gaskets.

D. Seal around frame attachment to duct and door to frame with neoprene or foam rubber.

E. Insulation:  [25-mm- (1-inch-) thick] [Thickness to match duct insulation], fibrous-glass or polystyrene-foam board.

2.12 FLEXIBLE CONNECTORS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Ductmate Industries, Inc.

2. Duro Dyne Corp.

3. Ventfabrics, Inc.

4. Ward Industries, Inc.

5. <Insert manufacturer's name.>

B. General Description:  Flame-retardant or noncombustible fabrics, coatings, and adhesives complying with UL 181, Class 1.

Coordinate five paragraphs and associated subparagraphs below with Part 3 "Application and Installation" Article.  Delete first paragraph if Contractor is allowed to shop fabricate metal-edge attachment or if metal-edge attachment is not necessary.

C. Metal-Edged Connectors:  Factory fabricated with a fabric strip [89 mm (3-1/2 inches)] [146 mm (5-3/4 inches)] wide attached to two strips of 70-mm- (2-3/4-inch-) wide, 0.7-mm- (0.028-inch-) thick, galvanized sheet steel or 0.8-mm- (0.032-inch-) thick aluminum sheets.  Select metal compatible with ducts.

Connector fabric in paragraph below is not suitable for exposure to sun, weather, or corrosive environments.  It is suitable for system temperatures from minus 10 to plus 200 deg F (minus 23 to plus 93 deg C).

D. Indoor System, Flexible Connector Fabric:  Glass fabric double coated with neoprene.

1. Minimum Weight:  880 g/sq. m (26 oz./sq. yd.).

2. Tensile Strength:  84 N/mm (480 lbf/inch) in the warp and 63 N/mm (360 lbf/inch) in the filling.

3. Service Temperature:  Minus 40 to plus 93 deg C (Minus 40 to plus 200 deg F).

Connector fabric in paragraph below is suitable for exposure to sun, weather, and system temperatures from minus 10 to plus 250 deg F (minus 23 to plus 121 deg C).

E. Outdoor System, Flexible Connector Fabric:  Glass fabric double coated with weatherproof, synthetic rubber resistant to UV rays and ozone.

1. Minimum Weight:  810 g/sq. m (24 oz./sq. yd.).

2. Tensile Strength:  93 N/mm (530 lbf/inch) in the warp and 77 N/mm (440 lbf/inch) in the filling.

3. Service Temperature:  Minus 45 to plus 121 deg C (Minus 50 to plus 250 deg F).

Connectors in paragraph below are suitable for system temperatures from minus 25 to plus 500 deg F (minus 32 to plus 260 deg C).

F. High-Temperature System, Flexible Connectors:  Glass fabric coated with silicone rubber.

1. Minimum Weight:  542 g/sq. m (16 oz./sq. yd.).

2. Tensile Strength:  50 N/mm (285 lbf/inch) in the warp and 32 N/mm (185 lbf/inch) in the filling.

3. Service Temperature:  Minus 55 to plus 260 deg C (Minus 67 to plus 500 deg F).

Connectors in paragraph below are suitable for systems handling corrosive gases with temperatures from minus 20 to plus 500 deg F (minus 29 to plus 260 deg C).

G. High-Corrosive-Environment System, Flexible Connectors:  Glass fabric with chemical-resistant coating.

1. Minimum Weight:  474 g/sq. m (14 oz./sq. yd.).

2. Tensile Strength:  79 N/mm (450 lbf/inch) in the warp and 60 N/mm (340 lbf/inch) in the filling.

3. Service Temperature:  Minus 55 to plus 260 deg C (Minus 67 to plus 500 deg F).

2.13 FLEXIBLE DUCTS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
1. Flexmaster U.S.A., Inc.

2. Hart & Cooley, Inc.

3. McGill AirFlow Corporation.

4. <Insert manufacturer's name.>
Retain one of first five paragraphs and associated subparagraphs below for insulated flexible ducts.

B. Insulated-Duct Connectors:  UL 181, Class 1, 2-ply vinyl film supported by helically wound, spring-steel wire; fibrous-glass insulation; [polyethylene] [aluminized] vapor barrier film.

1. Pressure Rating:  2500 Pa (10-inch wg) positive and 250 Pa (1.0-inch wg) negative.

2. Maximum Air Velocity:  20.3 m/s (4000 fpm).

3. Temperature Range:  Minus 23 to plus 71 deg C (Minus 10 to plus 160 deg F).

C. Insulated-Duct Connectors:  UL 181, Class 1, black polymer film supported by helically wound, spring-steel wire; fibrous-glass insulation; [polyethylene] [aluminized] vapor barrier film.

1. Pressure Rating:  1000 Pa (4-inch wg) positive and 125 Pa (0.5-inch wg) negative.

2. Maximum Air Velocity:  20.3 m/s (4000 fpm).

3. Temperature Range:  Minus 28 to plus 79 deg C (Minus 20 to plus 175 deg F).

D. Insulated-Duct Connectors:  UL 181, Class 1, multiple layers of aluminum laminate supported by helically wound, spring-steel wire; fibrous-glass insulation; [polyethylene] [aluminized] vapor barrier film.

1. Pressure Rating:  2500 Pa (10-inch wg) positive and 250 Pa (1.0-inch wg) negative.

2. Maximum Air Velocity:  20.3 m/s (4000 fpm).

3. Temperature Range:  Minus 28 to plus 99 deg C (Minus 20 to plus 210 deg F).

E. Insulated-Duct Connectors:  UL 181, Class 1, aluminum laminate and polyester film with latex adhesive supported by helically wound, spring-steel wire; fibrous-glass insulation; [polyethylene] [aluminized] vapor barrier film.

1. Pressure Rating:  2500 Pa (10-inch wg) positive and 250 Pa (1.0-inch wg) negative.

2. Maximum Air Velocity:  20.3 m/s (4000 fpm).

3. Temperature Range:  Minus 28 to plus 99 deg C (Minus 20 to plus 210 deg F).

F. Insulated-Duct Connectors:  UL 181, Class 0, interlocking spiral of aluminum foil; fibrous-glass insulation; [polyethylene] [aluminized] vapor barrier film.

1. Pressure Rating:  2280 Pa (8-inch wg) positive or negative.

2. Maximum Air Velocity:  25.4 m/s (5000 fpm).

3. Temperature Range:  Minus 28 to plus 121 deg C (Minus 20 to plus 250 deg F).

G. Flexible Duct Clamps:  [Stainless-steel band with cadmium-plated hex screw to tighten band with a worm-gear action] [Nylon strap], in sizes 75 to 450 mm (3 through 18 inches) to suit duct size.

2.14 DUCT ACCESSORY HARDWARE

A. Instrument Test Holes:  Cast iron or cast aluminum to suit duct material, including screw cap and gasket.  Size to allow insertion of pitot tube and other testing instruments and of length to suit duct insulation thickness.

B. Adhesives:  High strength, quick setting, neoprene based, waterproof, and resistant to gasoline and grease.

PART 3 -  EXECUTION

3.1 APPLICATION AND INSTALLATION

A. Install duct accessories according to applicable details in SMACNA's "HVAC Duct Construction Standards--Metal and Flexible" for metal.

B. Provide duct accessories of materials suited to duct materials; use galvanized-steel accessories in galvanized-steel and fibrous-glass ducts, stainless-steel accessories in stainless-steel ducts, and aluminum accessories in aluminum ducts.

C. Install backdraft dampers on exhaust fans or exhaust ducts nearest to outside and where indicated.

D. Install volume dampers in ducts.
E. Provide balancing dampers at points on supply, return, and exhaust systems where branches lead from larger ducts as required for air balancing.  Install at a minimum of two duct widths from branch takeoff.

F. Install remote damper operators in accordance with manufacturer’s instructions.

G. Provide test holes at fan inlets and outlets and elsewhere as indicated.

H. Install fire and smoke dampers, with fusible links, according to manufacturer's UL-approved written instructions.

I. Install duct silencers [independent of ducts with flexible duct connectors, lagged with loaded vinyl sheet on inlets and outlets] [rigidly to ducts].

J. Provide security manbars [as detailed ]at locations indicated.  Construct manbars from 4.18 mm (0.164inch) steel sleeve, continuously welded at all joints and 0.5-in diameter steel bars 150 mm (6-inches) on center in each direction in center of sleeve.  Weld each bar to steel sleeve and each crossing bar.  Weld 63 by 63 by 6 mm (2.5-inch by 2.5-inch by 25-inch) steel angle to four sides and both ends of sleeve.  Connect manbars to ducts with flexible connections.  Provide 300 by 300 mm (12 by 12-inch) hinged access panel with cam lock in duct each side of sleeve.
K. Install duct access doors to allow for inspecting, adjusting, and maintaining accessories and terminal units as follows:

1. On both sides of duct coils.

2. Downstream from volume dampers[, turning vanes,] and equipment.

3. Adjacent to fire or smoke dampers, providing access to reset or reinstall fusible links.

4. To interior of ducts for cleaning; before and after each change in direction, at maximum 15-m (50-foot) spacing.

5. On sides of ducts where adequate clearance is available.

Sizes below are from one manufacturer's literature.  SMACNA lists only three sizes, 12 by 12 inches (300 by 300 mm), 16 by 20 inches (400 by 500 mm), and 24 by 24 inches (600 by 600 mm), but makes no recommendations for applications.

L. Install the following sizes for duct-mounting, rectangular access doors:

1. One-Hand or Inspection Access:  200 by 125 mm (8 by 5 inches).

2. Two-Hand Access:  300 by 150 mm (12 by 6 inches).

3. Head and Hand Access:  460 by 250 mm (18 by 10 inches).

4. Head and Shoulders Access:  530 by 355 mm (21 by 14 inches).

5. Body Access:  635 by 355 mm (25 by 14 inches).

6. Body Plus Ladder Access:  635 by 430 mm (25 by 17 inches).

Sizes below are from one manufacturer's literature.

M. Install the following sizes for duct-mounting, round access doors:

1. One-Hand or Inspection Access:  200 mm (8 inches) in diameter.

2. Two-Hand Access:  250 mm (10 inches) in diameter.

3. Head and Hand Access:  300 mm (12 inches) in diameter.

4. Head and Shoulders Access:  460 mm (18 inches) in diameter.

5. Body Access:  600 mm (24 inches) in diameter.

Sizes below are from one manufacturer's literature.

N. Install the following sizes for duct-mounting, pressure relief access doors:

1. One-Hand or Inspection Access:  [125 mm (5 inches)] [175 mm (7 inches)] in diameter.

2. Two-Hand Access:  250 mm (10 inches) in diameter.

3. Head and Hand Access:  330 mm (13 inches) in diameter.

4. Head and Shoulders Access:  480 mm (19 inches) in diameter.

Coordinate first paragraph below with Division 15 Section "Mechanical Identification."

O. Label access doors according to Division 15 Section "Mechanical Identification."

P. Install flexible connectors immediately adjacent to equipment in ducts associated with fans and motorized equipment supported by vibration isolators.

Q. For fans developing static pressures of 1250 Pa (5-inch wg) and higher, cover flexible connectors with loaded vinyl sheet held in place with metal straps.

R. Connect terminal units to supply ducts[ directly or] with maximum 300-mm (12-inch) lengths of flexible duct.  Do not use flexible ducts to change directions.  Install with a maximum of two minor bends.
S. Connect diffusers or light troffer boots to low pressure ducts[ directly or] with maximum 1500-mm (60-inch) lengths of flexible duct clamped or strapped in place.

T. Connect flexible ducts to metal ducts with [draw bands] [adhesive plus sheet metal screws].

U. Install duct test holes where required for testing and balancing purposes.

3.2 ADJUSTING

A. Adjust duct accessories for proper settings.

B. Adjust fire and smoke dampers for proper action.

C. Adjust relief dampers to maintain a differential pressure of 0.05 inch w.g.
D. Final positioning of manual-volume dampers is specified in Division 15 Section "Testing, Adjusting, and Balancing."

END OF SECTION 15820
DUCT ACCESSORIES
15820 - 1

