Copyright 2002 AIA
GSA VERSION MASTERSPEC
09/02 (GSA 03/05)

Copyright 2002, The American Institute of Architects (AIA)

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15834 - AIR CURTAINS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.
PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes air curtains [with] [hot-water heat] [steam heat] [electric heat] [gas-fired heater].

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each unit.

Retain first paragraph and subparagraphs below if products are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Shop Drawings:  Signed and sealed by a qualified professional engineer.

1. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints.

2. Include plans, elevations, sections, details, and attachments to other work.

3. Wiring Diagrams:  Power, signal, and control wiring.

C. Coordination Drawings:  Plans and details drawn to scale and coordinating penetrations of exterior walls.

D. Samples for Initial Selection:  For units with factory-applied color finishes.

Delete paragraph above if colors are preselected and specified or scheduled.

E. Operation and Maintenance Data:  For air curtains to include in maintenance manuals.

F. Warranties:  Special warranties specified in this Section.

1.4 QUALITY ASSURANCE

Delete paragraph below if Contractor is not required to engage the services of a qualified professional engineer in "Submittals" Article.

A. Professional Engineer Qualifications:  A professional engineer who is legally qualified to practice in jurisdiction where Project is located and who is experienced in providing engineering services of the kind indicated.  Engineering services are defined as those performed for installations of air curtains that are similar to those indicated for this Project in material, design, and extent.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

B. Product Options:  Drawings indicate size, profiles, and dimensional requirements of air curtains and are based on the specific product indicated.  Refer to Division 1 Section "Product Requirements."

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Verify availability of certification below; not all manufacturers use AMCA certification for fan performance.

D. Comply with AMCA 220, "Test Methods for Air Curtain Units," for airflow, outlet velocity, and power consumption.

Verify availability of certification below; not all manufacturers certify coils.

E. Comply with ARI 410, "Forced-Circulation Air-Cooling and Air-Heating Coils," for components, construction, and rating.

1. Certify coils according to ARI 410.

Delete paragraph below if not applicable to Project.

F. Comply with NSF 37, "Air Curtains for Entranceways in Food and Food Service Establishments."

G. CSA Compliance:  CSA label for gas-fired units.

1.5 COORDINATION

Edit this Article to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of air curtains and suspension system components with other construction, including light fixtures, fire-suppression-system components, and partition assemblies.

B. Coordinate installation of wall penetrations and louvers.  These items are specified in Division 10 Section "Louvers and Vents."

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

Not all manufacturers provide five-year warranty period.  Revise first subparagraph below to suit Project.

1. Warranty Period (Nonheating Units):  [Five years] [Two years] [One year] <Insert period>.

2. Warranty Period (Water or Steam Heating Units):  [Five years] [Two years] [One year] <Insert period>.

3. Warranty Period (Gas Heating Units):  [One year] <Insert period>.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below, before construction begins, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraph below to suit Project.

1. Furnish one set of filters and fan belts for each unit.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
The purpose of listing manufacturers is to inform contractors of manufacturers with the capacity to provide the product(s) specified.  Long lists should be edited to a modest length representing general geographical availability.
B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Air Economy Corporation.

2. Berner International Corp.

3. Biddle Air Systems Limited.

4. Cambridge Engineering, Inc.

5. Disco Engineering, Inc.

6. Fantech.

7. KING.

8. Loren Cook Company.

9. Marley Engineered Products.

10. Mars Air Products; Dynaforce Division.

11. Mars Air Products; Mars Air Door Division.

12. MesTec AG; L. J. Wing Division.

13. Miniveil Air Systems.

14. TMI Inc.

15. TMI Inc.; Curtron Products Division.

16. <Insert manufacturer's name.>

2.2 MATERIALS

Retain one of first four paragraphs and associated subparagraphs below.

A. Housing Materials:  Galvanized steel with electrostatically applied epoxy enamel finish over powdered mirror.

B. Housing Materials:  One-piece, molded, high-impact, white polymer material.

C. Housing Materials:  Heavy-gage, electroplated-zinc steel with welded construction and polyester-coated finish.

D. Housing Materials:  Heavy-gage, aluminum construction.

1. Anodized Finish:  Match finish and color of adjacent architectural metals.  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

2. Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain finishes in subparagraphs below to suit Project.  If retaining more than one, indicate location of each on Drawings or by inserts.  Revise mechanical finish if custom finish is required and availability is verified.

Below is standard finish with many manufacturers; heavy-anodized finish may be available and required.  Verify availability with manufacturers selected.

a. Class II, Clear Anodic Finish:  AA-M12C22A31 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class II, clear coating 0.010 mm or thicker) complying with AAMA 611.

b. Class II, Color Anodic Finish:  AA-M12C22A32/A34 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte; Anodic Coating:  Architectural Class II, integrally colored or electrolytically deposited color coating 0.010 mm or thicker).

Retain subparagraph below with any of four paragraphs above.

3. Mounting Brackets:  Steel, for [wall] [ceiling] mounting.

E. Intake Louvers:  Integral part of the housing, mechanically field adjustable and capable of reducing air-outlet velocity by [60] <Insert number> percent with louver in totally closed position.

F. Discharge Nozzle:  Integral part of the housing, containing adjustable air-directional vanes with [40] [20] [15] <Insert number>-degree sweep front to back.

2.3 FANS

A. Fans:  [Galvanized steel,] [Painted steel,] [Aluminum,] [Centrifugal, forward curved, double width, double inlet;] [Vane axial,] statically and dynamically balanced.

B. Fan Drives:  [Direct] [Belt, equipped with belt guards and adjustable sheaves and pulleys for adjusting air-outlet velocity].

2.4 MOTORS

A. Motor Type:  [Two speed] [Multispeed], resiliently mounted, continuous duty, [totally enclosed, air over] [totally enclosed, fan cooled] [open, dripproof] [explosion proof] [, with integral thermal-overload protection].

B. Bearings:  Permanently sealed, lifetime, prelubricated, ball bearings.

C. Disconnect:  Internal power cord with plug and receptacle.

2.5 WATER COILS

Retain one of three descriptions in first paragraph below.

A. Description:  [Continuous-circuit] [Self-draining] [Cleanable] coil.

B. Piping Connections:  Threaded on [same end] [opposite ends].

C. Tubes:  Copper, complying with ASTM B 75M (ASTM B 75).

1. Tube Diameter:  15.9 mm (0.625 inch).

Delete fin spacing in first paragraph below if in schedule.

D. Fins:  [Aluminum] [Copper] with fin spacing [4.23 mm (0.167 inch)] [3.18 mm (0.125 inch)] [2.31 mm (0.091 inch)] [1.80 mm (0.071 inch)] [1.70 mm (0.067 inch)] [1.42 mm (0.056 inch)] [0.19 mm (0.0075 inch)].

E. Fin and Tube Joint:  [Mechanical bond] [Silver brazed].

Retain one of four options in first paragraph below.

F. Headers:  [Cast iron with drain and air vent tappings] [Cast iron with cleaning plugs, and drain and air vent tappings] [Seamless copper tube with brazed joints, prime coated] [Fabricated steel with brazed joints, prime coated].

G. Frames:  Galvanized-steel channel frame, [1.3 mm (0.052 inch)] [1.6 mm (0.064 inch)] [2.0 mm (0.079 inch)] [1.59 mm (0.0625 inch)].

H. Ratings:  According to ASHRAE 33.

Pressure/temperature ratings in subparagraph below are standard for most copper-tube coils.  Other materials have different ratings; edit to suit Project.

1. Working-Pressure Ratings:  1380 kPa (200 psig), 163 deg C (325 deg F).

I. Source Quality Control:  Test to 2070 kPa (300 psig) and to 1380 kPa (200 psig) underwater.

2.6 STEAM COILS

Single-tube coil is also available.  Specify same-end connections if freeze protection is required.

A. Description:  Distribution header coil, with threaded steam supply and condensate connections.

Retain one connection in subparagraph below.

1. Connections:  [Same end] [Opposite ends] [Steam supply on both ends; condensate on one end].

B. Tubes:  Copper, complying with ASTM B 75M (ASTM B 75).

1. Tube Diameter:  15.9 mm (0.625 inch).

Delete fin spacing in first paragraph below if in schedule.

C. Fins:  [Aluminum] [Copper] with fin spacing [4.23 mm (0.167 inch)] [3.18 mm (0.125 inch)] [2.31 mm (0.091 inch)] [1.80 mm (0.071 inch)] [1.70 mm (0.067 inch)] [1.42 mm (0.056 inch)] [0.19 mm (0.0075 inch)].

D. Fin and Tube Joint:  [Mechanical bond] [Silver brazed].

Retain one of four options in first paragraph below.

E. Headers:  [Cast iron with drain and air vent tappings] [Cast iron with cleaning plugs, and drain and air vent tappings] [Seamless copper tube with brazed joints, prime coated] [Fabricated steel with brazed joints, prime coated].

F. Frames:  Galvanized-steel channel frame, [1.3 mm (0.052 inch)] [1.6 mm (0.064 inch)] [2.0 mm (0.079 inch)] [1.59 mm (0.0625 inch)].

G. Ratings:  According to ASHRAE 33.

Pressure/temperature ratings in subparagraph below are standard for most copper-tube coils.  Other materials have different ratings; edit to suit Project.

1. Working-Pressure Ratings:  690 kPa (100 psig), 205 deg C (400 deg F).

H. Source Quality Control:  Test to 2070 kPa (300 psig) and to 1380 kPa (200 psig) underwater.

2.7 ELECTRIC HEATING COILS

A. Coil Assembly:  Comply with UL 1995.

B. Frame:  Galvanized-steel frame.

C. Heating Elements:  [Coiled resistance wire of 80 percent nickel and 20 percent chromium; surrounded by compacted magnesium-oxide powder in tubular-steel sheath; with spiral-wound, copper-plated, steel fins continuously brazed to sheath] [Open-coil resistance wire of 80 percent nickel and 20 percent chromium, supported and insulated by floating ceramic bushings recessed into casing openings, fastened to supporting brackets, and mounted in galvanized-steel frame].

D. Overtemperature Protection:  Disk-type, automatically reset, thermal-cutout, safety device; serviceable through terminal box without removing heater from duct or unit.

1. Secondary Protection:  Load-carrying, manually reset or manually replaceable, thermal cutouts; factory wired in series with each heater stage.

E. Control Panel:  [Unit] [Remote] mounted with disconnecting means and overcurrent protection.  Include the following controls:

1. Magnetic contactor.

2. Mercury contactor.

3. Solid-state stepless pulse controller.

4. Toggle switches; one per step.

5. Step controller.

6. Time-delay relay.

7. Pilot lights; one per step.

8. Airflow proving switch.

2.8 GAS-FIRED HEATERS

A. CSA Approval:  Bear CSA label.
B. Type of Gas:  [Natural] [LP].

C. Assembly and Wiring:  Heaters factory assembled, piped, wired, and tested for 120-V ac.

D. Housing:  Steel, with integral draft hood and inserts for suspension-mounting rods.

1. External Casings and Cabinets:  Baked enamel over corrosion-resistant-treated surface.

E. Heat Exchanger: Stainless steel.

F. Burners:  Cast iron or aluminized steel with stainless-steel inserts.

G. Venting Provision:  Gravity.

Select paragraph above or first paragraph below.

H. Power Venter:  120-V ac, with stainless-steel shaft.

I. Automatic Gas Control:  [Single] [2]-stage, 24-V ac valve.

Select one ignition in paragraph below; spark ignition is optional feature.

J. Ignition:  [Standing pilot] [Electronically controlled spark with flame sensor].

2.9 FILTERS

A. Disposable Panel Filters:  Factory-fabricated, viscous-coated, flat-panel-type, disposable air filters with glass-fiber media sprayed with nonflammable adhesive in [cardboard] [galvanized-steel] frame.

B. Washable Panel Filters:  Removable, stainless-steel, baffle-type filters with spring-loaded fastening; with minimum 1.984-mm- (0.0781-inch-) thick, stainless-steel filter frame.

C. Mounting Frames:  Welded, galvanized steel with gaskets and fasteners and suitable for bolting together into built-up filter banks.

2.10 ACCESSORIES

Edit this Article to suit Project.

A. Factory-installed, [native ASHRAE 135, BACnet,] [LonWorks compatible] microprocessor controls specified by Division 15 Section, "Building Automation System" and “Temperature Controls”.

B.  [Built-in] [Field-Installed] Thermostat:  Line voltage, factory installed and wired to the junction box on air curtain.

C. Automatic Door Switch:  Plunger type installed in door area to activate air curtain when door opens and to deactivate air curtain when door closes.

D. Start-Stop, Push-Button Switch:  Manually activates and deactivates air curtain.

E. Time-Delay Relay:  Factory installed and adjustable to allow air curtain to operate from 0.5 seconds to 10 hours.

F. Motor-Control Panel:  Complete with motor starter, 115-V ac transformer with primary and secondary fuses, terminal strip, and NEMA 250, Type [1] [12] enclosure.

G. Mounting Brackets:  Adjustable mounting brackets for drum-type roll-up doors.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and conditions where air curtains will be installed for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Examine roughing-in for [hot-water] [steam] [gas] piping systems to verify actual locations of piping connections before air-curtain installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install air curtains with clearance for equipment service and maintenance.

Detail air-curtain mounting on Drawings and show vibration-control devices and seismic restraints appropriate for Project.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to air curtain to allow service and maintenance.

C. Breaching:  Comply with applicable requirements in Division 15 Section, "Breechings, Chimneys, and Stacks."  Connect breaching to full size at flue outlet.

D. Ground equipment according to Division 16 Section "Grounding and Bonding."

E. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. After installing air curtains completely, perform visual and mechanical check of individual components.

2. After electrical circuitry has been energized, start unit to confirm motor rotation and unit operation.  Certify compliance with test parameters.

3. Test gas train and verify that there are no gas leaks.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

B. Repair or replace malfunctioning units and retest as specified above.

3.5 ADJUSTING

A. Adjust belt tension.

B. Adjust motor and fan speed to achieve specified airflow.

C. Adjust discharge louver and dampers to regulate airflow.

D. Adjust air-directional vanes.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain air curtains.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15834
AIR CURTAINS
15834 - 8

