Copyright 2000 AIA
GSA VERSION MASTERSPEC
12/00 (GSA 03/05)

Copyright 2000, The American Institute of Architects (AIA)

This GSA Version MASTERSPEC Section is licensed by ARCOM to the U.S. General Services Administration (GSA) for internal use and for ARCOM to distribute to MASTERSPEC Licensed Users.  GSA has edited this Section from its original content for use on GSA projects as directed by GSA's Contracting Officer.  Use caution when editing this Section because GSA has modified some text and writing styles that are not compatible with other MASTERSPEC Sections.  Care must also be taken to coordinate requirements in this Section with other Sections and with the GSA Version of Division 1.

SECTION 15855 - DIFFUSERS, REGISTERS, AND GRILLES
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete editor’s comments before submitting specifications for a project.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes ceiling- and wall-mounted diffusers, registers, and grilles.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 10 Section "Louvers and Vents" for fixed and adjustable louvers and wall vents, whether or not they are connected to ducts.

2. Division 15 Section "Duct Accessories" for fire and smoke dampers and volume-control dampers not integral to diffusers, registers, and grilles.

1.3 SUBMITTALS

A. Product Data:  For each product indicated, include the following:

1. Data Sheet:  Indicate materials of construction, finish, and mounting details; and performance data including throw and drop, static-pressure drop, and noise ratings.

2. Diffuser, Register, and Grille Schedule:  Indicate Drawing designation, room location, quantity, model number, size, and accessories furnished.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

B. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Ceiling suspension assembly members.

2. Method of attaching hangers to building structure.

3. Size and location of initial access modules for acoustical tile.

4. Ceiling-mounted items including lighting fixtures, diffusers, grilles, speakers, sprinklers, access panels, and special moldings.

5. Duct access panels.

C. Samples for Initial Selection:  For diffusers, registers, and grilles with factory-applied color finishes.

Delete paragraph above if colors are preselected and specified or scheduled.  Retain below with or without above.

D. Samples for Verification:  For diffusers, registers, and grilles, in manufacturer's standard sizes to verify color selected.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.  

2.2 GRILLES AND REGISTERS

Insert number to complete drawing designation for each product retained in this Article.  Use these designations on Drawings to show where each product is required.

A. Adjustable Bar [Grille] [Register] <Insert drawing designation>:

1. Available Manufacturers:

a. A-J Manufacturing Co., Inc.

b. Anemostat; a Mestek Company.

c. Carnes.

d. Dayus Register & Grille.

e. Hart & Cooley, Inc.; Hart & Cooley Div.

f. Krueger.

g. METALAIRE, Inc.; Metal Industries Inc.

h. Nailor Industries of Texas Inc.

i. Price Industries.

j. Titus.

k. Tuttle & Bailey.

l. <Insert manufacturer's name.>

2. Material:  [Steel] [Aluminum] [Stainless steel].

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] <Insert finish>.

4. Face Blade Arrangement:  [Fixed horizontal] [Adjustable horizontal] [Fixed vertical] [Adjustable vertical] spaced [76 mm (3 inches)] [38mm (1-1/2 inches)] [19 mm (3/4 inch)] [13 mm (1/2 inch)] apart.

Delete first subparagraph below if no rear blades.

5. Rear Blade Arrangement:  [Fixed horizontal] [Adjustable horizontal] [Fixed vertical] [Adjustable vertical] spaced [19 mm (3/4 inch)] [13 mm (1/2 inch)] apart.

6. Frame:  [32 mm (1-1/4 inches)] [25 mm (1 inch)] wide.

Delete first subparagraph below if no mounting frame.

7. Mounting Frame:  [Filter] <Insert frame size and style>.

8. Mounting:  [Countersunk screw] [Concealed] [Lay in].

9. Damper Type:  [Adjustable opposed-blade assembly] [Opposed blade with spring-closing and UL-listed fusible link for 71 deg C (160 deg F)].

10. Accessories:  [Front] [Rear]-blade gang operator.

B. Security [Grille] [Register] <Insert drawing designation>:

1. Available Manufacturers:

a. A-J Manufacturing Co., Inc.

b. Anemostat; a Mestek Company.

c. Carnes.

d. Hart & Cooley, Inc.; Hart & Cooley Div.

e. Krueger.

f. Nailor Industries of Texas Inc.

g. Price Industries.

h. Titus.

i. Tuttle & Bailey.

j. <Insert manufacturer's name.>

2. Material:  [Steel] [Aluminum].

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] <Insert finish>.

4. Face Arrangement:  [5-mm- (3/16-inch-) thick front lattice plate with 51-by-51-mm- (2-by-2-inch-) square holes and 25-mm (1-inch) frets, 3.43-mm (0.135-inch) wire mesh, and 6-mm- (1/4-inch-) thick backer plate] [5-mm- (3/16-inch-) thick perforated faceplate with 8-mm- (5/16-inch-) diameter holes spaced 11 mm (7/16 inch) o.c., staggered at 60 degrees] [38-mm (1-1/2-inches) bars and mandrel tubes and rods with zero-degree deflection in 32-by-32-by-5-mm (1-1/4-by-1-1/4-by-3/16-inch) angle border] [38-mm (1-1/2-inch) bars and mandrel tubes and rods with 15-degree deflection in 32-by-32-by-5-mm (1-1/4-by-1-1/4-by-3/16-inch) angle border] [35-mm (1-3/8-inch) bars and double mandrel tubes with zero-degree deflection in 45-mm (1-3/4-inch) angle border] [35-mm (1-3/8-inch) bars and double mandrel tubes with 15-degree deflection in 45-mm (1-3/4-inch) angle border].

5. Wall Sleeve:  [5 mm (3/16 inch) welded to face] [3 mm (1/8 inch) welded to face] [Mechanically fastened to border].

6. Mounting:  [25-by-25-by-5-mm (1-by-1-by-3/16-inch) retaining angle frame] [32-by-32-by-5-mm (1-1/4-by-1-1/4-by-3/16-inch) retaining angle frame] [32-by-32-by-5-mm (1-1/4-by-1-1/4-by-3/16-inch) cast-in-place frame and tamperproof machine screws].

7. Damper Type:  [Adjustable opposed-blade assembly] [Opposed blade with spring-closing and UL-listed fusible link for 71 deg C (160 deg F)].

C. Fixed Face [Grille] [Register] <Insert drawing designation>:

1. Available Manufacturers:

a. A-J Manufacturing Co., Inc.

b. Anemostat; a Mestek Company.

c. Carnes.

d. Dayus Register & Grille.

e. Hart & Cooley, Inc.; Hart & Cooley Div.

f. Krueger.

g. Nailor Industries of Texas Inc.

h. Price Industries.

i. Titus.

j. Tuttle & Bailey.

k. <Insert manufacturer's name.>

2. Material:  [Steel] [Aluminum].

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] <Insert finish>.

4. Face Arrangement:  [13-by-13-by-13-mm (1/2-by-1/2-by-1/2-inch) grid core] [Perforated core].

5. Frame:  [32 mm (1-1/4 inches)] [25 mm (1 inch)] wide.

Delete first subparagraph below if no mounting frame.

6. Mounting Frame:  [Filter] <Insert frame size and style>.

7. Mounting:  [Countersunk screw] [Concealed] [Lay in].

8. Damper Type:  [Adjustable opposed-blade assembly] [Opposed blade with spring-closing and UL-listed fusible link for 71 deg C (160 deg F)].

2.3 LINEAR SLOT OUTLETS

Insert number to complete drawing designation for each product retained in this Article.  Use these designations on Drawings to show where each product is required.

Retain paragraph below for VAV operations.

General

1. Devices shall be specifically designed for variable-air volume flows.

B. Linear Bar Grille or Diffuser <Insert drawing designation>:

1. Available Manufacturers:

a. Air Research Diffuser Products, Inc.

b. Anemostat; a Mestek Company.

c. Carnes.

d. Dayus Register & Grille.

e. Hart & Cooley, Inc.; Hart & Cooley Div.

f. Krueger.

g. METALAIRE, Inc.; Metal Industries Inc.

h. Nailor Industries of Texas Inc.

i. Price Industries.

j. Titus.

k. Tuttle & Bailey.

l. <Insert manufacturer's name.>

2. Material:  [Steel] [Aluminum] [Stainless steel].

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] <Insert finish>.

Retain core from one of first five subparagraphs below.

4. Narrow Core Spacing Arrangement:  3-mm- (1/8-inch-) thick blades spaced 6 mm (1/4 inch) apart, [zero] [15]-degree deflection.

5. Wide Core Spacing Arrangement:  3-mm- (1/8-inch-) thick blades spaced 13 mm (1/2 inch) apart, [zero] [15]-degree deflection.

6. Wide Core Spacing Arrangement:  5-mm- (3/16-inch-) thick blades spaced 13 mm (1/2 inch) apart, [zero] [15] [30]-degree deflection.

7. Pencil-Proof Core Spacing Arrangement:  5-mm- (3/16-inch-) thick blades spaced 11 mm (7/16 inch) apart, [zero] [15] [30]-degree deflection.

8. [One] [Two]-Way Deflection Vanes:  Extruded construction fixed louvers with removable core.

9. Frame:  [32 mm (1-1/4 inches)] [25 mm (1 inch)] [19 mm (3/4 inch)] [13 mm (1/2 inch)] [5 mm (3/16 inch)] wide.

Delete first subparagraph below if no mounting frame.

10. Mounting Frame:  [Filter] <Insert frame size and style>.

11. Mounting:  [Countersunk screw] [Concealed bracket] [Spring clip].

12. Damper Type:  [Adjustable opposed-blade assembly] [Hinged single blade].

13. Accessories:  [Plaster frame] [Directional vanes] [Alignment pins] [Core clips] [Blank-off strips].

C. Linear Slot Diffuser <Insert drawing designation>:

1. Available Manufacturers:

a. Air Research Diffuser Products, Inc.

b. Anemostat; a Mestek Company.

c. Carnes.

d. Hart & Cooley, Inc.; Hart & Cooley Div.

e. Krueger.

f. METALAIRE, Inc.; Metal Industries Inc.

g. Nailor Industries of Texas Inc.

h. Price Industries.

i. Titus.

j. Tuttle & Bailey.

k. <Insert manufacturer's name.>

2. Material - Shell:  [Steel] [Aluminum], [insulated] [noninsulated].

3. Material - Pattern Controller and Tees:  Aluminum.

4. Finish - Face and Shell:  [Baked enamel, black] <Insert finish>.

5. Finish - Pattern Controller:  [Baked enamel, black] <Insert finish>.

6. Finish - Tees:  [Baked enamel, white] [Baked enamel, color selected by Architect] <Insert finish>.

7. Slot Width:  [13 mm (1/2 inch)] [19 mm (3/4 inch)] [25 mm (1 inch)] [38 mm (1-1/2 inches)].

8. Number of Slots:  [One] [Two] [Three] [Four] <Insert number>.

9. Length:  [600 mm (24 inches)] [750 mm (30 inches)] [900 mm (36 inches)] [1200 mm (48 inches)] [1500 mm (60 inches)].

10. Accessories:  [Plaster frame] [T-bar slot] [Center notch] [T-bar on inlet side] [T-bar on both sides] [T-bar clip on one side] [T-bar clips on both sides].

D. Light Troffer Diffuser <Insert drawing designation>:

1. Available Manufacturers:

a. Anemostat; a Mestek Company.

b. Carnes.

c. Hart & Cooley, Inc.; Hart & Cooley Div.

d. Krueger.

e. METALAIRE, Inc.; Metal Industries Inc.

f. Nailor Industries of Texas Inc.

g. Price Industries.

h. Titus.

i. Tuttle & Bailey.

j. <Insert manufacturer's name.>

2. Material:  Steel[ with external insulation].

3. Finish:  [None] [Black enamel on visible surfaces] <Insert finish>.

4. Slot Width:  [13 mm (1/2 inch)] [19 mm (3/4 inch)] [25 mm (1 inch)] [1-1/2 inches38 mm].

5. Number of Sides:  [One] [Two].

6. Length:  [600 mm (24 inches)] [900 mm (36 inches)] [1200 mm (48 inches)].

7. Pattern:  [Fixed] [Adjustable].

8. Inlet:  [Top] [Side].

9. Inlet Size:  [125 mm (5 inches)] [150 mm (6 inches)] [200 mm (8 inches)].

2.4 CEILING DIFFUSER OUTLETS

Insert number to complete drawing designation for each product retained in this Article.  Use these designations on Drawings to show where each product is required.

Retain paragraph below for VAV operations.

A. General

1. Devices shall be specifically designed for variable-air volume flows.

B. Round Ceiling Diffuser <Insert drawing designation>:

1. Available Manufacturers:

a. Anemostat; a Mestek Company.

b. Carnes.

c. Hart & Cooley, Inc.; Hart & Cooley Div.

d. METALAIRE, Inc.; Metal Industries Inc.

e. Nailor Industries of Texas Inc.

f. Price Industries.

g. Titus.

h. Tuttle & Bailey.

i. <Insert manufacturer's name.>

2. Material:  [Steel] [Aluminum].

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] [Anodized aluminum] <Insert finish>.

4. Face Style:  [Four] [Three] [Two] cone.

5. Pattern:  [Fully adjustable] [Two position horizontal].

6. Dampers:  [Radial opposed blade] [Butterfly] [Combination damper and grid].

7. Accessories:

a. Equaling grid.

b. Plaster ring.

c. Safety chain.

d. Wire guard.

e. Sectorizing baffles.

f. Operating rod extension.

C. Rectangular and Square Ceiling Diffusers <Insert drawing designation>:

1. Available Manufacturers:

a. A-J Manufacturing Co., Inc.

b. Anemostat; a Mestek Company.

c. Carnes.

d. Hart & Cooley, Inc.; Hart & Cooley Div.

e. Krueger.

f. METALAIRE, Inc.; Metal Industries Inc.

g. Nailor Industries of Texas Inc.

h. Price Industries.

i. Titus.

j. Tuttle & Bailey.

k. <Insert manufacturer's name.>

2. Material:  [Steel] [Aluminum].

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] [Anodized aluminum] <Insert finish>.

4. Face Size:  [600 by 600 mm (24 by 24 inches)] [500 by 500 mm (20 by 20 inches)] [300 by 300 mm (12 by 12 inches)] <Insert size>.

5. Face Style:  [Three cone] [Four cone] [Plaque].

6. Mounting:  [Surface] [T-bar] [Snap in] [Spline] [Mounting panel].

7. Pattern:  [Fixed] [Two position] [Adjustable].

8. Dampers:  [Radial opposed blade] [Butterfly] [Combination damper and grid].

9. Accessories:

a. Equaling grid.

b. Plaster ring.

c. Safety chain.

d. Wire guard.

e. Sectorizing baffles.

f. Operating rod extension.

D. Perforated Diffuser <Insert drawing designation>:

1. Available Manufacturers:

a. Air Research Diffuser Products, Inc.

b. A-J Manufacturing Co., Inc.

c. Anemostat; a Mestek Company.

d. Carnes.

e. Hart & Cooley, Inc.; Hart & Cooley Div.

f. Krueger.

g. METALAIRE, Inc.; Metal Industries Inc.

h. Nailor Industries of Texas Inc.

i. Price Industries.

j. Titus.

k. Tuttle & Bailey.

l. Warren Technology.

m. <Insert manufacturer's name.>

2. Material:  Steel backpan and pattern controllers, with [steel] [aluminum] face.

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] [Anodized aluminum] <Insert finish>.

4. Face Size:  [300 by 300 mm (12 by 12 inches)] [600 by 300 mm (24 by 12 inches)] [900 by 300 mm (36 by 12 inches)] [1200 by 300 mm (48 by 12 inches)] [400 by 400 mm (16 by 16 inches)] [500 by 500 mm (20 by 20 inches)] [600 by 600 mm (24 by 24 inches)] [900 by 600 mm (36 by 24 inches)] [1200 by 600 mm (48 by 24 inches)] <Insert size>.

5. Duct Inlet:  [Round] [Square].

6. Face Style:  [Flush] [Drop extended].

7. Pattern Controller:  [Four louvered deflector patches] [Fixed with curved blades at inlet] [Adjustable with louvered pattern modules at inlet] [None].

8. Mounting:  [Surface] [T-bar] [Snap in] [Spline] [Mounting panel].

9. Dampers:  [Opposed blade] [Radial opposed blade] [Butterfly] [Combination damper and grid] [Combination volume and fire].

10. Accessories:

a. Equaling grid.

b. Plaster ring.

c. Safety chain.

d. Wire guard.

e. Sectorizing baffles.

f. Operating rod extension.

E. Louver Face Diffuser <Insert drawing designation>:

1. Available Manufacturers:

a. A-J Manufacturing Co., Inc.

b. Anemostat; a Mestek Company.

c. Carnes.

d. METALAIRE, Inc.; Metal Industries Inc.

e. Nailor Industries of Texas Inc.

f. Price Industries.

g. Titus.

h. Tuttle & Bailey.

i. <Insert manufacturer's name.>

2. Material:  [Steel] [Aluminum].

3. Finish:  [Baked enamel, white] [Baked enamel, color selected by Architect] [Anodized aluminum] <Insert finish>.

4. Face Size:  <Insert mm (inches)>.

5. Mounting:  [Surface] [Surface with beveled frame] [T-bar] [Snap in] [Spline] [Mounting panel].

Insert manufacturer's core style code in first subparagraph below.

6. Pattern:  [One-way] [Two-way] [Two-way corner] [Three-way] [Four-way], <Insert code> core style.

7. Dampers:  [Radial opposed blade] [Butterfly] [Combination damper and grid].

8. Accessories:

a. Square to round neck adaptor.

b. Adjustable pattern vanes.

c. Throw reducing vanes.

d. Equaling grid.

e. Plaster ring.

f. Safety chain.

g. Wire guard.

h. Sectorizing baffles.

i. Operating rod extension.

2.5 FLEXIBLE DIFFUSION OUTLETS

Insert number to complete drawing designation for each product retained in this Article.  Use these designations on Drawings to show where each product is required.

A. Continuous Tubular Diffuser <Insert drawing designation>:

1. Available Manufacturers:

a. DuctSox Fabric Air Dispersion Products.

b. Patron Products Inc.

c. <Insert manufacturer's name.>
2. Material:  [Flame-retardant, woven polyethylene fabric] [Flame-retardant, coated polyester and fiberglass fabric] [Flame-retardant, permeable polyester and fiberglass fabric] [Polyethylene].

3. Duct Connection:  Round.

4. Duct Connection Size:  <Insert mm (inches)>.

5. Diffusion Hole Size:  <Insert mm (inches)>.

6. Diffusion Hole Frequency - Number per 30 m (100 Feet):  <Insert number.>

7. Accessories:

a. Quick-connect joint.

b. Snap hooks.

c. Cleanout zipper.

d. Condensate drain.

2.6 SOURCE QUALITY CONTROL

A. Verification of Performance:  Rate diffusers, registers, and grilles according to ASHRAE 70, "Method of Testing for Rating the Performance of Air Outlets and Inlets."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas where diffusers, registers, and grilles are to be installed for compliance with requirements for installation tolerances and other conditions affecting performance of equipment.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install diffusers, registers, and grilles level and plumb.

B. Ceiling-Mounted Outlets and Inlets:  Drawings indicate general arrangement of ducts, fittings, and accessories.  Air outlet and inlet locations have been indicated to achieve design requirements for air volume, noise criteria, airflow pattern, throw, and pressure drop.  Make final locations where indicated, as much as practicable.  For units installed in lay-in ceiling panels, locate units in the center of panel.  Where architectural features or other items conflict with installation, notify Architect for a determination of final location.

C. Install diffusers, registers, and grilles with airtight connections to ducts and to allow service and maintenance of dampers, air extractors, and fire dampers.

3.3 ADJUSTING

A. After installation, adjust diffusers, registers, and grilles to air patterns indicated, or as directed, before starting air balancing.

END OF SECTION 15855
DIFFUSERS, REGISTERS, AND GRILLES
15855 - 1

