NIH SUPPLEMENT TO MASTERSPEC

08/03
NIH Supplement dated 16 Oct 2002


Copyright 2002 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc (ARCOM) for the AIA

This section uses the term Contracting Officer, Contracting Officer's Technical Representative and/or Project Officer in specific locations within this section based on specific authorities granted each individual under the terms of the contract.  Any changes in these terms at specific locations within these specifications must be coordinated with the Contracting Officer.

15951 Attachment 1 must be included with every project specification.  This includes a Figure on Projected Sash Leakage that is referenced in the body of the specification.

SECTION 15951 TESTING CONSTANT VOLUME FUME HOODS

PART 1 -  GENERAL

Test identified below was created by Farhad Memarzadeh of the National Institutes of Health in 1997 and further revised by Memarzadeh and Brightbill in 1999. Any proposed changes to the testing procedures or protocol MUST be approved in writing by the NIH prior to making the changes.

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. The work of this section consists of testing the performance of constant volume chemical fume hoods. Any proposed changes to the testing procedures or protocol MUST be approved in writing by the NIH prior to making the changes.

B. Work related to on site and off site testing of fume hoods is included in this Section. 

C. Related Sections:  This specification section is related to any and all specification sections with explicit or implicit reference to project management and coordination.  Specific submittal requirements of these related specification sections are not included in this section.  Related sections include but are not limited to the following specification sections:

Edit the following list to include pertinent sections included in the project.  List below only products and construction for this Project that the reader might expect to find in this Section but are specified elsewhere.  Verify that Section titles listed below are correct for this Project's Specifications because Section titles may have changed since this Section was updated.

1. Division 11 Section “Laboratory Fume Hoods, By-Pass Type with Vertical Sashes.”

2. Division 11 Section “Laboratory Fume Hoods, By-Pass Type with Horizontal Sliding Sashes.”

3. Division 11 Section “Laboratory Fume Hoods, By-Pass Type with Combination Sashes.”

1.3 REFERENCES

A. American National Standard Institute (ANSI).

B. ANSI/ASHRAE 110‑1999 Standard for testing performance of Fume hoods

C. National Fire Protection Association NFPA 45 - Fire Protecting for Laboratories Using Chemicals

D. ANSI/ASHRAE III Testing and Balancing

E. ANSI/AIHA Z9.5 Laboratory Ventilation Standard

1.4 SUBMITTALS

A. Testing Equipment and Facilities

1. Submit 3 copies of specification sheets on all equipment proposed for on site testing specified in Part 3 of this section. 

2. Submit 3 copies of sample test reports for approval.  Contractor shall demonstrate the ability to perform necessary calculations on site the day of the test for the on site testing requirements.

3. Submit 3 copies of layouts of the testing facility.

B. Certifications

1. Submit test data attesting that each type of hood to be provided has been tested in accordance with the modified ANSI/ASHRAE 110-1999 and meets the requirements of this specification.

C. Qualifications

1. Submit 3 copies of the independent testing agency Statement of Qualifications, demonstrating testing agency’s experience relative to fume hood testing, provide a sample report, and include qualifications of personnel proposed to execute the testing. 

1.5 QUALITY CONTROL

A. Testing agency for On Site testing shall be independent of the fume hood control system manufacturer.

B. Independent testing agency shall be approved by the NIH Contracting Officer.  Testing agency shall submit Statement of Qualifications demonstrating experience relating to fume hood testing.  As a minimum, the testing agency shall:

1. Have a registered Professional Engineer or Industrial Hygienist executing the testing.

2. Demonstrate prior execution of indicated tests and submit a sample of the test report.

PART 2 -  PRODUCTS

2.1 TEST AND MEASUREMENT EQUIPMENT

A. Anemometers: 

1. Accuracy: (5% of reading

2. Internal Time Constant: <= 100ms 

a.  The Internal Time Constant (ITC) is the amount of time it takes the sensor to respond 63% of the way to a step change.  

b. The Response Time is the length of time to get to within the stated accuracy of the sensor.

c. Response Time = ITC * 3 or 5 depending on what accuracy.  Example: If the Response Time is 200 ms, the ITC = 40-70 ms.

B. Tracer Gas Ejector shall be in accordance with ANSI/ASHRAE 110.

C. Tracer Gas (SF6) Sensor:

1. Sensitivity:  0.01 to 100 ppm

2. Accuracy: 

a. Above 0.1 ppm: (10% of reading

b. Below 0.1 ppm: (25% of reading

D. Data Acquisition System: Minimum 6 channel system capable of simultaneous sampling at 10 Hz or greater. 

PART 3 -  EXECUTION

Both on-site and off site containment testing is required for all NIH projects.  Any deviations from the testing procedures or protocol specified MUST be approved in writing by the NIH prior to modifying these specifications.

3.1 FUME HOOD CONTAINMENT TESTING (ON SITE)

A. General: Laboratory areas and constant volume fume hoods shall be tested as installed to assess the level of containment.  Testing shall be conducted as outlined below for 50% of the hoods provided in the project.  Hoods to be tested will be selected by the Project Officer.  

B. Testing shall be conducted in accordance with ASHRAE 110 “Method of Testing Performance of Laboratory Fume Hoods” with the following modifications.  This is primarily a test of the hood and laboratory configuration.

1. Hoods will be tested with simulated apparatus.  This apparatus will consist of: two each 3.8L round paint cans, one 300mm by 300mm by 300mm cardboard box, three each 150mm by 150mm by 300mm cardboard boxes.  These items will be positioned from 150mm to 250mm behind the sash, randomly distributed, and supported off the work surface by 50mm by 50mm blocks.

2. The test gas will have a 6 LPM flow rate.

3. The test will be conducted at the center position for the manikin only.

4. Each test duration will be 5 minutes.

5. Acceptable test results will be 0.05 ppm or better.

6. At the conclusion of each 5-minute test there will be three rapid walk-bys at 300mm behind the manikin.  Each walk-by will be spaced 30 seconds apart.  If there is a rise in test gas concentration, it cannot exceed 0.10 ppm and must return to 0.05 ppm within 15 seconds.

7. There will be a minimum of three and a maximum of five people in the test room during the test procedure.

8. Representatives of the NIH will witness the tests.

C. Face velocity testing shall be conducted to determine flow rates and turbulence at the face of the hood.

1. Face Velocity Parameters shall include:

a. Measured Face Velocity (FVm expressed in m/s): Face velocity measured in the plane of the sash at three locations at any point in time. Samples for each sensor shall be recorded simultaneously at no less than 10 Hz.  The sensors shall basically be point sensors located in the middle of 1’-0” by 1’-0” grid sectors. Move the three sensors to other sectors for subsequent testing periods.  Averages shall be calculated for any point in time to assess overall measured face velocity, however individual sensor samples shall be used in calculating TI for each sensor.  These face velocity measurements shall be made with sash(es) open and “closed”.  Open shall mean the sashes positioned to their maximum design position (to sash stop typically 18” to 22”).  Closed shall mean open to 6” for a vertical rising only sash and center panels open 6” on the horizontally sliding panels with the vertically rising sash closed.

b. Steady State Face Velocity (SSFV):  The average of all sampled face velocities for a 5 second period.  Two SSFVs will be determined for both measured face velocity and calculated face velocity; one before the event (SSFVb) and one after (SSFVa).  The SSFVa will start two seconds after the end of TSS. The second suffix of m for measured and c for calculated shall be used to indicated the type of assessment 

c. Turbulence Intensity (TI expressed in m/s): Calculated root mean square of the fluctuating face velocity determined using FVm, calculated as follows:
sqrt[Sum 1-n{(FVm1-SSFV)^2+...+(FVmn-SSFV)^2}/n] This value shall be calculated for each of the steady state conditions preceding and following each event.  This shall be correlated to a "Box Leakage Factor" using the graph “Projected Sash Leakage” of the installation using the “Methodology for Optimization of Laboratory Fume Hood Containment” (MOLHC) by NIH Office of the Director, Farhad Memarzadeh principal investigator.  While this value does not have a pass/fail requirement, it is the fundamental indicator of containment and therefore shall be clearly reported.

The Designer MUST include “15951 Attachment 1” to this specification section to provide a graphic representation of the Projected Sash Leakage.

d. A graphic representation of Projected Sash Leakage is included as attachment 1 to this specification section.  

D. Hood Static Pressure:  Take traverse readings to measure exhaust rate and measure the hood static pressure two straight-line duct diameters downstream from the point of connection between the hood and the exhaust line.  The readings shall be taken with a face velocity of .51 m/s ( .05 m/s at the full open sash position (open sash typically is 18” to 22”).
E. Performance Parameter Requirements  

1. Tracer Gas Leakage per ANSI/ASHRAE-110: 4.00 AM 0.05
2. Average Face Velocity 

a. Sash(es) open:.51 m/s ( .05m/s  (Open to sash stop typically 18” to 22”).

b. Sash(es) Closed: <1.53 m/s ( .15 m/s (exhaust rate shall not change) 
3. SSFV Deviation Across Face: <15% of average face velocity

4. Pressure Drop Through the Hood: <= 13 mm water gage 

F. Test Execution:  Testing agency shall be equipped to execute the testing and assess all performance parameters on site the day of the test.  Data acquisition of required parameters shall be simultaneous.

G. Test Documentation:  All testing, calculated, and recorded parameters shall be presented in a report that shows the recorded parameters graphically and tabulates and summarizes all the results.  Performance of the hood, the hood controls, and the laboratory in general shall be described and summarized.

3.2 FUME HOOD CONTAINMENT TESTING (OFF SITE MOCK-UP)

A. The manufacturer of the proposed fume hood control system shall mock up a fume hood installation and demonstrate the performance of their system to validate that they can meet the requirements specified in Article “Fume Hood Containment Testing (On-Site).”  The off site test shall include all parameters under the control of the control system (FVBL, TSS, CL, RTC, SSD, and Controllability).  It is not necessary to mock up the installation and assess TI.  Events to be tested off site include all specified sash movements on the hood being tested.  Walkbys and door opening affects are not required for the off site test. 

B. The testing shall be accomplished by an independent testing agency approved by the A/E and NIH.  Reports shall be provided with the laboratory control submittals and no approval will be given for the fume hood control system until documentation of successful demonstration of the performance requirements are submitted.
END OF SECTION 15951

TESTING CONSTANT VOLUME FUME HOODS
15951 - 2

