SECTION 15121

EXPANSION COMPENSATION

PART 1 - GENERAL

1.1   SECTION INCLUDES

A.  Flexible pipe connectors, expansion joints (compensating), pipe loops, offsets and swing joints.

1.2   REFERENCES

A.  Expansion Joint Manufacturers' Association.

1.3   BASIS OF CALCULATIONS

A.  Base expansion calculations on 50 degrees F installation temperature to 250 degrees F for steam, 225 degrees F for hot water heating and 140 degrees F for domestic hot water, plus 30 percent safety factor.

1.4   SUBMITTALS

A.     Include maximum allowable temperature and pressure rating, overall face-to-face length, live length, hose wall thickness, hose convolutions per foot and per assembly, fundamental frequency of assembly, braid structure, total number of wires in braid in flexible pipe connector, and maximum expansion compensation in expansion joint

PART 2-PRODUCTS

2.1   MANUFACTURERS (FLEXIBLE CONNECTIONS AND EXPANSION JOINTS)

A.    Amber/Booth.

B.    Senior Flexonics.

C.    Metraflex.

D.    Flex-Hose Company.

2.2   MANUFACTURERS (PIPE, ROLLERS, GUIDES, AND ANCHORS)

A.  Grinnell.

B.  Superstrut.

2.3   FLEXIBLE PIPE CONNECTIONS

A.  For steel piping construct with stainless steel inner hose and braided exterior sleeve.

B.  For copper piping construct with bronze inner hose and braided exterior sleeve.

C.  Construct spool pieces to exact size for insertion of flexible connection.

2.4   EXPANSION JOINTS

A.  Steel Piping 3 inch and under: Provide stainless steel bellows type with anti-torque device, limit stops, and internal guide.

B.  Steel Piping over 3 inch: Provide external ring controlled type with hydraulically formed stainless steel bellows.

C.  Copper Piping: Provide all bronze type with two-ply bronze bellows, anti-torque device limit stops, internal guides, and solder joint end.

2.5    CONNECTIONS: Provide flexible pipe connections and expansion joints suitable to connect to adjoining piping as specified for pipe joints. Use pipe-sized units.

2.6    PIPE GUIDES:  Provide heavy-duty carbon steel guides, equivalent to Grinnell Figure

#255.

2.7    PIPE ROLLERS: Provide adjustable pipe roller stand with carbon steel base plate, equivalent to Grinnel Figure #274.

2.8   PIPE ANCHORS: Provide welded carbon steel pipe anchors, equivalent to Grinnell Figure #257A, attached to building structure.

PART 3 - EXECUTION

3.1   INSPECTION

A.     Examine piping layout and notify A/E of additional anchors required to adequately protect system.

B.     Provide inspection services by manufacturer's representative for final installation and certify installation is in accordance with manufacturer's recommendations and connectors are performing satisfactorily.

3.2   INSTALLATION

A.    Accomplish structural work and provide equipment required to control expansion and contraction of piping, loops, pipe offsets, and swing joints, and provide corrugated bellows type expansion joints where required.

B.    Install flexible connectors at right angles to displacement. Install one end immediately adjacent to isolated equipment and anchor other end.  

C.  Provide pipe anchors as shown on the drawings and/or as required to facilitate proper operation of pipe guides.  Install anchors so as to be in compression. Weld anchors to pipe and to building structure.

D.  Provide pipe guides at a maximum spacing of 25 feet on centers for pipe sizes 2” and smaller, at a maximum spacing of 35 feet on centers for pipe sizes 2-1/2” through 4”, at a maximum spacing of 50 feet on centers for pipe sizes 5” through 8”, at a maximum spacing of 85 feet on centers for pipe sizes 10" through 16", unless otherwise indicated on the drawings or required by the design of the building structure. Provide pipe guides so that movement takes place along axis of pipe only.  Guide sizes shall be the nominal pipe size with insulation in accordance with Piping Insulation Specification. Install per the manufacturer’s recommendations. Guides are not designed to carry dead weight load on pipe and are not intended to take the place of the required pipe supports and rollers.

END OF SECTION
SECTION  15121
Page 1 of 3

