New Walk-In Cooler / Freezer

To be Kolpak, or equal, nominal dimension as shown on plans, standard height. Provide complete operating system, start, test, operate, and demonstrate system prior to acceptance. Standard wall panels to be 4” thick foamed in place urethane sandwich between metal surfaces. Foam plastics shall meet the requirements of Southern Building Code Section 717. Exterior floor, ceiling, to be 26-gauge galvalume. Concealed exterior walls to be 26 gauge embossed galvalume. Interior walls and ceiling to be 22-gauge stainless steel, interior floor to be 1/8” thick aluminum tread plate. Exposed exterior walls to be 22-gauge stainless steel. Entrance doors to be standard 34” x 78”, with cylinder lock and inside safety release handle. Unit to have NSF label and be complete with refrigeration lines, matching closure trim, skirts, base cove, etc.  Provide standard refrigeration system with remote all weather condensing unit, air-cooled. Provide copper condensate and drain lines. Provide proper electrical connections, wiring, service, fittings, etc. Provide standard 10-year panel warranty and 5-year refrigeration warranty, operation and maintenance instructions.

