
SECTION 02225PRIVATE 


TRENCHING

1 PART 1   GENERAL


.1
SECTION INCLUDES



A.
Excavate trenches for utilities. 



B.
Backfilling and compaction.


.2
RELATED SECTIONS



A.
Section 01400‑ Quality Control: 01410 ‑ Testing Laboratory Services: Testing fill compaction.



B.
Section 01500 ‑ Construction Facilities and Temporary Controls: Water control in excavations.



C.
Section 02202 ‑ Rock removal: Removal of rock during excavation.



D.
Section 02211 ‑ Rough Grading: Topsoil and subsoil removal from site surface.



E.
Section 02218 ‑ Landscape Grading: Filling of topsoil over backfilled trenches to finish grade elevation.



F.
Section 02222 ‑ Excavation: General building excavation.



G.
Section 02223 ‑ Backfilling: General backfilling.



H.
Section 03300 ‑ Cast‑in‑Place Concrete: Concrete materials.


.3
REFERENCES



A.
ANSI/ASTM C136 ‑ Method for Sieve Analysis of Fine and Coarse Aggregates.



B.
ANSI/ASTM D698 ‑ Test Methods for Moisture‑Density Relations of Soils and Soil‑Aggregate Mixtures, Using 5.5 lb. (2.49 kg) Rammer and 12-inch (304.8 mm) Drop.



C.
ANSI/ASTM D1556 ‑ Test Method for Density of Soil in Place by the Sand‑Cone Method.



D.
ANSI/ASTM D1557 ‑ Test Methods for Moisture‑Density Relations of Soils and Soil‑Aggregate Mixtures Using 10 lb. (4.54 kg) Rammer and 18 inch (457 mm) Drop.


.4
SUBMITTALS



A.
Submit under provisions of Section 01300.


.5
FIELD MEASUREMENTS



A.
Verify that survey benchmark and intended elevations for the Work are as shown on Drawings.

2 PART 2   PRODUCTS


.1
FILL MATERIALS



A.
Types B Subsoil materials as specified in Section 02223.


.2
BED MATERIALS



A.
Type 1 ‑ Coarse Stone Crushed: Pit run, washed natural stone; free of shale, clay, friable material, sand, debris; graded in accordance with ANSI/ASTM C136 within the following limits:




Sieve_Size




Percent_Passing



3/4 inch (19 mm)            95  to 100 



    5/8 inch (16 mm)            75  to 100

       3/8 inch (9 mm)             55  to 85 

       No. 4                       35  to 60




   (4.75 mm)




No. 16     


        15  to 35




   (1.18 mm)




No. 40 


            10 to 25




   (450  mm)




No. 200 


         5 to 10 





(75  micro m)



B.
Type 3 ‑ Sand: Natural river or bank sand; [washed; free of silt, clay, loam, friable or soluble materials, or organic matter; graded in accordance with ANSI/ASTM C136, within the following limits:




Sieve_Size




Percent_Passing



No. 4 


            100




   (4.75 mm)




No. 14 


            10 to 100




   (1.40 mm)




No. 50 


            5 to 90




   (300 micro m)




No. 100 


        4 to 30 




   (150 micro m)




No. 200 


        0




   (75  micro m)



c.
Subsoil Material: As specified in Section 02223.

3 PART 3   EXECUTION


.1
EXAMINATION



A.
Verify fill materials to be reused, is acceptable.


.2
PREPARATION



A.
Identify required lines, levels, contours, and datum.



B.
Maintain and protect existing utilities remaining, which pass through work area.



C.
Protect plant life, lawns, rock outcropping and other features remaining as a portion of final landscaping.



D.
Protect benchmarks, existing structures, fences, sidewalks, paving, and curbs from excavation equipment and vehicular traffic.



E.
Protect above and below grade utilities which are to remain.



F.
Cut out soft areas of subgrade not capable of insitu compaction.  Backfill with Type 2 fill and compact to density equal to or greater than requirements for subsequent backfill material.


.3
EXCAVATION



A.
Excavate subsoil required for storms sewer.



B.
Cut trenches sufficiently wide to enable installation of utilities and allow inspection.



C.
Correct unauthorized excavation at no cost to Owner.



D.
Correct areas over‑excavated by error in accordance with Section 02222.



E.
Stockpile excavated material in area designated on site and remove excess material not being used, from site.


.4
BEDDING



A.
Support pipe and conduit during placement and compaction of bedding fill.


.5
BACKFILLING



A.
Backfill trenches to contours and elevations with unfrozen materials.



B.
Systematically backfill to allow maximum time for natural settlement.  Do not backfill over porous, wet, frozen or spongy subgrade surfaces.



C.
Place geotextile fabric over Type A fill prior to placing next lift of fill.



D.
Soil Fill: Place and compact material in continuous layers not exceeding 8 inches compacted depth.



E.
Employ a placement method that does not disturb or damage existing utilities, roadbeds, etc.



F.
Maintain optimum moisture content of backfill materials to attain required compaction density.



G.
Remove surplus backfill materials from site.



H.
Leave fill material stockpile areas completely free of           excess fill materials.


.6
TOLERANCES



A.
Top Surface of Backfilling: Under Paved Areas: Plus or minus one inch (25 mm) from required elevations.



B.
Top Surface of General Backfilling: Plus or minus one inch (25 mm) from required elevations.


.7
FIELD QUALITY CONTROL



A.
Field inspection and testing will be performed under provisions of Section 01400. 

B. Tests and analysis of fill material will be performed in accordance with ANSI/ASTM D698 D1557 and with Section 01400. 



C.
Compaction testing will be performed in accordance with ANSI/ASTM D698 and with Section 01400. 



D.
If tests indicate Work does not meet specified requirements, remove Work, replace and retest at no cost to Owner.


.8
PROTECTION OF FINISHED WORK



A.
Protect finished Work under provisions of Section 01500.



B.
Recompact fills subjected to vehicular traffic.


.9
SCHEDULE



A.
Storm and Sanitary Piping:




1.
Bedding Fill: Type 1, compacted to 95 percent,




2.
Cover with Common fill, in 8 (200-mm) lifts, compacted to 95 percent.


END OF SECTION
PAGE  
Error! Main Document Only.
Section 02225 Page 1 of 1     

