

SECTION 09260PRIVATE 


GYPSUM BOARD SYSTEMS

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.

1 PART 1 GENERAL


.1

SECTION INCLUDES



A.
Gypsum board.



B.
Taped and sanded joint treatment.


.2

RELATED SECTIONS



A.
Section 08112 ‑ Standard Steel Frames.



B.
Section 09900 ‑ Painting: Surface finish.


.3

REFERENCES



A.
ASTM C36 ‑ Gypsum Wallboard.



B.
ASTM C475 ‑ Joint Treatment Materials for Gypsum Wallboard Construction.



C.
ASTM C514 ‑ Nails for the Application of Gypsum Wallboard.



D.
K.
ASTM C840 ‑ Application and Finishing of Gypsum Board.

E. GA‑201 ‑ Gypsum Board for Walls and Ceilings.


.4

SUBMITTALS



A.
Submit under provisions of Section 01300.

B. Product Data:  Provide data on metal framing, gypsum board, joint tape.



C.
Reference to General Conditions.


.5

QUALITY ASSURANCE



A.
Perform Work in accordance with ASTM C840.

2 PART 2 PRODUCTS


.1

MANUFACTURERS ‑ GYPSUM BOARD SYSTEM



A.
U.S. Gypsum



B.
Other acceptable manufacturers offering equivalent products.




1.
Gold Bond


2. Elephant Brand.


.2

FRAMING MATERIALS



A.
Furring, Framing and Accessories: ASTM C645.



B.
Fasteners:  ASTM C514.



C.
Anchorage to Substrate: Tie wire, nails, screws and other metal supports, of type and size to suit application; to rigidly secure materials in place.



D.
Adhesive:  ASTM C557.


.3

GYPSUM BOARD MATERIALS



A.
Fire Rated Gypsum Board:
ASTM C36; fire resistive type, UL rated; 5/8 inch thick, maximum permissible length; ends square cut, tapered edges.


.4

ACCESSORIES



A.
Corner Beads: Metal.



B.
Joint Materials:
ASTM C475; reinforcing tape, joint compound, adhesive, and water.



C.
Fasteners:
ASTM C1002, Type S12.

3 PART 3 EXECUTION


.1

EXAMINATION



A.
Verify site conditions under provisions of Section 01039. 


.2

WALL FURRING INSTALLATION



A.
Erect wall furring for direct attachment to concrete block walls.



B.
Erect furring channels horizontally; space maximum 16 inches on center, not more than 4 inches (100 mm) from floor and ceiling lines.


.3

GYPSUM BOARD INSTALLATION



A.
Install gypsum board in accordance with GA‑201.

B. Erect single layer fire rated gypsum board vertically, with edges and ends occurring over firm bearing.



C.
Use screws when fastening gypsum board to metal furring or framing.



D.
Place corner beads at external corners.  Use longest practical length.  Place edge trim where gypsum board abuts dissimilar materials


.4

JOINT TREATMENT



A.
Tape, fill, and sand exposed joints, edges, and corners to produce smooth surface ready to receive finishes.


.5

TEXTURE FINISH



A.
Spray apply finish texture coating in accordance with manufacturer's instructions.


.6

TOLERANCES



A.
Maximum Variation of Finished Gypsum Board Surface from True Flatness:  1/8 inch in 10 feet (3 mm in 3 m) in any direction.


END OF SECTION
PAGE  
Error! Main Document Only.
Section 09260 Page 2 of 3

