

SECTION 15121PRIVATE 


PIPING EXPANSION COMPENSATION

PART 1
GENERAL

.1

SECTION INCLUDES


A. Flexible pipe connectors.


B. Expansion joints and compensators.


C. Pipe loops, offsets, and swing joints.

.2

RELATED SECTIONS



A. Section 15410 ‑ Plumbing Piping.


B. Section 15510 ‑ Hydronic Piping.

.3

REFERENCES


A.MIL‑E‑17814E ‑ Expansion Joints, Pipe, Slip‑Type, Packed.

.4

PERFORMANCE REQUIREMENTS


A. 
Provide structural work and equipment required to control expansion and contraction of piping.  Verify that anchors, guides, and expansion joints provided, adequately protect system.


B.  Expansion Calculations:


    1.Installation Temperature: 50 degrees F.


    2.Hot Water Heating: 210 degrees F.


    3.Domestic Hot Water: 140 degrees F.


    4.Safety Factory: 30 percent.

.5

SUBMITTALS


A.  Submit under provisions of Section 01300.


B.  Product Data:


   
1.Flexible Pipe Connectors: Indicate maximum temperature 

        and pressure rating, face‑to‑face length, live length, 

        hose wall thickness, hose convolutions per foot (meter) 

        and per assembly, fundamental frequency of assembly, braid 

        structure, and total number of wires in braid.

 

2.Expansion Joints: Indicate maximum temperature and 

        pressure rating, and maximum expansion compensation.


C. Samples:  Submit two low pressure compensators.


D. Design Data: Indicate selection calculations.


E. Manufacturer's Installation Instructions:  Indicate special procedures, and external controls.

.6

PROJECT RECORD DOCUMENTS


A. Submit under provisions of Section 01700.

.7
OPERATION AND MAINTENANCE DATA


A. Submit under provisions of Section 01700.


B. Maintenance Data: Include adjustment instructions.

.8

QUALIFICATIONS


A. 
Manufacturer:  Company specializing in manufacturing the products specified in this section with minimum three years documented] experience.


B. 
Design expansion compensating system under direct supervision of a Professional Engineer experienced in design of this work and licensed in the State of  LA.

.9

DELIVERY, STORAGE, AND HANDLING

A. Deliver, store, protect and handle products to site under 

   provisions of Section 01600.


B. Accept expansion joints on site in factory packing with 

     shipping bars and positioning devices intact.  Inspect for damage.

B. Protect equipment from exposure by leaving factory coverings, 

pipe end protection, and packaging in place until         installation.

.10
WARRANTY


A. Provide five year warranty.


B. Warranty:  Include coverage for leak free performance of 

PART 2
PRODUCTS

.1

FLEXIBLE PIPE CONNECTORS


A. Steel Piping:


   1.Inner Hose: Stainless Steel.


   2.Exterior Sleeve: stainless steel.


   3.Pressure Rating:  125 psig  and 450 degrees F 

  
   4.Joint: As specified for pipe joints.


   5.Size: Use pipe sized units.


   6.Maximum offset: 1 inch 25 mm on each side of installed 

       center line.

.2

EXPANSION JOINTS

1. Pressure Rating:  125 psig  WSP and 400 degrees F    


2. Maximum Compression: 1‑3/4 inch.


3. Maximum Extension: 1/4 inch. 


4. Joint: As specified for pipe joints.


5. Size: Use pipe sized units


6. Application:  Steel piping 3 inch (75 mm) and under.

PART 3
EXECUTION

.1
INSTALLATION


A.  Install in accordance with manufacturer's instructions.


B.  Construct spool pieces to exact size of flexible connection for future insertion.


C. Install flexible pipe connectors on pipes connected to equipment supported by vibration isolation.  Provide line size flexible connectors.

C.  Install flexible connectors at right angles to displacement.  

D.  Install one end immediately adjacent to isolated equipment and anchor other end.  Install in horizontal plane unless indicated otherwise.


E.  Rigidly anchor pipe to building structure where necessary.  Provide pipe guides so movement is directed along axis of pipe only.  Erect piping such that strain and weight is not on cast connections or apparatus.


F.  Provide support and equipment required to control expansion and contraction of piping.  Provide loops, pipe offsets, and swing joints, or expansion joints where indicated.


G.  Provide victaulic piping with minimum one joint per (inch) (25 mm) pipe diameter instead of flexible connector supported by vibration isolation.  Victaulic piping need not be anchored.


H.  Provide expansion loops as indicated on drawings.

.2

MANUFACTURER'S FIELD SERVICES


A. Prepare and start systems under provisions of Section 01400. 


B.  Provide inspection services by flexible pipe manufacturer's representative for final installing and certify installation is in accordance with manufacturer's recommendations and connectors are performing satisfactorily.


END OF SECTION
PAGE  
Error! Main Document Only.
Section 15121 Page 1 of 3      

