

SECTION 15140PRIVATE 


SUPPORTS AND ANCHORS

PART 1
GENERAL

.1

SECTION INCLUDES


A. Pipe and equipment hangers and supports.


B. Equipment bases and supports.


C. Sleeves and seals.


D. Flashing and sealing equipment and pipe stacks.

.2

RELATED SECTIONS


A.  Section 07270 ‑ Firestopping: Joint seals for piping and   duct penetration of fire rated assemblies.


B.  Section 09900 ‑ Painting.


C.  Section 15242 ‑ Vibration Isolation.


D.  Section 15260 ‑ Piping Insulation.


E.  Section 15280 ‑ Equipment Insulation.


F.  Section 15310 ‑ Fire Protection Piping.


G.  Section 15410 ‑ Plumbing Piping.


H.  Section 15510 ‑ Hydrontic Piping.


I.  Section 15535 ‑ Refrigerant Piping and Specialties.

.3

REFERENCES


A.  ASME B31.1 ‑ Power Piping


B.  ASME B31.2 ‑ Fuel Gas Piping


C.  ASME B31.5 ‑ Refrigeration Piping


D.  ASME B31.9 ‑ Building Services Piping


E.  ASTM F708 ‑ Design and Installation of Rigid Pipe Hangers.


F.  MSS SP58 ‑ Pipe Hangers and Support ‑ Materials, Design and 


    Manufacturer.


G.  MSS SP69 ‑ Pipe Hangers and Supports ‑ Selection and Application.


H.  MSS SP89 ‑ Pipe Hangers and Supports ‑ Fabrication and

      Installation Practices.


.4

SUBMITTALS


A.  Submit under provisions of Section 01300.

B. Shop Drawings:  Indicate system layout with location and

    detail of trapeze hangers.


C.  Product Data: Provide manufacturers catalog data including load capacity.


D. 
Design Data: Indicate load carrying capacity of trapeze,   multiple pipe, and riser support hangers.


E.
Manufacturer's Installation Instructions: Indicate special procedures and assembly of components.

.5

REGULATORY REQUIREMENTS

A.  Conform to applicable code for support of plumbing

    hydronic piping.


B.  Supports for Sprinkler Piping: In conformance with NFPA 13.


C.  Supports for Standpipes: In conformance with NFPA 14.

PART 2
PRODUCTS

.1

PIPE HANGERS AND SUPPORTS


A.  Manufacturers:




Not Used


B.  
Plumbing Piping ‑ DWV:


 1.
Conform to ASME B31.9 


 2.
Hangers for Pipe Sizes 1/2 to 1‑1/2 Inch (13 to 38 mm): Malleable       
iron , adjustable swivel, split ring.

3. Hangers for Pipe Sizes 2 Inches (50 mm) and Over: Carbon steel, adjustable, clevis.

4. Multiple or Trapeze Hangers: Steel channels with welded spacers 

Steel, adjustable, clevis.


 5.
Wall Support for Pipe Sizes to 3 Inches (75 mm): Cast iron hook.

 6. 
Wall Support for Pipe Sizes 4 Inches (100 mm) and Over: Welded 

steel bracket and wrought steel clamp.


 7.
Vertical Support: Steel riser clamp.

8. Floor Support: Cast iron adjustable pipe saddle, lock nut, nipple, 

floor flange, and concrete pier or steel support.


 9.
Copper Pipe Support: Carbon steel ring, adjustable, copper plated.


C.  Plumbing Piping ‑ Water:



1.
Conform to ASME B31.9.



2.
Hangers for Pipe Sizes 1/2 to 1‑1/2 Inch (13 to 38 mm): Malleable iron, adjustable swivel, split ring.



3.
Hangers for Cold Pipe Sizes 2 Inches (50 mm) and Over: Carbon steel, adjustable, clevis.



4.
Hangers for Hot Pipe Sizes 2 to 4 Inches (50 to 100 mm): Carbon steel, adjustable, clevis.



5.
Hangers for Hot Pipe Sizes 6 Inches (150 mm) and Over:  Adjustable steel yoke, cast iron roll, double hanger.



6.
Multiple or Trapeze Hangers: Steel channels with welded spacers and hanger rods.



7.
Multiple or Trapeze Hangers for Hot Pipe Sizes 6 Inches (150 mm) and Over: Steel channels with welded spacers and hanger rods, cast iron roll.



8.
Wall Support for Pipe Sizes to 3 Inches (76 mm): Cast iron hook.



9.
Wall Support for Pipe Sizes 4 Inches (100 mm) and Over: Welded steel bracket and wrought steel clamp.

  

10. Wall Support for Hot Pipe Sizes 6 Inches (150 mm) and Over: Welded steel bracket and wrought steel clamp with adjustable steel yoke and cast iron roll.


    
11. Vertical Support: Steel riser clamp.


   
12. Floor Support for Cold Pipe:  Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support.


   
13. Floor Support for Hot Pipe Sizes to 4 Inches (100 mm): Cast iron adjustable pipe saddle, lock nut,  nipple, floor flange, and concrete pier or steel support.


   
14. Floor Support for Hot Pipe Sizes 6 Inches (150 mm) and Over: Adjustable cast iron roll and stand, steel screws, and concrete pier or steel support.


   
15. Copper Pipe Support: Carbon steel ring, adjustable, copper plated.


D.
Hydronic Piping:



1.
Conform to ASME B31.9.



2.
Hangers for Pipe Sizes 1/2 to 1‑1/2 Inch (13 to 38 mm): Malleable iron, adjustable swivel, split ring.



3.
Hangers for Cold Pipe Sizes 2 Inches (50 mm) and Over: Carbon steel, adjustable, clevis.



4.
Hangers for Hot Pipe Sizes 2 to 4 Inches (50 to 100 mm): Carbon steel, adjustable, clevis.



5.
Hangers for Hot Pipe Sizes 6 Inches (150 mm) and Over:  Adjustable steel yoke, cast iron roll, double hanger.



6.
Multiple or Trapeze Hangers: Steel channels with welded spacers and hanger rods.



7.
Multiple or Trapeze Hangers for Hot Pipe Sizes 6 Inches (150 mm) and Over: Steel channels with welded spacers and hanger rods, cast iron roll.



8.
Wall Support for Pipe Sizes to 3 Inches (76 mm): Cast iron hook.



9.
Wall Support for Pipe Sizes 4 Inches (100 mm) and Over: Welded steel bracket and wrought steel clamp.



10. Wall Support for Hot Pipe Sizes 6 Inches (150 mm) and Over: Welded steel bracket and wrought steel clamp with adjustable steel yoke and cast iron roll.



11. Vertical Support: Steel riser clamp.



12. Floor Support for Cold Pipe:  Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support.



13. Floor Support for Hot Pipe Sizes to 4 Inches (100 mm): Cast iron adjustable pipe saddle, lock nut,  nipple, floor flange, and concrete pier or steel support.



14. Floor Support for Hot Pipe Sizes 6 Inches (150 mm) and Over: Adjustable cast iron roll and stand, steel screws, and concrete pier or steel support.



15. Copper Pipe Support: Carbon steel ring, adjustable,    copper plated.


E.
Steam and Steam Condensate Piping:




Not Used

   
1.
Vertical Support: Steel riser clamp.



2.
Floor Support for Pipe Sizes to 4 Inches (100 mm): Cast iron

     

adjustable pipe saddle, lock nut, nipple, floor flange, and 

     

concrete pier or steel support.


 
3.
Floor Support for Pipe Sizes 6 Inches (150 mm) and  Over: 

     

Adjustable cast iron roll and stand, steel screws, and 

     

concrete pier or steel support.


 
4.
Copper Pipe Support: Carbon steel ring, adjustable, copper 

     

plated.


F. 
Refrigerant Piping:




Not Used

.2

ACCESSORIES


A.  Hanger Rods: Mild steel threaded both ends, threaded one end, or continuous threaded.

.3

INSERTS


A. 
Inserts: Malleable iron case of galvanized steel shell and expander plug for threaded connection with lateral adjustment, top slot for reinforcing rods, lugs for attaching to forms; size inserts to suit threaded hanger rods.

.4

FLASHING


A. Metal Flashing: 26 gage galvanized steel.


B.  Metal Counterflashing: 22 gage (0.8 mm thick) galvanized steel.

.5

EQUIPMENT CURBS



Not Used

.6

SLEEVES

A. Sleeves for Pipes Through Non‑fire Rated Floors:  18 gage 

   (1.2 mm thick) galvanized steel.

B. Sleeves for Pipes Through Non‑fire Rated Beams, Walls, 

Footings, and Potentially Wet Floors:  Steel pipe or 18       gage galvanized steel.

C. Sleeves for Pipes Through Fire Rated and Fire Resistive 

Floors and Walls, and Fire Proofing: Prefabricated fire rated    sleeves including seals, UL listed.


D. Sleeves for Round Ductwork:  Galvanized steel.


E. Sleeves for Rectangular Ductwork:  Galvanized steel or wood.

F. Firestopping Insulation: Glass fiber type, non‑combustible. 


G. Sealant: Acrylic.

PART 3
EXECUTION

.1

INSTALLATION


A.  Install in accordance with manufacturer's instructions.

.2

INSERTS


A. Provide inserts for placement in concrete formwork.

B. Provide inserts for suspending hangers from reinforced  

   concrete slabs and sides of reinforced concrete beams.

C. Provide hooked rod to concrete reinforcement section for  

   inserts carrying pipe over 4 inches (100 mm).

D. Where concrete slabs form finished ceiling, locate inserts 

   flush with slab surface.

E. Where inserts are omitted, drill through concrete slab  from 

   below and provide through‑bolt with recessed square steel 

   plate and nut[ flush with top of] slab.

.3

PIPE HANGERS AND SUPPORTS

A. Support horizontal piping as scheduled, or additionally as 

   required to provide adequate support.

B. Install hangers to provide minimum 1/2 inch (13 mm) space 

   between finished covering and adjacent work.

C. Place hangers within 12 inches (300 mm) of each horizontal 

   elbow.

D. Use hangers with 1‑1/2 inch (38 mm) minimum vertical 

   adjustment.

E. Support horizontal cast iron pipe adjacent to each hub, with 

   5 feet (1.5 m) maximum spacing between hangers.

F. Support vertical piping at every [other] floor.  Support 

   vertical cast iron pipe at each floor at hub.

G. Where several pipes can be installed in parallel and at same 

   elevation, provide multiple or trapeze hangers.

H. Support riser piping independently of connected horizontal 

   piping.

I. Provide copper plated hangers and supports for copper  

   piping.

J. Design hangers for pipe movement without disengagement of 

   supported pipe.

K. Prime coat and paint with two coats. exposed steel hangers 

and supports.  Hangers and supports located in crawl spaces,     pipe shafts, and suspended ceiling spaces are not considered 

     exposed.

.4

EQUIPMENT BASES AND SUPPORTS

A. Provide housekeeping pads of concrete, minimum 4 inches 

100 mm thick and extending 6 inches (150 mm) beyond supported equipment.

B. Provide templates, anchor bolts, and accessories for mounting 

   and anchoring equipment.

C. Construct supports of steel members.  Brace and fasten with 

   flanges bolted to structure.

D. Provide rigid anchors for pipes after vibration isolation 

   components are installed.

.5

FLASHING

A. Provide flexible flashing and metal counterflashing where 

   piping and ductwork penetrate weather or waterproofed walls,          floors, and roofs.

B. Provide acoustical lead flashing around ducts and pipes 

   penetrating equipment rooms, installed in accordance with             manufacturer's instructions for sound control.

C. Provide curbs for mechanical roof installations 14 inches 

   minimum high above roofing surface.  Flash and counter flash with     sheet metal; seal watertight.  Attach counter flashing mechanical

   equipment and lap base flashing     on roof curbs.  Flatten and       solder joints. Do not penetrate roof.


D.  Adjust storm collars tight to pipe with bolts; caulk around top edge.  Use storm collars above roof jacks.  Screw vertical flange section to face of curb.

.6

SLEEVES


A.  Set sleeves in position Provide reinforcing around sleeves.

B. Size sleeves large enough to allow for movement due to    

    expansion and contraction. Provide for continuous insulation          wrapping.

D.  Extend sleeves through floors one inch (25 mm) above 

    finished floor level.  Caulk sleeves.


D.  Where piping or ductwork penetrates floor, ceiling, or wall, close off space between pipe or duct and adjacent work with fire stopping insulation and caulk.  air tight.  Provide close fitting metal collar or escutcheon covers at both sides of penetration.


E.  Install stainless steel escutcheons at finished surfaces.

.7

SCHEDULES














HANGER ROD



PIPE SIZE

   
MAX. HANGER SPACING

DIAMETER



Inches (mm)


Feet (m)



    Inches (mm)



1/2 to 1‑1/4 

    6.5



  
     3/8 



1‑1/2 to 2 


10 


         
3/8 



2‑1/2 to 3


10



      
1/2 



4 to 6 



10 (3)



  
5/8 



8 to 12 


    14 


  
        7/8 



14 and Over


20



  
     1 



PVC (All Sizes)

6


  
        3/8 


END OF SECTION
PAGE  
Error! Main Document Only.
Section 15140 Page 2 of 7     

