

SECTION 15430PRIVATE 


PLUMBING SPECIALTIES

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.
1 PART 1 GENERAL


.1
SECTION INCLUDES



A.
Roof and floor drains.



B.
Cleanouts.



C.
Hose bibs.



D.
Hydrants.



E.
Backflow preventers.



F.
Water hammer arrestors.



G.
Interceptors.



H.
Thermostatic mixing valves.



I.
Catch basins and manholes.


.2
RELATED SECTIONS



A.
Section 15410 ‑ Plumbing Piping.

B. Section 15440 ‑ Plumbing Fixtures.



C.
Reference to General Conditions.


.3
REFERENCES



A.
ANSI/ASSE 1012 – Back flow Preventers with Immediate     Atmospheric Vent.



B.
ANSI/ASSE 1013 – Back flow Preventers, Reduced Pressure Principle.



C.
ANSI/ASSE 1019 ‑ Wall Hydrants, Frost Proof Automatic Draining Anti‑Back flow Types.



D.
ANSI A112.21.1 ‑ Floor Drains.



E.
ANSI A112.26.1 ‑ Water Hammer Arrestors.



F.
AWWA C506 – Back flow Prevention Devices ‑ Reduced Pressure Principle and Double Check Valve Types.



G.
PDI WH‑201 Water Hammer Arresters.


.4
SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Shop Drawings: Indicate dimensions, weights, and placement of openings and holes.



C.
Product Data: Provide component sizes, rough‑in requirements, service sizes, and finishes.



D.
Manufacturer's Installation Instructions: Indicate assembly and support requirements.


.5
PROJECT RECORD DOCUMENTS



A.
Submit under provisions of Section 01700.



B.
Record actual locations of equipment, clean outs, back flow preventers.


.6
OPERATION AND MAINTENANCE DATA



A.
Submit under provisions of Section 01700.



B.
Maintenance Data:  Include installation instructions, spare parts lists, exploded assembly views.


.7
DELIVERY, STORAGE, AND HANDLING



A.
Deliver, store, protect and handle products to site under provisions of Section 01600.



B.
Accept specialties on site in original factory packaging.  Inspect for damage.


.8
EXTRA MATERIALS



A.
Furnish under provisions of Section 01700.

2 PART 2 PRODUCTS


.1
FLOOR DRAINS




Not Used


.2
SERVICE SINKS




Not Used


.3
CLEANOUTS



A.
Manufacturers:



1. JOSAM, ZURN OR WADE



B.
Exterior Surfaced Areas (CO‑1): Round cast nickel bronze access frame and non‑skid cover.



C.
Exterior Unsurfaced Areas: See details on plans..



D.
Interior Finished Floor Areas (CO‑3): [Lacquered] [Galvanized] cast iron, two piece body with double drainage flange, weep holes, [reversible clamping collar,] and adjustable nickel‑bronze strainer, round with scoriated cover in service areas and [round] [square] with depressed cover to accept floor finish in finished floor areas; Model 58010 manufactured by Josam.



E.
Interior Finished Wall Areas (CO‑4): Line type with lacquered cast iron body and round epoxy coated gaskets cover, and round stainless steel access cover secured with machine screw; Model 58740 manufactured by Josam.


.4
HOSE BIBS




Non Freezing type


.5
WATER EJECTOR PUMP




Not Used

 .6  
ELEVATOR PIT SUMP PUMP



A.
Pump shall be automatic 1/3 horsepower minimum with     minimum of 30 GHP @ ft. head.

3 PART 3 EXECUTION


.1
PREPARATION




Not Used


.2
INSTALLATION



A.
Install in accordance with manufacturer's instructions.



B.
Extend clean outs to finished floor or wall surface. Lubricate threaded clean out plugs with mixture of graphite and linseed oil.  Ensure clearance at clean out for rodding of drainage system.

C. Install 12” high air chamber on hot and cold water supply 

Piping to lavatories, sinks and washing machine outlets.


END OF SECTION
PAGE  
Error! Main Document Only.
Section 15430 Page 2 of 3      

