

SECTION 15440PRIVATE 


PLUMBING FIXTURES

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.

1 PART 1 GENERAL


.1

SECTION INCLUDES



A.
Water closets.



B.
Urinals.



C.
Lavatories.



D.
Service sinks.



E.
Electric water coolers.



F.
Drinking fountains.



.2

REFERENCES



A.
ASME A112.18.1 ‑ Finished and Rough Brass Plumbing Fixture Fittings.



B.
ANSI/ASME A112.19.1 ‑ Enameled Cast Iron Plumbing Fixtures.



C.
ANSI/ASME A112.19.2 ‑ Vitreous China Plumbing Fixtures.



D.
ANSI/ASME A112.19.4 ‑ Porcelain Enameled Formed Steel Plumbing Fixtures.



E.
ANSI/ASME A112.19.5 ‑ Trim for Water‑Closet Bowls, Tanks, and Urinals (Dimensional Standards).

F. ANSI/ARI 1010 ‑ Drinking‑Fountains and self-contained, Mechanically‑Refrigerated Drinking‑Water Coolers.



G.
Reference to General Conditions.



.3

SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Product Data: Provide catalogue illustrations of fixtures, sizes, rough‑in dimensions, utility sizes, trim, and finishes.



C.
Manufacturer's Installation Instructions.


.4

OPERATION AND MAINTENANCE DATA



A.
Submit under provisions of Section 01700.



B.
Maintenance Data: Include fixture trim exploded view and replacement parts lists.


.5 
DELIVERY, STORAGE, AND HANDLING



A.
Deliver, store, protect and handle products to site under provisions of Section 01600.



B.
Accept fixtures on site in factory packaging.  Inspect for damage.



C.
Protect installed fixtures from damage by securing areas and by leaving factory packaging in place to protect fixtures and prevent use.


.6

FIELD MEASUREMENTS



A.
Verify that field measurements are as instructed by the manufacturer.



B.
Confirm that millwork is constructed with adequate provision for the installation of countertop lavatories and sinks.


.7

WARRANTY

A. Provide five-year warranty under provisions of Section 01700.



B.
Warranty:  Include coverage of electric water cooler compressor.


.8

EXTRA MATERIALS



A.
Furnish under provisions of Section 01700.



B.
Provide two faucet washers flush valve service kits

2 PART 2 PRODUCTS


.1

FIXTURES: Plumbing contractor shall furnish and install all plumbing fixtures shown on accompanying drawings.  Refer to both plumbing and architectural and provide all fixtures shown on either.  Fixtures shall be complete with all necessary brass and accessories required for a complete installation including traps, escutcheons, angle supplies, basin cocks, etc.  All fixtures shall be new and must be delivered to the building properly crated in perfect condition.




All brass must be of the best quality, lightweight goods will not be accepted.  All brass pipes shall be seamless brass tubing and nipples shall be extra heavy.  All fittings and trim shall be chromium plated heavy brass unless otherwise specified.  “P” traps shall be cast brass with clean-outs.  All exposed piping shall be chromium plated.  Provide cut-off valves at each fixture in both hot and cold water piping.




All plumbing trim shall be Delta or equal – (No Acrylic Allowed.)




For the purpose of establishing type and class of fixtures required, the following plate numbers have been taken from the Kohler catalog unless otherwise indicated.  Fixtures as manufactured by Crane, Eljer, or American Standard, of equivalent quality and manufacturer will be accepted.




All fixtures shall be new except as indicated above.  All wall-hung fixtures shall have factory type mounting brackets in wall.




A.
Water Closet (Men’s Room):
(15” high) – Kihler K-4263-ET. White, vitreous china, siphon jet, elongated water closet.  K-4670-C, solid plastic, white open-front toilet seamless cover and with check hinge; Sloan 110-3 flush valve with vacuum breaker and stop.




B.
Water Closet Handicap (Men’s & Ladies Room):
(18” high) – Kohler K-4268-ET white, vitreous china, siphon jet, elongated water closet, K-4670-C, solid plastic, white, open-front toilet seat less cover and with check hinges.  Sloan 110-3 valve with vacuum breaker and stop.




C.
Lavatory (Men):
Kohler K-2868, 20: x 18” white acid resisting enameled, cast iron, wall mounted lavatory with Josam concealed arm floor anchored carrier.  K-7715 lavatory drain with perforated grate and 1-¼” tailpiece.  Kohler K-9000, 1-¼” cast brass p-trap,K-7606, 3/8” angle supply with stop.  See Architectural drawings for mounting height.  K-9610 soap dispenser.  Gaskets shall be Bradley, with handicap wrist operators.  Mount handicap unit at proper height.

D. Lavatory (Ladies): Kohler 16” round vitreous china, mounted ion cabinet top.  Mixing faucet.




E.
Urinals:

Kohler handicap Model K-5007-T, vitreous china blow out action Delany 452-HVB flush valve.




F.
Tub allowance - $85.00 + tax and shipping charges.



Pre approved equals See list by contractor.

3 PART 3 EXECUTION


.1

EXAMINATION



A.
Verify that walls and floor finishes are prepared and ready for installation of fixtures.



B.
Verify that electric power is available and of the correct characteristics.


.2

PREPARATION



A.
Rough‑in fixture piping connections in accordance with minimum sizes indicated in fixture rough‑in schedule for particular fixtures.


.3

INSTALLATION



A.
Install in accordance with manufacturer's instructions.



B.
Install each fixture with trap, easily removable for servicing and cleaning.



C.
Provide chrome plated rigid or flexible supplies to fixtures with screwdriver stops, reducers, and escutcheons.



D.
Install components level and plumb.



E.
Install and secure fixtures in place with wall supports and bolts.



F.
Seal fixtures to wall and floor surfaces with sealant as specified in Section 07900, color to match fixture.



G.
Solidly attach water closets to floor with lag screws.   Lead flashing is not intended hold fixture in place.


.4

INTERFACE WITH OTHER PRODUCTS



A.
Review millwork shop drawings.  Confirm location and size of fixtures and openings before rough in and installation.


.5

ADJUSTING



A.
Adjust work under provisions of Section 01700.



B.
Adjust stops or valves for intended water flow rate to fixtures without splashing, noise, or overflow.


.6

CLEANING



A.
Clean work under provisions of 01700.



B.
At completion clean plumbing fixtures and equipment.


.7

PROTECTION OF FINISHED WORK



A.
Protect finished Work under provisions of Section 01500. 



B.
Do not permit use of fixtures.


END OF SECTION
PAGE  
Section 15440 Page 4 of 1                 
Error! Main Document Only.

