

SECTION 15682PRIVATE 


AIR COOLED WATER CHILLERS

1 PART 1   GENERAL


.1

SECTION INCLUDES



A.
Chiller package.



B.
Charge of refrigerant and oil.



C.
Controls and control connections.



D.
Chilled water connections.



E.
Starters.



F.
Electrical power connections.


.2

seq level2 \h \r0 

RELATED SECTIONS



A.
Section 15252 ‑ Vibration Isolation.



B.
Section 15510 ‑ Hydronic Piping.



C.
Section 15535 ‑ Refrigeration Piping and Specialties.


.3

seq level2 \h \r0 

REFERENCES



A.
ANSI/ARI 590 ‑ Reciprocating Water ‑ Chilling Packages.



B.
ANSI/ASHRAE 15 ‑ Safety Code for Mechanical Refrigeration.



C.
ANSI/ASHRAE 90A ‑ Energy Conservation in New Building Design.



D.
ANSI/ASME SEC 8 ‑ Boiler and Pressure Vessel Code



E.
ANSI/NEMA MG 1 ‑ Motors and Generators.



F.
ANSI/UL 465 ‑ Central Cooling Air Conditioners.


.4

seq level2 \h \r0 

SUBMITTALS



A.
Submit shop drawings under provisions of Section 01340.



B.
Submit shop drawings indicating components, assembly, dimensions, weights and loadings, required clearances, and location and size of field connections.  Indicate valves, strainers, and thermostatic valves required for complete system.



C.
Submit product data under provisions of Section 01340.



D.
Submit product data indicating rated capacities, weights, specialties and accessories, electrical requirements and wiring diagrams.



E.
Submit written certification that components of package not furnished by manufacturer have been selected in accordance with manufacturers requirements.



F.
Submit manufacturer's installation instructions under provisions of Section 01300.


.5

seq level2 \h \r0 

OPERATION AND MAINTENANCE DATA



A.
Submit operations data under provisions of Section 01730.



B.
Include start‑up instructions, maintenance data, parts lists, controls, and accessories.  Include trouble-shooting guide.



C.
Submit maintenance data under provisions of Section 01730.


.6

seq level2 \h \r0 

REGULATORY REQUIREMENTS



A.
Conform to ANSI/ARI 590 code for testing and rating of reciprocating water chillers.



B.
Conform to ANSI/UL 465 code for construction of reciprocating water chillers and provide UL label.



C.
Conform to ANSI/ASME SEC 8 Boiler and Pressure Vessel Code for construction and testing of reciprocating water chillers.



D.
Conform to ANSI/ASHRAE 15 code for construction and operation of reciprocating water chillers.



E.
Provide certification of inspection for conforming authority having jurisdiction approval.


.7

seq level2 \h \r0 

DELIVERY, STORAGE, AND HANDLING



A.
Store and protect products under provisions of Section 01620.



B.
Comply with manufacturer's installation instructions for rigging, unloading, and transporting units.



C.
Protect units on site from physical damage.


.8
seq level2 \h \r0 
WARRANTY



A.
Provide five-year warranty under provisions of Section 01740.



B.
Warranty: Include coverage for complete assembly including materials and labor. 

.9

seq level2 \h \r0 

MAINTENANCE SERVICE



A.
Furnish service and maintenance of complete assembly for one year from Date of Substantial Completion.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2   PRODUCTS




Not Used


.1

seq level2 \h \r0 

MANUFACTURED UNITS



A.
Provide factory assembled and tested outdoor air cooled liquid chillers consisting of reciprocating compressors, condenser, evaporator, thermal expansion valve, refrigeration accessories, and control panel. Construction and ratings shall be in accordance with ANSI/ARI 590.


.2
seq level2 \h \r0 
COMPRESSORS



A.
Construct semi‑hermetic reciprocating compressors with heat treated forged steel or ductile iron shafts, aluminum alloy connecting rods, automotive type pistons, rings to prevent gas leakage, suction and discharge valves, and sealing surface immersed in oil.



B.
Statically and dynamically balance rotating parts and mount on vibration isolators.



C.
Provide reversible, positive displacement, oil pump lubrication system with oil charging valve, oil level sight glass, oil filter, and magnetic plug on strainer, arranged to ensure adequate lubrication during starting, stopping, and normal operation.



D.
Provide compressor with automatic capacity reduction equipment consisting of suction valve un-loaders.  Use lifting mechanism operated by oil pressure. Provide for unloaded compressor start.



E.
Provide constant speed 1800 rpm compressor motor, suction gas cooled with solid state sensor and electronic winding overheating protection, designed for across‑the-line starting.  Refer to Section 15170.  Furnish with starter.



F.
Provide crankcase heater to evaporate refrigerant returning to crankcase during shut down.  Energize heater when compressor is not operating.


.3

seq level2 \h \r0 

EVAPORATOR



A.
Provide shell and tube type evaporator, seamless or welded steel construction with cast iron or fabricated steel heads, seamless copper tubes or red brass tubes with integral fins, rolled or silver brazed into tube sheets. Provide multiple refrigerant circuits on multiple compressor units.



B.
Design, test, and stamp refrigerant side for 225 psig (1550 kPa) working pressure and water side for 150 psig (1034 kPa) working pressure, in accordance with ANSI/ASME SEC 8.



C.
Insulate with 0.75 inch  minimum thick flexible expanded polyvinyl chloride polyurethane foam insulation with maximum K value of 0.26.  Provide heat tape to protect evaporator to ‑20 degrees F.



D.
Provide water drain connection and thermometer wells for temperature controller and low temperature cutout.


.4
seq level2 \h \r0 
CONDENSERS



A.
Construct condenser coils of aluminum fins mechanically bonded to seamless copper tubing.  Provide sub‑cooling circuits with liquid accumulators.  Air test under water to 425 psig (2900kPa).



B.
Provide vertical discharge direct driven propeller type condenser fans with fan guard on discharge. Equip with roller or ball bearings with grease fittings extended to outside of casing. Provide factory mounted, louvered, galvanized steel coil guard panels with lint screens.



C.
Provide fan motors with permanently lubricated ball bearings and built‑in current and overload protection. Refer to Section 15170.


.5

seq level2 \h \r0 

ENCLOSURES



A.
House components in welded steel frame with galvanized steel panels with weather resistant, baked enamel finish.



B.
Mount starters and disconnects in weatherproof panel provided with full opening access doors.  Provide mechanical interlock to disconnect power when door is opened.


.6

seq level2 \h \r0 

HEAT RECOVERY CONDENSERS



A.
Provide condensers of shell  and tube type, seamless or welded steel construction with cast iron or fabricated steel heads, seamless copper tubes or red brass tubes with integral fins, rolled or silver brazed into tube sheets.



B.
Design, test, and stamp refrigerant side for 450 psig (3100 kPa) working pressure in accordance with ANSI/ASME SEC. 8



C.
Provide 450 psig (3100 kPa) safety relief valve on condenser shell.



D.
Design, test and stamp water side for 150 psig (1034 kPa) working pressure in accordance with ANSI/ASME SEC. 8.


.7
seq level2 \h \r0 
REFRIGERANT CIRCUIT



A.
Provide refrigerant circuits, factory supplied and piped. Refer to Section 15535.



B.
Provide for each refrigerant circuit:




1.
Liquid line solenoid valve.




2.
Filter dryer (replaceable core type).




3.
Liquid line sight glass and moisture indicator.




4.
Thermal expansion valve sized for maximum operating pressure.




5.
Charging valve.




6.
Insulated suction line.




7.
Discharge line check valve.




8.
Compressor discharge service valve.




9.
Condenser pressure relief valve.


.8

seq level2 \h \r0 

seq level3 \h \r0 

CONTROLS



A.
On chiller, mount weatherproof steel control panel, containing starters power and control wiring, molded case disconnect switch, factory wired with single point power connection.



B.
For each compressor, provide part winding starter, non‑recycling compressor overload, starter relay, and control power transformer or terminal for controls power.  Provide manual reset current overload protection.



C.
Provide the following safety controls with indicating lights arranged so that operating any one will shut down machine and require manual reset:




1.
Low chilled water temperature switch.




2.
High discharge pressure switch for each compressor.




3.
Low suction pressure switch for each compressor.




4.
Oil pressure switch.




5.
Flow switch in chilled water line.




6.
Relay for remote mounted emergency shut‑down switch.



D.seq level3 \h \r0 
Provide the following operating controls:




1.
Multi‑step chilled water temperature controller which cycles compressors and activates cylinder unloaders.




2.
Five minute off timer prevents compressor from short cycling.




3.
Periodic pump‑out timer to pump down on chilled water flow and high evaporator refrigerant pressure.




4.
Solenoid valve between heat recovery condenser and receiver to limit refrigerant level in condenser.




5.
Load limit thermostat to limit compressor loading on high return water temperature.




6.
Low ambient control consisting of external damper assembly, controls head pressure for operation down to 0 degrees F (‑18 degrees C).




7.
Hot gas bypass sized for minimum compressor loading [on one compressor only], bypasses hot refrigerant gas to evaporator.



E.seq level3 \h \r0 
Provide pre‑piped gage board with pressure gages for suction and discharge refrigerant pressures, and oil 




pressures for each compressor.



F.
For multiple units, provide remote mounted sequence panel to allow operation in series parallel with lead‑lag switching.

3

seq level1 \h \r0 

seq level2 \h \r0  PART 3   EXECUTION


.1

INSTALLATION



A.
Install in accordance with manufacturer's instructions.



B.
Align chiller package on steel or concrete foundations.



C.
Install units in vibration isolation.  Refer to Section 15252.



D.
Connect to electrical service.
Refer to Section 16180.



E.
Connect to chilled water piping.
Refer to Section 15510. On inlet, provide thermometer well for temperature controller, thermometer well for temperature limit controller, flow switch, flexible pipe connector, and shut‑off valve.  On outlet, provide flexible pipe connector and balancing valve.



F.
Connect to heat recovery condenser water piping.
Refer to Section 15510.  On inlet, provide flexible pipe connector and shut‑off valve.  On outlet, provide flexible pipe connector and shut‑off balancing valve.



G.
Arrange piping for easy dismantling to permit tube cleaning.


.2

seq level2 \h \r0 

MANUFACTURER'S FIELD SERVICES



A.
Prepare and start systems under provisions of Section 01650.



B.
Supply service of factory trained representative for a period of 1 day to supervise testing, dehydration and charging of machine, start‑up, and instruction on operation and maintenance to Owner.



C.
Supply initial charge of refrigerant and oil.


.3

seq level2 \h \r0 

DEMONSTRATION



A.
Provide systems demonstration under provisions of Section 01670.  Provide 8 hours of training of school personnel.



B.
Demonstrate system operation and verify specified performance.  Refer to Section 15990.


END OF SECTION
PAGE  
Section 15682 Page 2 of 6

