

SECTION 15890PRIVATE 


DUCTWORK

1 PART 1   GENERAL


.1

WORK INCLUDED



A.
Low pressure ducts.



B.
Medium and high-pressure ductwork.



C.
Casings.



D.
Fibrous glass ductwork.


.2

seq level2 \h \r0 

RELATED WORK



A.
Section 15290 – Duct Installation.



B.
Section 15910 ‑ Ductwork Accessories.



C.
Section 15936 – Air Inlets and Outlets.


.3
seq level2 \h \r0 
REFERENCES



A.
ASHRAE ‑ Handbook 1981 Fundamentals; Chapter 33 ‑ Duct Design.



B.
ASHRAE ‑ Handbook 1983 Equipment; Chapter 1 ‑ Duct Construction.



C.
ASTM A 90 ‑ Weight of Coating on Zinc‑Coated (Galvanized) Iron or Steel Articles.



D.
ASTM A 167 ‑ Stainless and Heat‑Resisting Chromium‑Nickel Steel Plate, Sheet, and Strip.



E.
ASTM A 525 ‑ General Requirements for Steel Sheet, Zinc-




Coated (Galvanized) by the Hot‑Dip Process.



F.
ASTM A 527 ‑ Steel Sheet, Zinc‑Coated (Galvanized) by Hot-Dip Process, Lock Forming Quality.



G.
ASTM B209 ‑ Aluminum and Aluminum Alloy Sheet and Plate.



H.
NFPA 90A ‑ Installation of Air Conditioning and Ventilating Systems.



I.
NFPA 90B ‑ Installation of Warm Air Heating and Air Conditioning Systems.



J.
NFPA 96 ‑ Installation of Equipment for the Removal of Smoke and Grease‑Laden Vapors from Commercial Cooling Equipment.



K.
SMACNA ‑ Low Pressure Duct Construction Standards.



L.
SMACNA ‑ High Pressure Duct Construction Standards.



M.
SMACNA ‑ Fibrous Glass Duct Construction Standards.



N.
UL 181 ‑ Factory‑Made Air Ducts and Connectors.



O.
Reference to General Conditions.


.4

seq level2 \h \r0 

DEFINITIONS



A.
Duct Sizes: Inside clear dimensions.
For lined ducts, maintain sizes inside lining.



B.
Low Pressure: Three pressure classifications: 1/2 inch WG (125 Pa) positive or negative static pressure and velocities less than 2,000 fpm (10 m/sec); 1 inch WG (250 Pa) positive or negative static pressure and velocities less than 2,500 fpm (12.7 m/sec) and 2 inch WG (500 Pa) positive or negative static pressure and velocities less than 2,500 fpm (12.7 m/sec).



C.
Medium Pressure: Three pressure classifications: 3 inch WG (750 Pa) positive or negative static pressure and velocities less than 4,000 fpm (20 m/sec), 4 inch WG (1,000 Pa) positive static pressure and velocities greater than 2,000 fpm (10 m/sec), 6 inch WG (1,500 Pa) positive static pressure and velocities greater than 2,000 fpm (10 m/sec). 



D.
High Pressure: 10 inch WG (4300 Pa) positive static pressure and velocities greater than 2,000 fpm (10 m/sec).


.5
seq level2 \h \r0 
REGULATORY REQUIREMENTS



A.
Construct ductwork to NFPA 90A and SMACNA standards.


.6

seq level2 \h \r0 

SUBMITTALS



A.
Submit shop drawings and product data under provisions of Section 01300.



B.
Indicate duct fittings, particulars such as gages, sizes, welds, and configuration prior to start of work for low pressure.


.7

seq level2 \h \r0 

DELIVERY, STORAGE, AND HANDLING





Not Used

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2   PRODUCTS


.1
seq level2 \h \r0 
MATERIALS



A.
General: Non‑combustible or conforming to requirements for Class 1 air duct materials, or UL 181.



B.
Steel Ducts: ASTM A525 or ASTM A527 galvanized steel sheet, lock‑forming quality, having zinc coating of 1.25 oz per sq ft (382 g/sq m) for each side in conformance with ASTM A90.



C.
Fasteners: Rivets, bolts, or sheet metal screws.



D.
Sealant: Non‑hardening, water resistant, fire resistive, compatible with mating materials; liquid used alone or with tape, or heavy mastic.



E.
Hanger Rod: Steel, galvanized; threaded both ends, threaded one end, or continuously threaded.


.2
seq level2 \h \r0 
LOW PRESSURE DUCTWORK



A.
Fabricate and support in accordance with SMACNA Low Pressure Duct Construction Standards and ASHRAE handbooks, except as indicated.  Provide duct material, gages, reinforcing, and sealing for operating pressures indicated.



B.
Size round ducts installed in place of rectangular ducts in accordance with ASHRAE table of equivalent rectangular and round ducts.  No variation of duct configuration or sizes permitted except by written permission.



C.
Construct T's, bends, and elbows with radius of not less than 1‑1/2 times width of duct on centerline.  Where not possible and where rectangular elbows are used, provide air foil turning vanes.  Where acoustical lining is indicated, provide turning vanes of perforated metal with glass fiber insulation.



D.
Increase duct sizes gradually, not exceeding 15 degrees divergence wherever possible.  Divergence upstream of equipment shall not exceed 30 degrees; convergence downstream shall not exceed 45 degrees.



E.
Provide easements where low pressure ductwork conflicts with piping and structure.  Where easements exceed 10 percent duct area, split into two ducts maintaining original duct area.



F.  Use double nuts and lock washers on threaded rod supports.

3

seq level1 \h \r0 

seq level2 \h \r0  PART 3   EXECUTION


.1

INSTALLATION



A.
Provide openings in ductwork where required to accommodate thermometers and controllers.  Provide pilot tube openings where required for testing of systems, complete with metal can with spring device or screw to ensure against air leakage.  Where openings are provided in insulated ductwork, install insulation material inside a metal ring.



B.
Locate ducts with sufficient space around equipment to allow normal operating and maintenance activities.



C.
Set plenum doors 6 to 12 inches (150 to 300 mm) above floor.  Arrange door swings so that fan static pressure holds door in closed position.




D.
Connect terminal units to medium or high pressure ducts directly or with one foot (300 mm) maximum length of flexible duct.  Do not use flexible duct to change direction.



E.
Connect diffusers or Troffer boots to low pressure ducts with 5 feet (1.5 m) maximum length of flexible duct.  Hold 




in place with strap or clamp.



F.
During construction, provide temporary closures of metal or taped polyethylene on open ductwork to prevent construction dust from entering ductwork system.


.2

ADJUSTING AND CLEANING



D.
Clean duct system and force air at high velocity through duct to remove accumulated dust.  To obtain sufficient air, clean half the system at a time.  Protect equipment, which may be harmed by excessive dirt with temporary filters, or bypass during cleaning.



E.
Clean duct systems with high power vacuum machines. Protect equipment, which may be harmed by excessive dirt with filters, or bypass during cleaning.  Provide adequate access into ductwork for cleaning purposes.


END OF SECTION
920
Section 15890 Page 2 of 4

