

SECTION 16141PRIVATE 


WIRING DEVICES

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.
1 PART 1   GENERAL


.1

SECTION INCLUDES



A.
Wall switches.



B.
Wall dimmers.



C.
Receptacles.



D.
Device plates and decorative box covers.



E.
Floor box service fittings.



F.
Poke‑through service fittings.

.2 
RELATED SECTIONS seq level2 \h \r0 


A.
Section 16130 ‑ Boxes.

.3
seq level2 \h \r0 
REFERENCES


A.
NEMA WD 1 ‑ General Purpose Wiring Devices.



B.
NEMA WD 6 ‑ Wiring Device Configurations.



C.
Reference to General Conditions.

.4
seq level2 \h \r0 
SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Product Data:  Provide manufacturer's catalog information showing dimensions, colors, and configurations.



C.
Manufacturer's Instructions:




1.
Indicate application conditions and limitations of use stipulated by product testing agency specified under regulatory requirements.




2.
Include instructions for storage, handling, protection, examination, preparation, operation and installation of product.


.5
seq level2 \h \r0 

seq level3 \h \r0 
QUALIFICATIONS



A.
Manufacturer:  Company specializing in manufacturing products specified in this Section with minimum three years documented experience.


.6
seq level2 \h \r0 
REGULATORY REQUIREMENTS



A.
Conform to requirements of ANSI/NFPA 70.



B.
Furnish products listed and classified by underwriters laboratories, Inc. as suitable for purpose specified and shown.

2 PART 2   PRODUCTS

 .1

wall switches

A. Description:  NEMA WD 1,, AC only general-use snap switch.

B. Device Body:  White plastic with toggle handle.

C. Voltage Rating:  120 volts, AC, 480 volts for 277 volt light switches.

D. Current Rating:  15 amperes/20amps.

E. Ratings:  Match branch circuit and load characteristics.

 .2

RECEPTACLES

A. Description:  NEMA WD 1, general-duty general-use receptacle.

B.
Device Body:
White plastic.

C.   Configuration:  NEMA WD 6; type as specified and indicated.

D. Convenience Receptacle:  Type 5-15.

E. GFCI Receptacle: Convenience receptacle with intergral ground fault circuit interrupter to meet regulatory requirements.

F. Telephone Jack:  As located.

 .3

WALL PLATES

A. Decorative Cover plates: Smooth white.
B.
Weatherproof Cover plate: Gasketed cast metal with gasketed device cover.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 3   EXECUTION


.1

EXAMINATION



A.
Verify conditions under provisions of Section 01039 .



B.
Verify outlet boxes are installed at proper height.



C.
Verify wall openings are neatly cut and will be completely covered by wall plates.



D.
Verify floor boxes are adjusted properly.



E.
Verify branch circuit wiring installation is completed, tested, and ready for connection to wiring devices.


.2
seq level2 \h \r0 
PREPARATION



A.
Provide extension rings to bring outlet boxes flush with finished surface.



B.
Clean debris from outlet boxes.


.3

seq level2 \h \r0 

INSTALLATION



A.
Install products in accordance with manufacturer's instructions.



B.
Install devices plumb and level.



C.
Install switches with OFF position down.



D.
Connect wiring device grounding terminal to branch circuit equipment grounding conductor.


E.
Install decorative plates on switch, receptacle, and blank outlets in finished areas.


F.
Connect wiring devices by wrapping conductor around screw terminal.


G.
Use jumbo size plates for outlets installed in masonry walls.


H.
Install galvanized steel plates on outlet boxes and junction boxes in unfinished areas, above accessible ceilings, and on surface mounted outlets.

.4
seq level2 \h \r0 
INTERFACE WITH OTHER PRODUCTS



A.
Coordinate locations of outlet boxes provided under Section 16130 to obtain mounting heights [specified and] indicated on Drawings.



B.
Install wall switch 48 inches (1.2 m) above finished floor.



C.
Install convenience receptacle 24 inches above finished floor.



D.
Install convenience receptacle 6 inches (150 mm) above counter backsplash of counter.



E.
Install telephone jack 18 inches (450 mm) above finished floor.


F.
Install telephone jack for wall telephone 48 bove finished floor.

.5
seq level2 \h \r0 
FIELD QUALITY CONTROL



A.
Inspect each wiring device for defects.



B.
Operate each wall switch with circuit energized and verify proper operation.



C.
Verify that each receptacle device is energized.



D.
Test each receptacle device for proper polarity.



E.
Test each GFCI receptacle device for proper operation.



F.
Verify that each telephone jack is properly connected and circuit is operational.


.6
seq level2 \h \r0 
ADJUSTING



A.
Adjust devices and wall plates to be flush and level.


END OF SECTION
PAGE  
Section 16141 Page 2 of 3

