

SECTION 16170PRIVATE 


GROUNDING AND BONDING

1 PART 1   GENERAL


.1

SECTION INCLUDES



A.
Grounding electrodes and conductors.



B.
Equipment grounding conductors.



C.
Bonding.


.2seq level2 \h \r0 

RELATED SECTIONS

A. Section 02781 – Site Grounding

B. Section 03200 – Concrete Reinforcement

C. Section 03300 – Cast-in-Place concrete

D. Section 16670 – Lightning Protection System.

 .3

REFERENCES



A.
ANSI/NFPA 70 ‑ National Electrical Code.



B.
Reference to General Conditions.


.4seq level2 \h \r0 

GROUNDING ELECTRODE SYSTEM



A.
Metal underground water pipe.



B.
Metal frame of the building.

C. Concrete-encased electrode.

D. Ground ring specified in Section 02781.

E. Metal underground gas piping system.

F. Rod electrode.

G. Plate electrode.

H. Active electrode.


.5
seq level2 \h \r0 
PERFORMANCE REQUIREMENTS



A.
Grounding System Resistance: 25 ohms.


.6
seq level2 \h \r0 
SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Product Data: Provide data for grounding electrodes and connections.



C.
Test Reports: Indicate overall resistance to ground and resistance of each electrode.



D.
Manufacturer's Instructions:
Include instructions for storage, handling, protection, examination, preparation and installation of exothermic connectors.


.7
seq level2 \h \r0 
PROJECT RECORD DOCUMENTS



A.
Submit under provisions of Section 01700.



B.
Accurately record actual locations of grounding electrodes.


.8
seq level2 \h \r0 
QUALIFICATIONS



A.
Manufacturer:  Company specializing in manufacturing Products specified in this Section with minimum three years experience.


.9
seq level2 \h \r0 
REGULATORY REQUIREMENTS



A.
Conform to requirements of ANSI/NFPA 70.



B.
Furnish products listed and classified by Underwriters Laboratories, Inc. as suitable for purpose specified and shown.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2   PRODUCTS


 .1
ROD ELECTRODE



A.seq level3 \h \r0 
Material:  Copper‑clad steel.



B.
Diameter:  3/4 inch.



C.
Length:    10 feet.



 .2
MECHANICAL CONNECTORS



A.
Material: bronze.


 .3
seq level2 \h \r0 

seq level3 \h \r0 WIRE



A.
Material:  Stranded copper.



B.  Grounding Electrode Conductor: Size to meet NFPA 70 requirements.

3

seq level1 \h \r0 

seq level2 \h \r0  PART 3   EXECUTION


.1

EXAMINATION



A.
Inspect grounding and bonding system conductors and connections for tightness and proper installation.



B.
Use suitable test instrument to measure resistance to ground of system.  Perform testing in accordance with test instrument manufacturer's recommendations using the fall-of‑potential method.







END OF SECTION

PAGE  
Section 16170 Page 1 of 1

