

SECTION 16190PRIVATE 


SUPPORTING DEVICES

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.
1 PART 1 
GENERAL


.1

SECTION INCLUDES



A.
Conduit and equipment supports.



B.
Anchors and fasteners.


.2

seq level2 \h \r0 

REFERENCES



A.
NECA ‑ National Contractors Association.



B.
ANSI/NFPA 70 ‑ National Electrical Code.



C.
Reference to General Conditions.

.3

seq level2 \h \r0 

SUBMITTALS



A.
Submit under provisions of Section 01300. 



B.
Product Data:  Provide manufacturer's catalog data for fastening systems.



C.
Manufacturer's Instructions:
Indicate application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements.  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of Product.


.4

seq level2 \h \r0 

REGULATORY REQUIREMENTS



A.
Conform to requirements of ANSI/NFPA 70.



B.
Furnish products listed and classified by Underwriters Laboratories, Inc. as suitable for purpose specified and shown.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2 
PRODUCTS


.1

PRODUCT REQUIREMENTS



A.
Materials and Finishes: Provide adequate corrosion resistance.



B.
Provide materials, sizes, and types of anchors, fasteners and supports to carry the loads of equipment and conduit.  Consider weight of wire in conduit when selecting products.



C.
Anchors and Fasteners:




1.
Concrete Structural Elements: Use, expansion anchors. 



2.
Steel Structural Elements: Use beam clamps.




3.
Concrete Surfaces: Use expansion anchors.




4.
Hollow Masonry, Plaster, and Gypsum Board Partitions:  Use toggle bolts and hollow wall fasteners.




5.
Solid Masonry Walls:
Use expansion anchors.




6.
Sheet Metal: Use sheet metal screws.




7.
Wood Elements:
Use wood screws.

3

seq level1 \h \r0 

seq level2 \h \r0  PART 3 
EXECUTION


.1

INSTALLATION



A.
Install products in accordance with manufacturer's instructions.



B.
Provide anchors, fasteners, and supports in accordance with NECA "Standard of Installation".



C.
Do not fasten supports to pipes, ducts, mechanical equipment, and conduit.



D.
Do not use spring steel clips and clamps.


   E.  Fabricate supports from structural steel or steel channel.               Rigidly weld members or use hexagon head bolts to present neat           appearance with adequate strength and rigidity.  Use spring lock         washers under all nuts.
 



F.
Install surface‑mounted cabinets and panelboards with minimum of four anchors.


G.
In wet and damp locations use steel channel supports to stand cabinets and panelboards one inch (25 mm) off wall.


H.
Use sheet metal channel to bridge studs above and below cabinets and panelboards recessed in hollow partitions.

END OF SECTION
1
Section 16190 Page 2 of 2

