16.12
BOXES
16.12.1
Outlet Boxes

Outlet boxes shall be of the style and type to accept the device specified on the project drawings.  Where more than one device is to be installed in an outlet, gang type boxes shall be used.  Outlet boxes for surface mounted devices in non-hazardous areas shall be 'FD' deep boxes.  Outlet boxes for flush mounted devices in non-hazardous areas shall be standard galvanized steel boxes for dry wall construction designed for use with rigid metallic conduit.  Metal covers shall be used.
16.12.2
Junction Boxes and Pull Boxes

Junction boxes and pull boxes four inch square and smaller shall be cast metal with cast blank covers.  Junction boxes and pull boxes over four inch square in non-hazardous indoor areas shall be constructed of code-gauge galvanized sheet steel and shall have screw fastened covers.  Outdoor type junction boxes shall have watertight hubs and gasketed covers fastened with cadmium plated or stainless steel screws.

STD SPEC
16.12 - 1

