Replace the main electrical equipment serving the Human Performance Center buildings on the UNO Main Campus.

Scope of Work
The Contractor shall provide all plant, materials and labor to demolish & replace the existing 500 KVA dry type 13.8 KV/208,120 volt distribution transformer located in the first floor electrical room of the Human Performance Center, including primary and secondary switches, an existing distribution panel located on the second floor & being converted into a junction box, and all related conductors, etc. and to provide a new outdoor liquid cooled transformer & switch with a capacity of 500 KVA and a total capacity of 750 KVA when a fan is added at a later time.  Provide new underground feeders & tie in at existing 13.8KV manhole, as located on the drawings.  Provide new transformer pad, fencing, etc., all as shown on the drawings.

The existing transformer, switchgear & distribution panel board removed by the above work shall become the property of the contractor, and shall be removed from the site.  The contractor shall video tape the project area prior to starting work, and on completion of the project work.
Repair all areas of the building and grounds that were damaged by work of this contract.  Prepare lawn and re sod where equipment operation and project installation has damaged lawn.

Clean and paint all damaged surfaces with two coats of paint to match existing.

In the event that the contractor, through his own negligence, causes an outage of the building that extends into normal weekday activities, the contractor shall project a portable generator sufficiently sized to carry all electrical loads of the building during normal class activities, for the duration of the outage.

