ST. TAMMANY FIRE PROTECTION DISTRICT NO. 1

NEW TRAINING FACILITY

34780 S. RANGE ROAD 

SLIDELL LA  70460


Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262416
PANELBOARDS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes distribution panelboards and lighting and appliance branch-circuit panelboards.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For each panelboard and related equipment.

1. Include dimensioned plans, elevations, sections, and details. Show tabulations of installed devices, equipment features, and ratings.

2. Detail enclosure types and details for types other than NEMA 250, Type 1.

3. Detail bus configuration, current, and voltage ratings.

4. Short-circuit current rating of panelboards and overcurrent protective devices.

Retain first subparagraph below if series rating of overcurrent protective devices is used.

5. Include evidence of NRTL listing for series rating of installed devices.

6. Detail features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

7. Include wiring diagrams for power, signal, and control wiring.

8. Include time-current coordination curves for each type and rating of overcurrent protective device included in panelboards.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See SEI/ASCE 7 for certification requirements for equipment and components.

A. Field quality-control reports.

B. Panelboard schedules for installation in panelboards.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with NEMA PB 1.

C. Comply with NFPA 70.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace transient voltage suppression devices that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods with manufacturers listed in Part 2 articles.

1. Warranty Period: Five years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 GENERAL REQUIREMENTS FOR PANELBOARDS

Retain first paragraph below for projects in seismic areas. Coordinate with "Informational Submittals" Article for submittal of manufacturer's seismic qualification certification.

A. Fabricate and test panelboards according to IEEE 344 to withstand seismic forces.
B. Enclosures: Flush-mounted cabinets.

1. Rated for environmental conditions at installed location.

See "Enclosures" Article in the Evaluations for discussion of enclosure types. Coordinate first four subparagraphs below with Drawings (by identifying the designated areas) or schedules (by including the required enclosure type). Availability of some enclosure types are limited by a panelboard's ampacity rating, included devices, or physical size; consult manufacturers for availability of, and limitations on, other than Type 1 enclosures.

a. Indoor Dry and Clean Locations: NEMA 250, Type 1.

b. Outdoor Locations: NEMA 250, Type 3R.

c. Other Wet or Damp Indoor Locations: NEMA 250, Type 4.

Retain one of first two subparagraphs below.

2. Front: Secured to box with concealed trim clamps. For surface-mounted fronts, match box dimensions; for flush-mounted fronts, overlap box.

3. Hinged Front Cover: Entire front trim hinged to box and with standard door within hinged trim cover.

Retain first subparagraph below for use with lighting and appliance branch-circuit and distribution panelboards with doors.

4. Directory Card: Inside panelboard door, mounted in transparent card holder.

Retain first paragraph below, and coordinate with Drawings and schedules, if Project requirements include identifying specific entry locations for incoming service or feeder raceways.

C. Incoming Mains Location: Top.
D. Phase, Neutral, and Ground Buses: Hard-drawn copper.
Include instructions in first paragraph below if special sizing or oversizing of lugs is required, if allowing optional use of aluminum for circuits sized for copper conductors, or when upsizing conductors for voltage drop.

E. Conductor Connectors: Suitable for use with conductor material and sizes.

1. Material: Hard-drawn copper.

2. Main and Neutral Lugs: Mechanical type.

See Editing Instruction No. 4 in the Evaluations for guidance on using compression versus mechanical lugs in first three subparagraphs below.

3. Ground Lugs and Bus Configured Terminators: Compression or Mechanical type.

Retain first paragraph below for panelboards that incorporate one or more main service disconnecting and overcurrent protective devices and that are used as the service entrance, outside feeder, or separately derived source means of disconnect and overcurrent protection.

F. Service Equipment Label: NRTL labeled for use as service equipment for panelboards with one or more main service disconnecting and overcurrent protective devices.

Retain first paragraph below if future provisions are required.

G. Future Devices: Mounting brackets, bus connections, filler plates, and necessary appurtenances required for future installation of devices.

Retain one or both paragraphs below for series-rated system or system that has panelboards and circuit breakers rated for full value of short-circuit current available at location of equipment.

H. Panelboard Short-Circuit Current Rating: Rated for series-connected system with integral or remote upstream overcurrent protective devices and labeled by an NRTL. Include size and type of allowable upstream and branch devices, and listed and labeled for series-connected short-circuit rating by an NRTL.

I. Panelboard Short-Circuit Current Rating: Fully rated to interrupt symmetrical short-circuit current available at terminals.

2.2 PERFORMANCE REQUIREMENTS

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

Retain "Surge Suppression" Paragraph below unless field-mounted SPDs are used. Retain "Type 1" option for service equipment where the device is installed ahead of the service disconnect. Retain "Type 2" option for panelboards on the load side of the service disconnect. Field-mounted SPDs are specified in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits."

B. Surge Suppression: Factory installed as an integral part of indicated panelboards, complying with UL 1449 SPD Type 1.

2.3 DISTRIBUTION PANELBOARDS

Distribution panelboards, as specified in this article, fall under requirements of "Power Panelboards" in NFPA 70.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

C. Panelboards: NEMA PB 1, power and feeder distribution type.

Distribution panelboards, as standard, do not have doors; consult manufacturers for availability and types of doors. Retain first paragraph below if panelboards have doors.

D. Doors: Secured with vault-type latch with tumbler lock; keyed alike.

Select one of first two options in first paragraph below for panelboards with main overcurrent protective devices; select third option for panelboards with only main lugs for the incoming feeder. Consult manufacturers for limitations on ratings for each type of device selected.

E. Mains: Circuit breaker.

Retain one of three paragraphs below. Allowing only bolt-on circuit breakers will exclude Square D (Schneider Electric), which uses plug-in types with a positive-locking feature, as an approved manufacturer.

F. Branch Overcurrent Protective Devices: For Circuit-Breaker Frame Sizes 125 A and Smaller: Bolt-on circuit breakers.

G. Branch Overcurrent Protective Devices: For Circuit-Breaker Frame Sizes Larger Than 125 A: Bolt-on circuit breakers; plug-in circuit breakers where individual positive-locking device requires mechanical release for removal.

H. Branch Overcurrent Protective Devices: Fused switches.

2.4 LIGHTING AND APPLIANCE BRANCH-CIRCUIT PANELBOARDS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

C. Panelboards: NEMA PB 1, lighting and appliance branch-circuit type.

Retain first paragraph below if mains are not indicated on Drawings.

D. Mains: lugs only.

E. Branch Overcurrent Protective Devices: Bolt-on circuit breakers, replaceable without disturbing adjacent units.

F. Doors: Concealed hinges; secured with flush latch with tumbler lock; keyed alike.

G. Column-Type Panelboards: Narrow gutter extension, with cover, to overhead junction box equipped with ground and neutral terminal buses.

2.5 DISCONNECTING AND OVERCURRENT PROTECTIVE DEVICES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

Coordinate two paragraphs below with Drawings. See the "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for guidance on making selections.

C. Molded-Case Circuit Breaker (MCCB): Comply with UL 489, with interrupting capacity to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers: Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Electronic trip circuit breakers with rms sensing; field-replaceable rating plug or field-replicable electronic trip; and the following field-adjustable settings:

Retain one or more of first four subparagraphs below and coordinate required adjustable settings with Section 260573 "Overcurrent Protective Device Coordination Study." See "Electronic rms Trip versus MCCBs" Paragraph in "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for additional guidance on specifying full- or standard-function features.

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

4. Current-Limiting Circuit Breakers: Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

Retain first subparagraph below for GFCI circuit breakers for personnel ground-fault protection as required by NFPA 70; retain second subparagraph for GFEP circuit breakers (e.g., for self-limiting, heat-trace cables) as required by NFPA 70. GFCI, GFEP, and AFCI circuit breakers are only available fully rated up to interrupting ratings of 22 kA. For panelboards subject to fault currents above 22 kA, series ratings must be used.

5. GFCI Circuit Breakers: Single- and two-pole configurations with Class A ground-fault protection (6-mA trip).

6. Ground-Fault Equipment Protection (GFEP) Circuit Breakers: Class B ground-fault protection (30-mA trip).

7. Arc-Fault Circuit Interrupter (AFCI) Circuit Breakers: Comply with UL 1699; 120/240-V, single-pole configuration.

8. Molded-Case Circuit-Breaker (MCCB) Features and Accessories:

Not all features and accessories listed in subparagraphs below are available for every rating and from every listed manufacturer. Verify availability and unique characteristics with manufacturers selected.

a. Standard frame sizes, trip ratings, and number of poles.

See Editing Instruction No. 4 in the Evaluations for guidance on using compression versus mechanical lugs.

b. Lugs: Mechanical style, suitable for number, size, trip ratings, and conductor materials.

c. Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge (HID) lighting circuits.

Select first option in first subparagraph below for solid-state trip units; select second option for thermal-magnetic units. If selecting second option, also retain "Shunt Trip" Subparagraph below.

d. Ground-Fault Protection: Integrally mounted relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

For first subparagraph below, 120-V units trip at 55 percent or more of rated voltage; all other voltages trip at 75 percent or more of rated voltage.

e. Shunt Trip: 120V trip coil energized from separate circuit, set to trip at 55 percent of rated voltage.

Device defined in subparagraph below is not, and should not be, used as a safety device; it is used for holding the circuit-breaker handle in designated position to avoid accidental interruption of important circuits such as circuits for fire-alarm control panel or emergency lighting.

f. Handle Clamp: Loose attachment, for holding circuit-breaker handle in on position.

D. Fused Switch: NEMA KS 1, Type HD; clips to accommodate specified fuses; lockable handle.

2.6 ACCESSORY COMPONENTS AND FEATURES

Retain paragraph below for circuit breakers with solid-state trip devices; delete if specified elsewhere, such as in Section 262413 "Switchboards."

A. Portable Test Set: For testing functions of solid-state trip devices without removing from panelboard. Include relay and meter test plugs suitable for testing panelboard meters and switchboard class relays.

PART 3 -  EXECUTION

3.1 INSTALLATION

Referenced NECA and NEMA standards in first paragraph below include similar requirements. See "Testing and Inspecting" Article in the Evaluations.

A. Receive, inspect, handle, store and install panelboards and accessories according to NEMA PB 1.1.

Ensure that, whatever height is selected for top of trim in first paragraph below, the operating handle of top-most switch or circuit breaker, in on position, is not higher than 79 inches (2000 mm)above finished floor or grade.
B. Mount top of trim 90 inches above finished floor unless otherwise indicated.

C. Mount panelboard cabinet plumb and rigid without distortion of box. Mount recessed panelboards with fronts uniformly flush with wall finish and mating with back box.

D. Install overcurrent protective devices and controllers not already factory installed.

Subparagraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

1. Set field-adjustable, circuit-breaker trip ranges.

E. Install filler plates in unused spaces.

Retain first paragraph below if ceilings are accessible or there are raised floors, or when panelboards are located in spaces that will be finished.

F. Stub four 1-inch empty conduits from panelboard into accessible ceiling space or space designated to be ceiling space in the future.

G. Arrange conductors in gutters into groups and bundle and wrap with wire ties.

H. Comply with NECA 1.

3.2 IDENTIFICATION

A. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs. complying with Section 26055 "Identification for Electrical Systems."

B. Create a directory to indicate installed circuit loads and incorporating Owner's final room designations. Obtain approval before installing. Use a computer or typewriter to create directory; handwritten directories are not acceptable.

C. Panelboard Nameplates: Label each panelboard with a nameplate complying with requirements for identification specified in Section 26055 "Identification for Electrical Systems."

Retain paragraph below if nameplates are required for individual overcurrent devices in distribution panelboards.

D. Device Nameplates: Label each branch circuit device in distribution panelboards with a nameplate complying with requirements for identification specified in Section 26055 "Identification for Electrical Systems."

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain first two paragraphs below to describe tests and inspections to be performed.

B. Acceptance Testing Preparation:

1. Test insulation resistance for each panelboard bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

C. Tests and Inspections:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Panelboards will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports, including a certified report that identifies panelboards included and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

END OF SECTION 262416
	PANELBOARDS
	262416 - 1



