[image: image1.jpg]DAMMON

ENGINEERING | NLC.

Archilecls & FEngineers





554 Old Spanish Trail

Slidell, LA  70458

P  985.649.5832
www.dammonengineering.com

info@dammonengineering.com


Notice of Addendum #3 – February 20, 2026

PROJECT:


St. Tammany Fire Protection District No. 1




Fire Station #10



2745 Lakeshore Vista Blvd.




Slidell, LA  70461

PROJECT NO.:

2519

FROM:


DAMMON ENGINEERING




554 Old Spanish Trail




Slidell, LA  70458




(985) 649-5832

TO:


All on Record Holding Bidding Documents

This Addendum forms a part of the Contract Documents and modifies the original Bidding Documents dated December 3, 2025.  The contents of this Addendum shall be included in the Contract Documents when the Agreement is executed.  Changes made by this Addendum take precedence over the Documents of earlier date.

Acknowledge receipt of this Addendum in the space provided on the Bid Form.

GENERAL

1. The addendum is to be distributed to registered Plan Holders via Central Bidding.

MODIFICATIONS TO THE SPECIFICATIONS
N/A
MODIFICATIONS TO THE DRAWINGS

N/A
GENERAL QUESTIONS
The following questions were submitted. Answers are in bold.

2.  How tall is the flag pole.

  Height: 25', Diameter: 4", Color: Satin and shall be rated for 140 mph wind       
load. 
3.  Please clarify what back flow is to be used for the 2” sewer force main.
    See the attached pdfs of the check valve and valve cover.

SUBSTITUTIONS
N/A
ADDENDUM No. 01 CONSISTS OF:  
    Addendum Cover Letter and Narrative (2 pages)

   DRAWING SHEETS   (0 pages)

   SKETCHES (0 page)

    Attachments (3 pages)

   for a total of (5 pages) FOUR DOCUMENT SHEETS
All planholders must acknowledge receipt of this addendum via the
LOUISIANA UNIFORM PUBLIC WORK BID FORM.
Since 1984

