ST. TAMMANY FIRE PROTECTION DISTRICT NO. 1

FIRE STATION #10

2745 LAKESHORE VISTA BLVD

SLIDELL, LA 70461


Copyright 2002 (R 11/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA
SECTION 133419
METAL BUILDING SYSTEMS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.
PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes metal building systems that consist of integrated sets of mutually dependent components including structural framing and accessories.
If alternates, allowances, or unit prices apply to Work of this Section, insert brief paragraphs here to alert Contractor and reference appropriate Division 1 Sections for specific details.
1.3 DEFINITIONS
First five definitions below are from MBMA's "Metal Building Systems Manual," with additional clarification added in parentheses.
A. Bay:  Dimension between main frames measured normal to frame (at centerline of frame) for interior bays, and dimension from centerline of first interior main frame measured normal to end wall (outside face of end-wall girt) for end bays.

B. Building Length:  Dimension of the building measured perpendicular to main framing from end wall to end wall (outside face of girt to outside face of girt).

C. Building Width:  Dimension of the building measured parallel to main framing from sidewall to sidewall (outside face of girt to outside face of girt).

D. Clear Span:  Distance between supports of beams, girders, or trusses (measured from lowest level of connecting area of a column and a rafter frame or knee).

E. Eave Height:  Vertical dimension from finished floor to eave (the line along the sidewall formed by intersection of the planes of the roof and wall).

F. Clear Height under Structure:  Vertical dimension from finished floor to lowest point of any part of primary or secondary structure, not including crane supports, located within clear span.

G. Terminology Standard:  Refer to MBMA's "Metal Building Systems Manual" for definitions of terms for metal building system construction not otherwise defined in this Section or in referenced standards.

1.4 SYSTEM DESCRIPTION

First option in paragraph below allows manufacturers to use their own standard fabrications.

A. General:  Provide a complete, integrated set of metal building system manufacturer's standard mutually dependent components and assemblies that form a metal building system capable of withstanding structural and other loads, thermally induced movement, and exposure to weather without failure or infiltration of water into building interior.  Include primary and secondary framing and accessories complying with requirements indicated.

1. Provide metal building system of size and with spacings, slopes, and spans indicated.

Revise paragraph and subparagraphs below to correlate with information about design indicated on Drawings.

B. Primary Frame Type:

Retain one or more of six subparagraphs below.

1. Rigid Clear Span:  Solid-member, structural-framing system without interior columns.

Retain one of first two paragraphs below.  Load-bearing end walls (columns and rafters) in first paragraph are generally more economical than frames.  Second paragraph allows future expansion of building without replacing end frame.

C. End-Wall Framing:  Manufacturer's standard, for buildings not required to be expandable, consisting of primary frame, capable of supporting one-half of a bay design load, and end-wall columns.

D. Secondary Frame Type:  Manufacturer's standard purlins and joists.

Manufacturers can custom design metal buildings to almost any eave height to suit Project.  Dimensions in paragraph below are common.  Use of manufacturer's standard height usually results in lowest cost.

E. Eave Height: As indicated by nominal height on Drawings.

Revise two paragraphs below if roof or wall system uses metal panels from Division 7 Sections.

Insert other requirements to suit Project (e.g., brick masonry for custom-designed exterior elevations).

1.5 SYSTEM PERFORMANCE REQUIREMENTS

Retain paragraph and subparagraphs below or indicate structural performance requirements on Drawings.  If requirements in MBMA's "Metal Building Systems Manual" are used as design criteria, verify that they meet local building code requirements.

A. Structural Performance:  Provide metal building systems capable of withstanding the effects of gravity loads and the following loads and stresses within limits and under conditions indicated:

1. Engineer metal building systems according to procedures in MBMA's "Metal Building Systems Manual."

Requirements under each set of performance criteria below are examples only.  Revise to suit Project.  Consult a structural engineer experienced in engineering assemblies of type indicated to quantify design loads applicable to Project.  Verify compliance with codes.

If retaining first subparagraph below, indicate minimum loads on Drawings.  Include applicable live, dead, snow, collateral, seismic, wind, and uplift loads and load combinations.

2. Design Loads:  As indicated on Drawings.

3. Design Loads:  As required by MBMA's "Metal Building Systems Manual." and ASCE 7-10, "Minimum Design Loads for Buildings and Other Structures."

Retain one of two subparagraphs above or delete both and retain first six subparagraphs and associated subparagraph below.  Add specific loads and factors to suit Project.

4. Live Loads:  Include vertical loads induced by the building occupancy indicated on Drawings.  Include loads induced by maintenance workers, materials, and equipment for roof live loads.

5. Wind Loads:  Include horizontal loads induced by a basic wind speed corresponding to a 50-year, mean-recurrence interval at Project site of 155 mph.

6. Collateral Loads:  Include additional dead loads other than the weight of metal building system for permanent items such as sprinklers, mechanical systems, electrical systems, and ceilings.

Delete first subparagraph below if no cranes or equipment.

7. Auxiliary Loads:  Include dynamic live loads, such as those generated by cranes and materials-handling equipment indicated on Drawings.

8. Load Combinations:  Design metal building systems to withstand the most critical effects of load factors and load combinations as required by MBMA's "Metal Building Systems Manual." and ASCE 7-10, "Minimum Design Loads for Buildings and Other Structures."

Retain first subparagraph and associated subparagraphs below with or without loads above.

9. Deflection Limits:  Engineer assemblies shall be designed to accommodate long-term irreversible deflections under sustained loads:
Deflections in first four subparagraphs below are examples only.  Purlins and rafters supporting plaster ceilings generally require deflection limit of 1/360 of the span.  Masonry walls may require deflection limits of 1/600 or 1/720.  Verify limits with authorities having jurisdiction; manufacturer's standards are typically less stringent.
a. Purlins and Rafters:  Vertical deflection of 1/240 of the span.

10. Design secondary framing system to accommodate deflection of primary building structure and construction tolerances, and to maintain clearances at openings.

Although ASTM E 1592 applies to all types of single-sheet metal roof panels, only the standing-seam metal roof panels from most manufacturers can meet the following requirement.

11. Provide metal panel assemblies capable of withstanding the effects of loads and stresses indicated, based on testing according to ASTM E 1592.

Revise first paragraph below to indicate specific loads determined by Project's structural engineer or refer to loads indicated on Drawings.  Model building codes and ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

B. Seismic Performance:  Design and engineer metal building systems capable of withstanding the effects of earthquake motions determined according to ASCE 7-10, "Minimum Design Loads for Buildings and Other Structures":  Sections 11-23.

C. Thermal Movements:  Provide metal panel systems that allow for thermal movements resulting from the following maximum change (range) in ambient and surface temperatures by preventing buckling, opening of joints, overstressing of components, failure of joint sealants, failure of connections, and other detrimental effects.  Base engineering calculation on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Differential values in subparagraph below are suitable for most of the U.S.  Revise to suit local conditions.

1. Temperature Change (Range):  120 deg F, ambient; 180 deg F, material surfaces.

ASHRAE/IESNA 90.1, 1999 edition, includes maximum U-factors for opaque elements of overall assemblies and minimum R-values for insulation of metal buildings, depending on the climate where Project is located.

Pressure differences in two paragraphs below are examples only.  Revise to suit Project.  Value shown for the test-pressure difference for metal roof panels is for roofs with slope less than or equal to 30 degrees.

Delete paragraph below if UL class roof is not required.  Verify that products are listed in UL's "Roofing Materials & Systems Directory."

D. Wind-Uplift Resistance:  Provide metal roof panel assemblies that comply with UL 580 for Class 90.

If fire resistance is required, indicate on Drawings both the fire-resistance rating of each assembly and the designations of testing and inspecting agency that has established the assembly's fire-test-response characteristics.

1.6 SUBMITTALS

A. Product Data:  Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each type of the following metal building system components:

1. Structural-framing system.

2. Accessories.

B. Shop Drawings:  For the following metal building system components.  Include plans, elevations, sections, details, and attachments to other work.
Retain subparagraph below if products are required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify product's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."
1. For installed products indicated to comply with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
Usually retain remaining subparagraphs and associated subparagraphs.
2. Anchor-Bolt Plans:  Submit anchor-bolt plans before foundation work begins.  Include location, diameter, and projection of anchor bolts required to attach metal building to foundation.  Indicate column reactions at each location.

3. Structural-Framing Drawings:  Show complete fabrication of primary and secondary framing; include provisions for openings.  Indicate welds and bolted connections, distinguishing between shop and field applications.  Include transverse cross-sections.
Delete subparagraph and associated subparagraphs below for large-scale details if Product Data from manufacturer are adequate.  Delete specific scale if not required.

Delete paragraph above if colors are preselected and specified or scheduled.  Retain paragraph and subparagraphs below with or without above.
C. Product Certificates:  For each type of metal building system, signed by product manufacturer.
Letter of Design Certification below is useful in ensuring compliance with requirements and in comparing competitive quotes from several manufacturers.  MBMA's "Metal Building Systems Manual" expressly excludes compliance with codes, except as noted in Letter of Design Certification.
1. Letter of Design Certification:  Signed and sealed by a qualified professional engineer.  Include the following:

a. Name and location of Project.

b. Order number.

c. Name of manufacturer.

d. Name of Contractor.

e. Building dimensions including width, length, height, and roof slope.

f. Indicate compliance with AISC standards for hot-rolled steel and AISI standards for cold-rolled steel, including edition dates of each standard.

g. Governing building code and year of edition.

h. Design Loads:  Include dead load, roof live load, collateral loads, roof snow load, deflection, wind loads/speeds and exposure, seismic design category or effective peak velocity-related acceleration/peak acceleration, and auxiliary loads (cranes).

i. Load Combinations:  Indicate that loads were applied acting simultaneously with concentrated loads, according to governing building code.

j. Building-Use Category:  Indicate category of building use and its effect on load importance factors.

k. AISC Certification for Category MB:  Include statement that metal building system and components were designed and produced in an AISC-Certified Facility by an AISC-Certified Manufacturer.

D. Welding certificates.
Retain paragraph below if retaining "Erector Qualifications" Paragraph in "Quality Assurance" Article.
E. Erector Certificate:  Signed by manufacturer certifying that erector complies with requirements.
Retain paragraph below if retaining "Manufacturer Qualifications" Paragraph in "Quality Assurance" Article.
F. Manufacturer Certificate:  Signed by manufacturer certifying that products comply with requirements.
Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.
G. Qualification Data:  For Erector, manufacturer, professional engineer.

H. Material Test Reports:  Signed by manufacturers certifying that the following products comply with requirements:
Edit list below to suit Project.
1. Structural steel including chemical and physical properties.

2. Bolts, nuts, and washers including mechanical properties and chemical analysis.

3. Tension-control, high-strength, bolt-nut-washer assemblies.

4. Shop primers.

5. Nonshrink grout.
Retain paragraph below if Contractor is responsible for source quality-control testing.
I. Source quality-control test reports.
Retain first paragraph below if Contractor is responsible for field quality-control testing.
J. Field quality-control test reports.

K. Product Test Reports:  Based on evaluation of comprehensive tests performed by manufacturer and witnessed by a qualified testing agency, for insulation and vapor retarders.  Include reports for thermal resistance, fire-test-response characteristics, water-vapor transmission, and water absorption.
Delete paragraph below if survey is not required or if provided by Owner.  If retaining, include "Land Surveyor Qualifications" Paragraph in "Quality Assurance" Article.
L. Surveys:  Show final elevations and locations of major members.  Indicate discrepancies between actual installation and the Contract Documents.  Have surveyor who performed surveys certify their accuracy.
Delete option in first paragraph below if door hardware is specified in Division 8 Section "Door Hardware."
M. Warranties:  Special warranties specified in this Section.

1.7 QUALITY ASSURANCE

A. Erector Qualifications:  An experienced erector who has specialized in erecting and installing work similar in material, design, and extent to that indicated for this Project and who is acceptable to manufacturer.

B. Manufacturer Qualifications:  A qualified manufacturer and member of MBMA.

1. AISC Certification for Category MB:  An AISC-Certified Manufacturer that designs and produces metal building systems and components in an AISC-Certified Facility.

2. Engineering Responsibility:  Preparation of Shop Drawings and comprehensive engineering analysis by a qualified professional engineer.

C. Land Surveyor Qualifications:  A professional land surveyor who is legally qualified to practice in jurisdiction where Project is located and who is experienced in providing surveying services of the kind indicated.
Retain paragraph below if Contractor or manufacturer selects testing agency.
D. Testing Agency Qualifications:  An independent agency qualified according to ASTM E 329 for testing indicated, as documented according to ASTM E 548.
Metal building system manufacturers often obtain secondary components and accessories from other manufacturers.
E. Source Limitations:  Obtain primary metal building system components, including structural framing and metal panel assemblies, through one source from a single manufacturer.
Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.
F. Product Options:  Drawings indicate size, profiles, and dimensional requirements of metal building system and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."
Revise subparagraph below to suit Project.
1. Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval.  If modifications are proposed, submit comprehensive explanatory data to Architect for review.
Retain "Welding certificates" Paragraph in "Submittals" Article with first paragraph below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.
G. Welding:  Qualify procedures and personnel according to AWS D1.1, "Structural Welding Code--Steel," and AWS D1.3, "Structural Welding Code--Sheet Steel."

H. Structural Steel:  Comply with AISC's "Specification for Structural Steel Buildings--Allowable Stress Design, Plastic Design," or AISC's "Load and Resistance Factor Design Specification for Structural Steel Buildings," for design requirements and allowable stresses.

I. Pre-Erection Conference:  Conduct conference at Project site to comply with requirements in Division 1 Section "Project Management and Coordination."  Review methods and procedures related to metal building systems including, but not limited to, the following:
Delete subparagraphs below if not required.  If retaining, revise to include product-specific requirements.  Identify specific participants not mentioned in Division 1 or insert additional requirements to suit Project.
1. Inspect and discuss condition of foundations and other preparatory work performed by other trades.

2. Review structural load limitations.

3. Review and finalize construction schedule and verify availability of materials, Erector's personnel, equipment, and facilities needed to make progress and avoid delays.
Coordinate first subparagraph below with Division 1 Section "Quality Requirements" and with "Source Quality Control" and "Field Quality Control" articles in this Section.  Expand requirements to suit Project.
4. Review required testing, inspecting, and certifying procedures.

5. Review weather and forecasted weather conditions and procedures for unfavorable conditions.
Insert agenda items not listed in Division 1 Section "Project Management and Coordination."
1.8 DELIVERY, STORAGE, AND HANDLING

A. Deliver components, sheets, panels, and other manufactured items so as not to be damaged or deformed.  Package metal panels for protection during transportation and handling.

B. Unload, store, and erect metal panels in a manner to prevent bending, warping, twisting, and surface damage.

1.9 PROJECT CONDITIONS

A. Weather Limitations:  Proceed with installation only when weather conditions permit metal panels to be installed according to manufacturers' written instructions and warranty requirements.

B. Field Measurements:
Delete subparagraphs below if not allowed.
1. Established Dimensions for Foundations:  Comply with established dimensions on approved anchor-bolt plans, establishing foundation dimensions and proceeding with fabricating structural framing without field measurements.  Coordinate anchor-bolt installation to ensure that actual anchorage dimensions correspond to established dimensions.

1.10 COORDINATION

A. Coordinate size and location of concrete foundations and casting of anchor-bolt inserts into foundation walls and footings.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Section "Cast-in-Place Concrete."
Insert requirements for extra materials such as metal roof and wall panels, trim, and accessories if required.  Verify with Owner because these materials can present storage difficulties.
PART 2 -  PRODUCTS

2.1 MANUFACTURERS
See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.
A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."
B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:
Because there are significant differences between manufacturers' systems, metal building system Specifications are usually developed to satisfy design requirements of a single manufacturer.  Other manufacturers' systems should be evaluated to ensure that they are suitable for Project.
C. Basis-of-Design Product:  The design for metal building systems is based on Ruffin Building Systems.  Subject to compliance with requirements, provide the named product or a comparable product by one of the following:
Manufacturers listed below are examples; each one manufactures a complete line of metal building systems.  Exceptions may apply in some areas.  Verify availability before editing.  Add local manufacturers whose systems are also acceptable.
1. Alliance Steel, Inc.

2. American Buildings Company.

3. American Steel Building Company, Inc.; Division of NCI Building Systems, LLP.

4. Behlen Mfg. Co.

5. Butler Manufacturing Company.

6. Ceco Building Systems; Division of Robertson-Ceco Corporation.

7. Crown Metal Buildings, Inc.

8. Garco Building Systems.

9. Gulf States Manufacturers, Inc.

10. Mesco Metal Buildings; Division of NCI Building Systems, LLP.

11. Metallic Metal Building Company; Division of NCI Building Systems, LLP.

12. Package Industries, Inc.

13. Southern Structures, Inc.

14. Spirco Manufacturing; Division of Metal Building Products, Inc.

15. Star Building Systems; Division of Robertson-Ceco Corporation.

16. Steelox Systems Inc.

17. United Structures of America, Inc.

18. VP Buildings, Inc.; a United Dominion Company.

2.2 STRUCTURAL-FRAMING MATERIALS
Retain and revise this Article to suit Project.
A. W-Shapes:  ASTM A 992/A 992M; ASTM A 572/A 572M, Grade 50 or 55; or ASTM A 529/A 529M, Grade 50 or 55.

B. Channels, Angles, M-Shapes, and S-Shapes:  ASTM A 36/A 36M; ASTM A 572/A 572M, Grade 50 or 55; or ASTM A 529/A 529M, Grade 50 or 55.

C. Plate and Bar:  ASTM A 36/A 36M; ASTM A 572/A 572M, Grade 50 or 55; or ASTM A 529/A 529M, Grade 50 or 55.
Usually retain first two paragraphs below only for interior columns of rigid modular or truss-frame modular framing systems.
D. Steel Pipe:  ASTM A 53/A 53M, Type E or S, Grade B.

E. Cold-Formed Hollow Structural Sections:  ASTM A 500, Grade B or C, structural tubing.

F. Structural-Steel Sheet:  Hot-rolled, ASTM A 1011/A 1011M, Structural Steel (SS), Grades 30 through 55, or High-Strength Low Alloy Steel (HSLAS), Grades 45 through 70; or cold-rolled, ASTM A 1008/A 1008M, Structural Steel (SS), Grades 25 through 80, or High-Strength Low Alloy Steel (HSLAS), Grades 45 through 70.
Retain paragraph below instead of built-up steel plates or structural-steel shapes if required for primary structural framing.  Coordinate with requirements in "Structural Framing" Article.
G. Joist Girders:  Manufactured according to "Standard Specifications for Joist Girders," in SJI's "Standard Specifications, Load Tables, and Weight Tables for Steel Joists and Joist Girders," with steel-angle, top- and bottom-chord members; with end- and top-chord arrangements as indicated and required for primary framing.
Retain first paragraph below instead of cold-formed steel sheet if required for rafters or purlins.  Coordinate with requirements in "Structural Framing" Article.
H. Steel Joists:  Manufactured according to "Standard Specifications for Open Web Steel Joists, K-Series," in SJI's "Standard Specifications, Load Tables, and Weight Tables for Steel Joists and Joist Girders," with steel-angle, top- and bottom-chord members; with end- and top-chord arrangements as indicated and required for secondary framing.

I. Non-High-Strength Bolts, Nuts, and Washers:  ASTM A 307, Grade A, carbon-steel, hex-head bolts; ASTM A 563 carbon-steel hex nuts; and ASTM F 844 plain (flat) steel washers.

1. Finish: Mechanically deposited zinc coating, ASTM B 695, Class 50.

J. High-Strength Bolts, Nuts, and Washers:  ASTM A 325, Type 1, heavy hex steel structural bolts; ASTM A 563 heavy hex carbon-steel nuts; and ASTM F 436 hardened carbon-steel washers.

1. Finish:  Mechanically deposited zinc coating, ASTM B 695, Class 50.
Retain subparagraph and associated subparagraph below if required.  Tension-control (twist-off) bolt assemblies correspond to strength of ASTM A 325 (ASTM A 325M) bolts.
2. Tension-Control, High-Strength Bolt-Nut-Washer Assemblies:  ASTM F 1852, Type 1, heavy-hex-head steel structural bolts with splined ends.

a. Finish: Mechanically deposited zinc coating, ASTM B 695, Class 50.
Retain option in paragraph below if applicable.  Indicate locations if using bolts below for some connections and ASTM A 325 (ASTM A 325M) bolts in paragraph above for others.
K. High-Strength Bolts, Nuts, and Washers:  ASTM A 490, Type 1, heavy hex steel structural bolts; ASTM A 563 heavy hex carbon-steel nuts; and ASTM F 436 hardened carbon-steel washers, plain.
Select appropriate materials from paragraph and subparagraphs below or revise if other materials are required.  AISC uses the generic term "anchor rods" to include unheaded rods and headed bolts.  Plate washers are used with oversized base-plate holes to resist nut pull-through and transfer shear from base plate to anchor rod.
L. Unheaded Anchor Rods:  ASTM F 1554, Grade 36.

1. Configuration:  Straight.

2. Nuts:  ASTM A 563heavy hex carbon steel.

3. Plate Washers:  ASTM A 36/A 36M carbon steel.

4. Washers:  ASTM F 436 hardened carbon steel.

5. Finish:Hot-dip zinc coating, ASTM A 153, Class C.
Select appropriate materials from first paragraph and subparagraphs below or revise if other materials are required.  AISC uses the generic term "anchor rods" to include unheaded rods and headed bolts.  Plate washers are used with oversized base-plate holes to resist nut pull-through and transfer shear from base plate to anchor rod.
M. Headed Anchor Rods:  ASTM F 1554, Grade 36, straight.

1. Nuts:  ASTM A 563 heavy hex carbon steel.

2. Plate Washers:  ASTM A 36/A 36M carbon steel.

3. Washers:  ASTM F 436 hardened carbon steel.

4. Finish:  Hot-dip zinc coating, ASTM A 153, Class C.

N. Threaded Rods:  ASTM A 36.

1. Nuts:  ASTM A 563 heavy hex carbon steel.

2. Washers:  ASTM A 36 carbon steel.

3. Finish:  Hot-dip zinc coating, ASTM A 153.
Verify that primer in paragraph below is compatible with fireproofing if required.  See Evaluations.
O. Primer:  SSPC-Paint 15, Type I, red oxide.

2.3 MISCELLANEOUS MATERIALS

A. Fasteners:  Self-tapping screws, bolts, nuts, self-locking rivets and bolts, end-welded studs, and other suitable fasteners designed to withstand design loads.  Provide fasteners with heads matching color of materials being fastened by means of plastic caps or factory-applied coating.

1. Fasteners for Metal Roof Panels:  Self-drilling or self-tapping, zinc-plated, hex-head carbon-steel screws, with a stainless-steel cap or zinc-aluminum-alloy head and EPDM or neoprene sealing washer.

2. Fasteners for Metal Wall Panels:  Self-drilling or self-tapping, zinc-plated, hex-head carbon-steel screws, with nylon or polypropylene washer.
Retain one or both subparagraphs above, or delete both and retain first subparagraph below if corrosion resistance is required.
3. Fasteners for Metal Roof and Wall Panels:  Self-drilling Type 410 stainless-steel or self-tapping Type 304 stainless-steel or zinc-alloy-steel hex washer head, with EPDM or PVC washer under heads of fasteners bearing on weather side of metal panels.

4. Fasteners for Flashing and Trim:  Blind fasteners or self-drilling screws with hex washer head.

5. Blind Fasteners:  High-strength aluminum or stainless-steel rivets.

2.4 FABRICATION, GENERAL

A. General:  Design components and field connections required for erection to permit easy assembly.

1. Mark each piece and part of the assembly to correspond with previously prepared erection drawings, diagrams, and instruction manuals.

2. Fabricate structural framing to produce clean, smooth cuts and bends.  Punch holes of proper size, shape, and location.  Members shall be free of cracks, tears, and ruptures.

B. Tolerances:  Comply with MBMA's "Metal Building Systems Manual":  Chapter IV, Section 9, "Fabrication and Erection Tolerances."

2.5 STRUCTURAL FRAMING
Refer to the tables for metal building structural systems at the end of the Evaluations for a list of manufacturers' products.  Use these tables in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.
A. General:

1. Primary Framing:  Shop fabricate framing components to indicated size and section with baseplates, bearing plates, stiffeners, and other items required for erection welded into place.  Cut, form, punch, drill, and weld framing for bolted field assembly.

a. Make shop connections by welding or by using high-strength bolts.

b. Join flanges to webs of built-up members by a continuous submerged arc-welding process.

c. Brace compression flange of primary framing with steel angles or cold-formed structural tubing between frame web and purlin or girt web, so flange compressive strength is within allowable limits for any combination of loadings.
Revise first subparagraph below if other types of attachment are permitted.  Welded clips on roof rafters may not be allowed by authorities having jurisdiction.
d. Weld clips to frames for attaching secondary framing members.

e. Shop Priming:  Prepare surfaces for shop priming according to SSPC-SP 2.  Shop prime primary structural members with specified primer after fabrication.

2. Secondary Framing:  Shop fabricate framing components to indicated size and section by roll-forming or break-forming, with baseplates, bearing plates, stiffeners, and other plates required for erection welded into place.  Cut, form, punch, drill, and weld secondary framing for bolted field connections to primary framing.

a. Make shop connections by welding or by using non-high-strength bolts.

b. Shop Priming:  Prepare uncoated surfaces for shop priming according to SSPC-SP 2.  Shop prime uncoated secondary structural members with specified primer after fabrication.
Review the remainder of this Article for compliance with design concept and revise to suit Project.  Consult manufacturers for standard framing details.
B. Primary Framing:  Manufacturer's standard structural primary framing system, designed to withstand required loads and specified requirements.  Primary framing includes transverse and lean-to frames; rafter, rake, and canopy beams; sidewall, intermediate, end-wall, and corner columns; and wind bracing.

1. General:  Provide frames with attachment plates, bearing plates, and splice members.  Factory drill for field-bolted assembly.  Provide frame span and spacing indicated.
Delete subparagraph below if not allowed.
a. Slight variations in span and spacing may be acceptable if necessary to meet manufacturer's standard, as approved by Architect.
Retain one of five subparagraphs below.
2. Rigid Clear-Span Frames:  I-shaped frame sections fabricated from shop-welded, built-up steel plates or structural-steel shapes.  Interior columns are not permitted.
Delete first subparagraph below if Drawings adequately indicate requirements.
3. Frame Configuration:  Two-directional sloped.

4. Exterior Column Type: Tapered.

5. Rafter Type: Tapered.
Retain first paragraph and subparagraphs below if required or delete if half-load primary frames are used.  Retain columns only and delete rafters if full-load frames are used.
C. End-Wall Framing:  Manufacturer's standard primary end-wall framing fabricated for field-bolted assembly to comply with the following:

1. End-Wall and Corner Columns:  I-shaped sections fabricated from structural-steel shapes; shop-welded, built-up steel plates; or C-shaped, cold-formed, structural-steel sheet; with minimum thickness of 0.0598 inch.

2. End-Wall Rafters:  C-shaped, cold-formed, structural-steel sheet; with minimum thickness of 0.0598 inch; or I-shaped sections fabricated from shop-welded, built-up steel plates or structural-steel shapes.

D. Secondary Framing:  Manufacturer's standard secondary framing members, including purlins, girts, eave struts, flange bracing, base members, gable angles, clips, headers, jambs, and other miscellaneous structural members.  Fabricate framing from cold-formed, structural-steel sheet or roll-formed, metallic-coated steel sheet prepainted with coil coating, unless otherwise indicated, to comply with the following:
Retain one of two purlins below or retain both if required.
1. Purlins:  C- or Z-shaped sections; fabricated from minimum 0.0598-inch thick steel sheet, built-up steel plates, or structural-steel shapes; minimum 2-1/2-inch wide flanges.
Delete depths in subparagraph below if retaining Part 1 "System Description" Article and depths are determined by manufacturer.  Verify availability with manufacturers selected.  Insert manufacturer's proprietary size if required.
a. Depth: As required to comply with system performance requirements.

2. Purlins:  Steel joists of depths indicated.

3. Girts:  C- or Z-shaped sections; fabricated from minimum 0.0598-inch thick steel sheet, built-up steel plates, or structural-steel shapes.  Form ends of Z-sections with stiffening lips angled 40 to 50 degrees to flange and with minimum 2-1/2-inch wide flanges.
Delete depths in subparagraph below if retaining Part 1 "System Description" Article and depths are determined by manufacturer.  Verify availability with manufacturers selected.  Insert manufacturer's proprietary size if required.
a. Depth: As required to comply with system performance requirements] <Insert dimension.

4. Eave Struts:  Unequal-flange, C-shaped sections; fabricated from 0.0598-inch thick steel sheet, built-up steel plates, or structural-steel shapes; to provide adequate backup for metal panels.

5. Flange Bracing:  Minimum 2-by-2-by-1/8-inch structural-steel angles or 1-inch diameter, cold-formed structural tubing to stiffen primary frame flanges.

6. Sag Bracing:  Minimum 1-by-1-by-1/8-inch structural-steel angles.
Revise first subparagraph below if channel shape is required instead of base angles.
7. Base or Sill Angles:  Minimum 3-by-2-by-0.0598-inch zinc-coated (galvanized) steel sheet.

8. Purlin and Girt Clips:  Minimum 0.0598-inch thick, steel sheet.  Provide galvanized clips where clips are connected to galvanized framing members.

9. Secondary End-Wall Framing:  Manufacturer's standard sections fabricated from minimum 0.0598-inch thick, structural-steel sheet.

10. Framing for Openings:  Channel shapes; fabricated from minimum 0.0598-inch thick, cold-formed, structural-steel sheet or structural-steel shapes.  Frame head and jamb of door openings, and head, jamb, and sill of other openings.

11. Miscellaneous Structural Members:  Manufacturer's standard sections fabricated from cold-formed, structural-steel sheet; built-up steel plates; or zinc-coated (galvanized) steel sheet; designed to withstand required loads.
If required, insert requirements for crane runway beams, supports, and bracing; mezzanine framing and decking; and floor framing for multistory applications.

Profile requirements in metal panel articles below are often better described graphically than verbally.  If profiles are indicated on Drawings, delete profile descriptions and retain types of metals and metal thicknesses.

Copy paragraphs and subparagraphs in each Article below and re-edit them to suit Project.

Insert drawing designation for each metal panel product retained below.  Use these designations on Drawings to show where each product is required.

Unless colors are preselected and specified or scheduled, retain one of two options in each "Color" Subparagraph with finish selected for each type of metal panel.  Most manufacturers offer a variety of colors.
2.6 ACCESSORIES
This Article includes metal building system manufacturers' standard accessories.  If more stringent requirements are needed, delete Article and insert reference to specific Division 7 Sections in "Related Sections" Paragraph in Part 1 "Summary" Article,.

Retain accessories below required to suit Project.
A. General:  Provide accessories as standard with metal building system manufacturer and as specified.  Fabricate and finish accessories at the factory to greatest extent possible, by manufacturer's standard procedures and processes.  Comply with indicated profiles and with dimensional and structural requirements.
Pipe flashing below is not designed for high-temperature applications.
2.7 FINISHES, GENERAL

A. Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

2.8 SOURCE QUALITY CONTROL
Retain one of first two paragraphs and associated subparagraphs below.  Retain first paragraph if authorities having jurisdiction do not require that Owner engage a special inspector.  See "Testing and Inspecting Considerations" Article in the Evaluations.
A. Testing Agency: Engage a qualified testing and inspecting agency to perform the following tests and inspections and to submit reports.
Retain subparagraph and associated subparagraph below and delete "Tests and Inspections" Paragraph if requiring AISC-certified manufacturers and if authorities having jurisdiction approve fabrication work without special inspections.  If retaining, also retain "Manufacturer Qualifications" Paragraph in Part 1 "Quality Assurance" Article.
1. Special inspections will not be required if fabrication is performed by a manufacturer registered and approved by authorities having jurisdiction to perform such Work without special inspection.

a. After fabrication, submit certificate of compliance with copy to authorities having jurisdiction certifying that Work was performed according to Contract requirements.

B. Tests and Inspections:
RCSC prescribes inspection for snug-tightened joints and testing and inspection for each method of pretensioning joints.
1. Bolted Connections:  Shop-bolted connections shall be tested and inspected according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts."

2. Welded Connections:  In addition to visual inspection, shop-welded connections shall be tested and inspected according to AWS D1.1 and the following inspection procedures, at inspector's option:
Select applicable nondestructive testing methods from four subparagraphs below.  Revise to indicate extent of weld inspections if applicable and to add alternative acceptance criteria to AWS D1.1 if required.
a. Liquid Penetrant Inspection:  ASTM E 165.

b. Magnetic Particle Inspection:  ASTM E 709; performed on root pass and on finished weld.  Cracks or zones of incomplete fusion or penetration will not be accepted.

c. Ultrasonic Inspection:  ASTM E 164.

d. Radiographic Inspection:  ASTM E 94.

C. Correct deficiencies in Work that test reports and inspections indicate do not comply with the Contract Documents.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Erector present, for compliance with requirements for installation tolerances and other conditions affecting performance of work.
Delete subparagraph below if not required.
1. For the record, prepare written report, endorsed by Erector, listing conditions detrimental to performance of work.

B. Before erection proceeds, survey elevations and locations of concrete- and masonry-bearing surfaces and locations of anchor rods, bearing plates, and other embedments to receive structural framing, with Erector present, for compliance with requirements and metal building system manufacturer's tolerances.

1. Engage land surveyor to perform surveying.

C. Proceed with erection only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Clean and prepare surfaces to be painted according to manufacturer's written instructions for each particular substrate condition.

B. Provide temporary shores, guys, braces, and other supports during erection to keep structural framing secure, plumb, and in alignment against temporary construction loads and loads equal in intensity to design loads.  Remove temporary supports when permanent structural framing, connections, and bracing are in place, unless otherwise indicated.

3.3 ERECTION OF STRUCTURAL FRAMING

A. Erect metal building system according to manufacturer's written erection instructions and erection drawings.

B. Do not field cut, drill, or alter structural members without written approval from metal building system manufacturer's professional engineer.

C. Set structural framing accurately in locations and to elevations indicated and according to AISC specifications referenced in this Section.  Maintain structural stability of frame during erection.
Add leveling plates to first paragraph below if required.
D. Base and Bearing Plates:  Clean concrete- and masonry-bearing surfaces of bond-reducing materials, and roughen surfaces prior to setting plates.  Clean bottom surface of plates.

1. Set plates for structural members on wedges, shims, or setting nuts as required.

2. Tighten anchor rods after supported members have been positioned and plumbed.  Do not remove wedges or shims but, if protruding, cut off flush with edge of plate before packing with grout.

3. Promptly pack grout solidly between bearing surfaces and plates so no voids remain.  Neatly finish exposed surfaces; protect grout and allow to cure.  Comply with manufacturer's written installation instructions for shrinkage-resistant grouts.

E. Align and adjust structural framing before permanently fastening.  Before assembly, clean bearing surfaces and other surfaces that will be in permanent contact with framing.  Perform necessary adjustments to compensate for discrepancies in elevations and alignment.

1. Level and plumb individual members of structure.
Review subparagraph below with structural engineer and revise to suit Project.  Delete if not required.
2. Make allowances for difference between temperature at time of erection and mean temperature when structure will be completed and in service.

F. Primary Framing and End Walls:  Erect framing true to line, level, plumb, rigid, and secure.  Level baseplates to a true even plane with full bearing to supporting structures, set with double-nutted anchor bolts.  Use grout to obtain uniform bearing and to maintain a level base-line elevation.  Moist cure grout for not less than seven days after placement.
In turn-of-the-nut method in publication referenced in subparagraph below, bolts must first be snug tight, which is defined as the full effect of a man using an ordinary spud wrench.  Nuts are then turned an additional one-third of a turn to produce minimum allowed tension.  Refer to RCSC for specific requirements.
1. Make field connections using high-strength bolts installed according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts" for type of bolt and type of joint specified.

a. Joint Type:  Snug tightened or pretensioned.

G. Secondary Framing:  Erect framing true to line, level, plumb, rigid, and secure.  Fasten secondary framing to primary framing using clips with field connections using non-high-strength bolts.

1. Provide rake or gable purlins with tight-fitting closure channels and fasciae.

2. Locate and space wall girts to suit openings such as doors and windows.
Delete first subparagraph below if no canopy.
3. Locate canopy framing as indicated.

4. Provide supplemental framing at entire perimeter of openings, including doors, windows, louvers, ventilators, and other penetrations of roof and walls.
Retain first paragraph and subparagraphs below if steel joist purlins are required; otherwise, delete.
H. Steel Joists and Joist Girders:  Install joists, girders, and accessories plumb, square, and true to line; securely fasten to supporting construction according to SJI's "Standard Specifications, Load Tables, and Weight Tables for Steel Joists and Joist Girders," joist manufacturer's written recommendations, and requirements in this Section.

1. Before installation, splice joists delivered to Project site in more than one piece.

2. Space, adjust, and align joists accurately in location before permanently fastening.

3. Install temporary bracing and erection bridging, connections, and anchors to ensure that joists are stabilized during construction.

4. Bolt joists to supporting steel framework using carbon-steel bolts, unless otherwise indicated.
Retain subparagraph above or first subparagraph below.
5. Bolt joists to supporting steel framework using high-strength structural bolts, unless otherwise indicated.  Comply with RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts" for high-strength structural bolt installation and tightening requirements.

6. Install and connect bridging concurrently with joist erection, before construction loads are applied.  Anchor ends of bridging lines at top and bottom chords if terminating at walls or beams.

I. Bracing:  Install bracing in roof and sidewalls where indicated on erection drawings.

1. Tighten rod and cable bracing to avoid sag.

2. Locate interior end-bay bracing only where indicated.

J. Framing for Openings:  Provide shapes of proper design and size to reinforce openings and to carry loads and vibrations imposed, including equipment furnished under mechanical and electrical work.  Securely attach to structural framing.

K. Erection Tolerances:  Maintain erection tolerances of structural framing within AISC's "Code of Standard Practice for Steel Buildings and Bridges."

3.4 FIELD QUALITY CONTROL
Retain one of first two paragraphs below.  Retain first paragraph if authorities having jurisdiction do not require that the Owner engage a special inspector.  See "Testing and Inspecting Considerations" Article in the Evaluations.
A. Testing Agency:  Engage a qualified testing and inspecting agency to perform the following tests and inspections and to submit reports.

B. Tests and Inspections:
RCSC prescribes inspection for snug-tightened joints and testing and inspection for each method of pretensioning joints.
1. High-Strength, Field-Bolted Connections:  Connections shall be tested and inspected during installation according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts."

2. Welded Connections:  In addition to visual inspection, field-welded connections shall be tested and inspected according to AWS D1.1 and the following inspection procedures, at inspector's option:
Select applicable nondestructive testing methods from four subparagraphs below.  Revise to indicate extent of weld inspections if applicable and to add alternative acceptance criteria to AWS D1.1 if required.
a. Liquid Penetrant Inspection:  ASTM E 165.

b. Magnetic Particle Inspection:  ASTM E 709; performed on root pass and on finished weld.  Cracks or zones of incomplete fusion or penetration will not be accepted.

c. Ultrasonic Inspection:  ASTM E 164.

d. Radiographic Inspection:  ASTM E 94.

C. Correct deficiencies in Work that test reports and inspections indicate do not comply with the Contract Documents.

3.5 CLEANING AND PROTECTION
Retain first paragraph below if galvanized items are required.
A. Repair damaged galvanized coatings on galvanized items with galvanized repair paint according to ASTM A 780 and manufacturer's written instructions.

B. Touchup Painting:  After erection, promptly clean, prepare, and prime or reprime field connections, rust spots, and abraded surfaces of prime-painted structural framing, bearing plates, and accessories.

1. Clean and prepare surfaces by SSPC-SP 2, "Hand Tool Cleaning," or SSPC-SP 3, "Power Tool Cleaning."

2. Apply a compatible primer of same type as shop primer used on adjacent surfaces.
Delete paragraph and subparagraphs above and retain first paragraph below if touchup painting is required for Project but is not part of the Work of this Section.
C. Touchup Painting:  Cleaning and touchup painting are specified in Division 9 painting Sections.

END OF SECTION 133419
METAL BUILDING SYSTEMS
133419 - 17

