ST. TAMMANY FIRE PROTECTION DISTRICT NO. 1

FIRE STATION #10

2745 LAKESHORE VISTA BLVD

SLIDELL, LA 70461


SECTION 221400

STORM DRAINAGE
Copyright 2001 (R 12/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes gravity-flow, nonpressure storm drainage outside the building, with the following components:

1. Cleanouts.

2. Drains.

3. Precast concrete or Cast-in-place concrete or Fiberglass manholes.

1.3 DEFINITIONS

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. EPDM:  Ethylene-propylene-diene-monomer rubber.

C. FRP:  Fiberglass-reinforced plastic.

D. LLDPE:  Linear low-density, polyethylene plastic.

E. PE:  Polyethylene plastic.

F. PP:  Polypropylene plastic.

G. PVC:  Polyvinyl chloride plastic.

H. RTRF:  Glass-fiber-reinforced, thermosetting-resin fitting.

I. RTRP:  Glass-fiber-reinforced, thermosetting-resin pipe.

J. TPE:  Thermoplastic elastomer.

1.4 PERFORMANCE REQUIREMENTS

A. Gravity-Flow, Nonpressure, Drainage-Piping Pressure Rating:  10-foot head of water.  Pipe joints shall be at least silttight, unless otherwise indicated.

1.5 SUBMITTALS

A. Product Data:  For the following:

1. Pipe fittings.

2. Drains.

B. Shop Drawings:  For the following:

1. Catch Basins and Stormwater Inlets.  Include plans, elevations, sections, details, and frames, covers, and grates.

2. Stormwater Detention Structures:  Include plans, elevations, sections and details.

Retain paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Show pipe sizes, locations, and elevations.  Show other piping in same trench and clearances from storm drainage system piping.  Indicate interface and spatial relationship between manholes, piping, and proximate structures.

Retain paragraph below if profiles are not shown on Drawings.

D. Profile Drawings:  Show system piping in elevation.  Draw profiles at horizontal scale of not less than 1 inch equals 50 feet and vertical scale of not less than 1 inch equals 5 feet.  Indicate manholes, catch basins, stormwater inlets and piping.  Show types, sizes, materials, and elevations of other utilities crossing system piping.

Retain paragraph below if Contractor is responsible for field quality-control testing.

E. Field quality-control test reports.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Do not store plastic manholes, pipe, and fittings in direct sunlight.

B. Protect pipe, pipe fittings, and seals from dirt and damage.

Delete first paragraph below if only cast-in-place manholes are specified.

C. Handle manholes according to manufacturer's written rigging instructions.

D. Handle catch basins and stormwater inlets according to manufacturer's written rigging instructions.

1.7 PROJECT CONDITIONS

Delete this Article if no interruption of existing storm drainage service is required.

A. Interruption of Existing Storm Drainage Service:  Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

1. Notify Architect and Owner no fewer than two days in advance of proposed interruption of service.

2. Do not proceed with interruption of service without Owner and Architect's written permission.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 PIPING MATERIALS

See "Writing Guide" Article in Evaluations for a discussion of this Section's organization and the most efficient way to edit this Section.

A. Refer to Part 3 "Piping Applications" Article for applications of pipe, fitting, and joining materials.

2.3 HUB-AND-SPIGOT, CAST-IRON SOIL PIPE AND FITTINGS

Pipe and fittings in this Article are available in NPS 2 to NPS 15 (DN 50 to DN 375).

A. Pipe and Fittings:  ASTM A 74, Service class.

B. Gaskets:  ASTM C 564, rubber.

C. Calking Materials:  ASTM B 29, pure lead and oakum or hemp fiber.

2.4 HUBLESS CAST-IRON SOIL PIPE AND FITTINGS

Pipe, fittings, and couplings in this Article are available in NPS 1-1/2 to NPS 15 (DN 40 to DN 375).

A. Pipe and Fittings:  ASTM A 888 or CISPI 301.

B. Shielded Couplings:  ASTM C 1277 assembly of metal shield or housing, corrosion-resistant fasteners, and rubber sleeve with integral, center pipe stop.

Couplings in paragraph and subparagraphs below are economical.  They may not be suitable for installation in corrosive soil.

C. Shielded, Stainless-Steel Couplings:  CISPI 310, with ASTM A 666, Type 301, stainless-steel corrugated shield; stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. ANACO.

b. Dallas Specialty & Mfg. Co.

c. Fernco Inc.

d. Ideal Div.; Stant Corp.

e. Mission Rubber Company; a division of MCP Industries, Inc.

f. Tyler Pipe; Soil Pipe Div.

2. Couplings for NPS 1-1/2 to NPS 4:  2-1/8-inch- wide shield with 2 bands.

3. Couplings for NPS 5 and NPS 6:  3-inch- wide shield with 4 bands.

4. Couplings for NPS 8 and NPS 10:  4-inch- wide shield with 4 bands.

Couplings in first two paragraphs and associated subparagraphs below cover various configurations of manufacturers' nonstandard, "heavy-duty" shielded, stainless-steel couplings.  There is a new standard being developed for these couplings and this description (including dimensions) will comply.

D. Heavy-Duty, Shielded, Stainless-Steel Couplings, NPS 10 and Smaller:  With ASTM A 666, Type 301 or Type 304, stainless-steel shield; 2 or more stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. ANACO.

b. Clamp-All Corp.

c. Dallas Specialty & Mfg. Co.

d. Ideal Div.; Stant Corp.

e. Mission Rubber Company; a division of MCP Industries, Inc.

f. Tyler Pipe; Soil Pipe Div.

2. Couplings for NPS 1-1/2 to NPS 4:  3 inches.

3. Couplings for NPS 5 to NPS 10:  4 inches.

E. Heavy-Duty, Shielded, Stainless-Steel Couplings, NPS 12 and NPS 15:  With ASTM A 666, Type 301 or Type 304, stainless-steel shield; stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. ANACO.

b. Ideal Div.; Stant Corp.

c. Mission Rubber Company; a division of MCP Industries, Inc.

d. Tyler Pipe; Soil Pipe Div.

2. Couplings:  5-1/2-inch- wide shield with 6 bands.

F. Heavy-Duty, Cast-Iron Couplings:  ASTM A 48, two-piece, cast-iron housing; stainless-steel bolts and nuts; and ASTM C 564, rubber sleeve.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. MG Piping Products Co.

2. Couplings for NPS 1-1/2 to NPS 4:  2-1/8-inch- wide housing with 2 bolts.

3. Couplings for NPS 5 and NPS 6:  3-1/8-inch- wide housing with 4 bolts.

4. Couplings for NPS 8 and NPS 10:  4-inch- wide housing with 4 bolts.

Coupling in paragraph below should not be used for liquids at temperatures below 0 deg F (minus 18 deg C) or above 130 deg F (54 deg C).

G. Unshielded Couplings:  ASTM C 1461, rigid, sleeve-type, reducing- or transition-type mechanical coupling molded from ASTM C 1440, TPE material with corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. ANACO.

2. Couplings for NPS 1-1/2 to NPS 4:  Sleeve with two bands.

2.5 DUCTILE-IRON CULVERT PIPE AND FITTINGS

Pipe in paragraph below should be available in NPS 14 to NPS 64 (DN 350 to DN 1600).  Joints are gasket type.

A. Pipe:  ASTM A 716, for push-on joints.

Fittings in paragraph below should be available in NPS 3 to NPS 48 (DN 80 to DN 1200).

B. Standard Fittings:  AWWA C110, ductile or gray iron, for push-on joints.

Fittings in first paragraph below are available in NPS 3 to NPS 24 (DN 80 to DN 600) and NPS 54 to NPS 64 (DN 1350 to DN 1600).

C. Compact Fittings:  AWWA C153, for push-on joints.

D. Gaskets:  AWWA C111, rubber.

2.6 STEEL PIPE AND FITTINGS

Piping material in this Article is available in NPS 4 to NPS 144 (DN 100 to DN 3600).  Standard joints with bands are soiltight.  Special joints with bands and O-rings are silttight.

A. Corrugated-Steel Pipe and Fittings:  ASTM A 760/A 760M, Type I with fittings of similar form and construction as pipe.

1. Special-Joint Bands:  Corrugated steel with O-ring seals.

2. Standard-Joint Bands:  Corrugated steel.

3. Coating:  Aluminum.

2.7 PVC PIPE AND FITTINGS

Pipe in paragraph below is available in NPS 4 to NPS 12 (DN 100 to DN 300).  Joints are gasket type.

A. PVC Pressure Pipe:  AWWA C900, Class 150, for gasketed joints and using ASTM F 477, elastomeric seals.

1. Fittings NPS 4 to NPS 8:  PVC pressure fittings complying with AWWA C907, for gasketed joints and using ASTM F 477, elastomeric seals.

Ductile-iron fittings in subparagraph below mate with PVC pressure pipe and are available in NPS 3 to NPS 24 (DN 80 to DN 600).  Joints are gasket type.

2. Fittings NPS 10 and Larger:  Ductile-iron, compact fittings complying with AWWA C153, for push-on joints and using AWWA C111, rubber gaskets.

Piping in paragraph below is available in NPS 1/8 to NPS 24 (DN 6 to DN 600).  Joints are solvent-cemented type.

B. PVC Water-Service Pipe and Fittings:  ASTM D 1785, Schedule 40 pipe, with plain ends for solvent-cemented joints with ASTM D 2466, Schedule 40, socket-type fittings.

Piping in paragraph below is available in 4 SDRs and in NPS 4 to NPS 15 (DN 100 to DN 375).  Joints are solvent-cemented and gasket types.

C. PVC Sewer Pipe and Fittings, NPS 15 and Smaller:  ASTM D 3034, SDR 35, with bell-and-spigot ends for gasketed joints with ASTM F 477, elastomeric seals.

Piping in paragraph below is available in 2 thicknesses and in NPS 18 to NPS 36 (DN 450 to DN 900).  Joints are gasket type.

D. PVC Sewer Pipe and Fittings, NPS 18 and Larger:  ASTM F 679, T-1 wall thickness, with bell-and-spigot ends for gasketed joints with ASTM F 477, elastomeric seals.

Piping in paragraph below is available in at least NPS 8 to NPS 30 (DN 200 to DN 750).  Standard includes NPS 4 to NPS 48 (DN 100 to DN 1200), but availability in all sizes is uncertain.  Joints are gasket type and are watertight.

2.8 NONPRESSURE-TYPE PIPE COUPLINGS

A. Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition coupling, for joining underground nonpressure piping.  Include ends of same sizes as piping to be joined, and corrosion-resistant-metal tension band and tightening mechanism on each end.

B. Sleeve Materials:

1. For Plastic Pipes:  ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

2. For Dissimilar Pipes:  ASTM D 5926, PVC or other material compatible with pipe materials being joined.

C. Shielded Flexible Couplings:  ASTM C 1460, elastomeric or rubber sleeve with full-length, corrosion-resistant outer shield and corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. Cascade Waterworks Mfg.

b. Dallas Specialty & Mfg. Co.

c. Mission Rubber Company; a division of MCP Industries, Inc.

D. Ring-Type Flexible Couplings:  Elastomeric compression seal with dimensions to fit inside bell of larger pipe and for spigot of smaller pipe to fit inside ring.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. Fernco Inc.

b. Logan Clay Products Company (The).

c. Mission Rubber Company; a division of MCP Industries, Inc.

Coupling in paragraph below should not be used for liquids at temperatures below 0 deg F (minus 18 deg C) or above 130 deg F (54 deg C).

E. Nonpressure-Type Rigid Couplings:  ASTM C 1461, sleeve-type reducing- or transition-type mechanical coupling molded from ASTM C 1440, TPE material with corrosion-resistant-metal tension band and tightening mechanism on each end.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. ANACO.

2.9 PRESSURE-TYPE PIPE COUPLINGS

A. Reducing or transition, metal, bolted, sleeve-type, reducing or transition coupling, for joining underground pressure piping.  Include 200-psig minimum pressure rating and ends of same sizes as piping to be joined.

B. Tubular-Sleeve Couplings:  AWWA C219, with center sleeve, gaskets, end rings, and bolt fasteners.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. Cascade Waterworks Mfg.

b. Dresser, Inc.; DMD Div.

c. Ford Meter Box Company, Inc. (The); Pipe Products Div.

d. JCM Industries.

e. Romac Industries, Inc.

f. Smith-Blair, Inc.

g. Viking Johnson.

2. Center-Sleeve Material:  Manufacturer's standard.

3. Gasket Material:  Natural or synthetic rubber.

4. Metal Component Finish:  Corrosion-resistant coating or material.

2.10 BACKWATER VALVES

A. Gray-Iron Backwater Valves:  ASME A112.14.1, gray-iron body and bolted cover, with bronze seat.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. Josam Company.

b. Smith, Jay R. Mfg. Co.

c. Wade Div.; Tyler Pipe.

d. Watts Industries, Inc.

e. Watts Industries, Inc.; Enpoco, Inc. Div.

f. Zurn Industries, Inc.; Zurn Specification Drainage Operation.

g. <Insert manufacturer's name.>

2. Horizontal Type:  With swing check valve and hub-and-spigot ends.

3. Combination Horizontal and Manual Gate-Valve Type:  With swing check valve, integral gate valve, and hub-and-spigot ends.

4. Terminal Type:  With bronze seat, swing check valve, and hub inlet.

2.11 CLEANOUTS

A. Gray-Iron Cleanouts:  ASME A112.36.2M, round, gray-iron housing with clamping device and round, secured, scoriated, gray-iron cover.  Include gray-iron ferrule with inside calk or spigot connection and countersunk, tapered-thread, brass closure plug.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. Josam Company.

b. MIFAB Manufacturing, Inc.

c. Smith, Jay R. Mfg. Co.

d. Wade Div.; Tyler Pipe.

e. Watts Industries, Inc.

f. Watts Industries, Inc.; Enpoco, Inc. Div.

g. Zurn Industries, Inc.; Zurn Specification Drainage Operation.

2. Top-Loading Classification(s):  Heavy duty.

3. Sewer Pipe Fitting and Riser to Cleanout:  ASTM A 74, Service class, cast-iron soil pipe and fittings.

B. PVC Cleanouts:  PVC body with PVC threaded plug.  Include PVC sewer pipe fitting and riser to cleanout of same material as sewer piping.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. Canplas Inc.

b. IPS Corporation.

c. NDS Inc.

d. Plastic Oddities, Inc.

e. Sioux Chief Manufacturing Company, Inc.

f. Zurn Industries, Inc.; Zurn Light Commercial Specialty Plumbing Products.

2.12 DRAINS

A. Gray-Iron Area Drains:  ASME A112.21.1M, round body with anchor flange and round secured grate.  Include bottom outlet with inside calk or spigot connection, of sizes indicated.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. Available Manufacturers:

a. Josam Company.

b. MIFAB Manufacturing, Inc.

c. Smith, Jay R. Mfg. Co.

d. Wade Div.; Tyler Pipe.

e. Watts Industries, Inc.

f. Watts Industries, Inc.; Enpoco, Inc. Div.

g. Zurn Industries, Inc.; Zurn Specification Drainage Operation.

2. Top-Loading Classification(s):  Heavy duty.

2.13 CORROSION-PROTECTION PIPING ENCASEMENT

A. Encasement for Underground Metal Piping:  ASTM A 674 or AWWA C105.

1. Form:  Sheet.

Retain one of first three subparagraphs below.

2. Material:  LLDPE film of 0.008-inch minimum thickness.

3. Material:  High-density, crosslaminated PE film of 0.004-inch minimum thickness.

2.14 CONCRETE

A. General:  Cast-in-place concrete according to ACI 318/318R, ACI 350R, and the following:

1. Cement:  ASTM C 150, Type II.

2. Fine Aggregate:  ASTM C 33, sand.

3. Coarse Aggregate:  ASTM C 33, crushed gravel.

4. Water:  Potable.

B. Portland Cement Design Mix:  4000 psi minimum, with 0.45 maximum water-cementitious materials ratio.

1. Reinforcement Fabric:  ASTM A 185, steel, welded wire fabric, plain.

2. Reinforcement Bars:  ASTM A 615/A 615M, Grade 60, deformed steel.

C. Ballast and Pipe Supports:  Portland cement design mix, 3000 psi minimum, with 0.58 maximum water-cementitious materials ratio.

1. Reinforcement Fabric:  ASTM A 185, steel, welded wire fabric, plain.

2. Reinforcement Bars:  ASTM A 615/A 615M, Grade 60, deformed steel.

2.15 CATCH BASINS

A. Standard Precast Concrete Catch Basins:  ASTM C 478, precast, reinforced concrete, of depth indicated, with provision for sealant joints.

1. Base Section:  6-inch minimum thickness for floor slab and 4-inch minimum thickness for walls and base riser section, and having separate base slab or base section with integral floor.

2. Riser Sections:  4-inch minimum thickness, 48-inch diameter, and lengths to provide depth indicated.

3. Top Section:  Eccentric-cone type unless concentric-cone or flat-slab-top type is indicated.  Top of cone of size that matches grade rings.

4. Joint Sealant:  ASTM C 990, bitumen or butyl rubber.

Retain one of first two subparagraphs below if required.

5. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and shape matching catch basin frame and grate.  Include sealant recommended by ring manufacturer.

6. Grade Rings:  Include 2 or 3 reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch- diameter frame and grate.

7. Pipe Connectors:  ASTM C 923, resilient, of size required, for each pipe connecting to base section.

B. Designed Precast Concrete Catch Basins:  ASTM C 913, precast, reinforced concrete; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for sealant joints.

1. Joint Sealants:  ASTM C 990, bitumen or butyl rubber.

Retain one of first two subparagraphs below if required.

2. Adjusting Rings:  Interlocking rings with level or sloped edge in thickness and shape matching catch basin frame and grate.  Include sealant recommended by ring manufacturer.

3. Grade Rings:  Include 2 or 3 reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch- diameter frame and grate.

4. Pipe Connectors:  ASTM C 923, resilient, of size required, for each pipe connecting to base section.

C. Cast-in-Place Concrete, Catch Basins:  Construct of reinforced concrete; designed according to ASTM C 890 for structural loading; of depth, shape, dimensions, and appurtenances indicated.

1. Bottom, Walls, and Top:  Reinforced concrete.

2. Channels and Benches:  Concrete.

Retain paragraph and subparagraphs below for rectangular structures.

D. Frames and Grates:  ASTM A 536, Grade 60-40-18, ductile iron designed for A-16, structural loading.  Include flat grate with small square or short-slotted drainage openings.

1. Size:  24 by 24 inches minimum, unless otherwise indicated.

2. Grate Free Area:  Approximately 50 percent, unless otherwise indicated.

Retain paragraph and subparagraphs above or paragraph and subparagraph below.

Retain paragraph below for round, manhole-type structures.

E. Frames and Grates:  ASTM A 536, Grade 60-40-18, ductile iron designed for A-16, structural loading.  Include 24-inch ID by 7- to 9-inch riser with 4-inch minimum width flange, and 26-inch- diameter flat grate with small square or short-slotted drainage openings.

1. Grate Free Area:  Approximately 50 percent, unless otherwise indicated.

2.16 STORMWATER INLETS

Stormwater inlets are made of precast concrete, cast-in-place concrete, and brick.  Select from six inlet paragraphs in this Article.

Revise three paragraphs below to suit utility requirements.

A. Curb Inlets:  Made with vertical curb opening, of materials and dimensions according to utility standards.

B. Gutter Inlets:  Made with horizontal gutter opening, of materials and dimensions according to utility standards.  Include heavy-duty frames and grates.

C. Combination Inlets:  Made with vertical curb and horizontal gutter openings, of materials and dimensions according to utility standards.  Include heavy-duty frames and grates.

Retain paragraph below with either of last two paragraphs above.

D. Frames and Grates:  Heavy-duty frames and grates according to utility standards.

Retain, edit, or delete four paragraphs above or below.

Revise three paragraphs below to suit Project, and detail on Drawings.

E. Curb Inlets:  Vertical curb opening, of materials and dimensions indicated.

F. Gutter Inlets:  Horizontal gutter opening, of materials and dimensions indicated.  Include heavy-duty frames and grates.

G. Combination Inlets:  Vertical curb and horizontal gutter openings, of materials and dimensions indicated.  Include heavy-duty frames and grates.

Retain paragraph below with either of last two paragraphs above.

H. Frames and Grates:  Dimensions, opening pattern, free area, and other attributes indicated.

See Division 5 Section "Gratings" for fabricated-steel grating.

2.17 STORMWATER DETENTION STRUCTURES

Detail these structures.  They are usually made of cast-in-place concrete or sections of large piping and often include features for special applications.

A. Cast-in-Place Concrete, Stormwater Detention Structures:  Construct of reinforced-concrete bottom, walls, and top; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44), heavy-traffic, structural loading; of depth, shape, dimensions, and appurtenances indicated.

1. Ballast:  Increase thickness of concrete, as required to prevent flotation.

Delete first subparagraph below if grade rings are not required and edit "Manhole Frames and Covers" Paragraph if frame will be cast in concrete top.

2. Grade Rings:  Include 2 or 3 reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch- diameter frame and cover.

B. Manhole Frames and Covers:  ASTM A 536, Grade 60-40-18, ductile-iron castings designed for heavy-duty service.  Include 24-inch ID by 7- to 9-inch riser with 4-inch minimum width flange, and 26-inch- diameter cover.  Include indented top design with lettering "STORM SEWER" cast into cover.

2.18 PIPE OUTLETS

Revise this Article to suit Project, and detail on Drawings.  Delete first paragraph below if piping includes flared outlet fittings and concrete head walls are not required.

A. Head Walls:  Cast-in-place reinforced concrete, with apron and tapered sides.

B. Riprap Basins:  Broken, irregular size and shape, graded stone according to NSSGA's "Quarried Stone for Erosion and Sediment Control."

Retain one of three subparagraphs below or insert another grade.  Refer to NSSGA's "Quarried Stone for Erosion and Sediment Control" for sizes.

1. Average Size:  NSSGA No. R-3, screen opening 2 inches.

2. Average Size:  NSSGA No. R-4, screen opening 3 inches.

3. Average Size:  NSSGA No. R-5, screen opening 5 inches.

Delete two paragraphs below unless these sizes of stone are required.

C. Filter Stone:  According to NSSGA's "Quarried Stone for Erosion and Sediment Control," No. FS-2, No. 4 screen opening, average-size, graded stone.

D. Energy Dissipaters:  According to NSSGA's "Quarried Stone for Erosion and Sediment Control," No. A-1, 3-ton average weight armor stone, unless otherwise indicated.

2.19 MISCELLANEOUS MATERIALS

Retain this Article if painting of concrete manholes or ferrous frames and covers is required.

A. Paint:  SSPC-Paint 16.

B. PE Sheeting:  ASTM D 4397, with at least 8-mil thickness or other equivalent, impervious material.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Excavation, trenching, and backfilling are specified in Division 2 Section "Earthwork."

3.2 PIPING APPLICATIONS

A. Pipe couplings and special pipe fittings with pressure ratings at least equal to piping rating may be used in applications below, unless otherwise indicated.

1. Use nonpressure-type flexible couplings where required to join gravity-flow, nonpressure sewer piping, unless otherwise indicated.

a. Shielded flexible or rigid couplings for same or minor difference OD pipes.

b. Ring-type flexible couplings for piping of different sizes where annular space between smaller piping's OD and larger piping's ID permits installation.

2. Use pressure-type pipe couplings for force-main joints.

B. Special Pipe Fittings:  Use for pipe expansion and deflection.  Pipe couplings and special pipe fittings with pressure ratings at least equal to piping rating may be used in applications below, unless otherwise indicated.

Retain option in paragraph below to allow Contractor to select piping materials from those retained.

C. Gravity-Flow, Nonpressure Sewer Piping:  Use any of the following pipe materials for each size range:

Retain one or more of nine subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.
1. NPS 3:  PVC water-service pipe; PVC Schedule 40, water-service-pipe fittings; and solvent-cemented joints.
2. NPS 3:  NPS 4 PVC sewer pipe and fittings; gaskets; and gasketed joints.
3. NPS 4 and NPS 6:  Cellular-core PVC pipe, PVC sewer pipe fittings, and solvent-cemented joints.
4. NPS 4 and NPS 6:  PVC sewer pipe and fittings, gaskets, and gasketed joints.
5. NPS 8 to NPS 12:  Cellular-core PVC pipe, PVC sewer pipe fittings, and solvent-cemented joints.
6. NPS 8 to NPS 12:  PVC sewer pipe and fittings, gaskets, and gasketed joints.
7. NPS 8 to NPS 12:  PVC profile gravity sewer pipe and fittings, gaskets, and gasketed joints.
8. NPS 15:  PVC sewer pipe and fittings, gaskets, and gasketed joints.
9. NPS 15:  PVC profile gravity sewer pipe and fittings, gaskets, and gasketed joints.

3.3 PIPING INSTALLATION

A. General Locations and Arrangements:  Drawing plans and details indicate general location and arrangement of underground storm drainage piping.  Location and arrangement of piping layout take design considerations into account.  Install piping as indicated, to extent practical.  Where specific installation is not indicated, follow piping manufacturer's written instructions.

B. Install piping beginning at low point, true to grades and alignment indicated with unbroken continuity of invert.  Place bell ends of piping facing upstream.  Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements.

C. Install manholes for changes in direction unless fittings are indicated.  Use fittings for branch connections unless direct tap into existing sewer is indicated.

D. Install proper size increasers, reducers, and couplings where different sizes or materials of pipes and fittings are connected.  Reducing size of piping in direction of flow is prohibited.

E. Tunneling:  Install pipe under streets or other obstructions that cannot be disturbed by tunneling, jacking, or a combination of both.

F. Install gravity-flow, nonpressure drainage piping according to the following:

Revise three subparagraphs below to suit Project.

1. Install piping pitched down in direction of flow, at minimum slope of 1 percent, unless otherwise indicated.

2. Install piping NPS 6 and larger with restrained joints at tee fittings and at changes in direction.  Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place concrete supports or anchors.

Retain subparagraph above or first subparagraph below.

3. Install piping below frost line.

4. Install PVC sewer piping according to ASTM D 2321 and ASTM F 1668.

5. Install PVC profile gravity sewer piping according to ASTM D 2321 and ASTM F 1668.

6. Install reinforced-concrete sewer piping according to ASTM C 1479 and ACPA's "Concrete Pipe Installation Manual."

Retain paragraph and subparagraphs below only if required.

3.4 PIPE JOINT CONSTRUCTION

A. Where specific joint construction is not indicated, follow piping manufacturer's written instructions.

B. Join gravity-flow, nonpressure drainage piping according to the following:

1. Join hub-and-spigot, cast-iron soil piping with gasket joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for compression joints.

2. Join PVC sewer piping according to ASTM D 2321 and ASTM D 3034 for elastomeric-seal joints or ASTM D 3034 for elastomeric gasket joints.

3. Join PVC profile gravity sewer piping according to ASTM D 2321 for elastomeric-seal joints or ASTM F 794 for gasketed joints.

4. Join dissimilar pipe materials with nonpressure-type flexible[ or rigid] couplings.

C. Join force-main pressure piping according to the following:

1. Join PVC pressure piping according to AWWA M23 for gasketed joints.

2. Join PVC water-service piping according to ASTM D 2855 for solvent-cemented joints.

D. Join dissimilar pipe materials with pressure-type couplings.

3.5 CLEANOUT INSTALLATION

A. Install cleanouts and riser extension from sewer pipe to cleanout at grade.  Use cast-iron soil pipe fittings in sewer pipes at branches for cleanouts and cast-iron soil pipe for riser extensions to cleanouts.  Install piping so cleanouts open in direction of flow in sewer pipe.

1. Use light-duty, top-loading classification cleanouts in earth or unpaved foot-traffic areas.

2. Use medium-duty, top-loading classification cleanouts in paved foot-traffic areas.

3. Use heavy-duty, top-loading classification cleanouts in vehicle-traffic service areas.

4. Use extra-heavy-duty, top-loading classification cleanouts in roads areas.

B. Set cleanout frames and covers in earth in cast-in-place concrete block, 18 by 18 by 12 inches deep.  Set with tops 1 inchabove surrounding earth grade.

C. Set cleanout frames and covers in concrete pavement with tops flush with pavement surface.

3.6 DRAIN INSTALLATION

A. Install type of drains in locations indicated.

1. Use light-duty, top-loading classification drains in earth or unpaved foot-traffic areas.

2. Use medium-duty, top-loading classification drains in paved foot-traffic areas.

3. Use heavy-duty, top-loading classification drains in vehicle-traffic service areas.

4. Use extra-heavy-duty, top-loading classification drains in roads areas.

B. Embed drains in 4-inch minimum depth of concrete around bottom and sides.

C. Fasten grates to drains if indicated.

D. Set drain frames and covers with tops flush with pavement surface.

E. Assemble trench sections with flanged joints.

F. Embed trench sections in 4-inch minimum concrete around bottom and sides.

3.7 MANHOLE INSTALLATION

A. General:  Install manholes, complete with appurtenances and accessories indicated.

B. Install precast concrete manhole sections according to ASTM C 891.

Cast-in-place manholes in paragraph below require data or details on Drawings.

C. Construct cast-in-place manholes as indicated.

Retain first paragraph below if paint is to be field applied to exterior surfaces of cast-in-place concrete manholes.

D. Install PE sheeting on earth where cast-in-place-concrete manholes are to be built.

E. Set tops of frames and covers flush with finished surface of manholes that occur in pavements.  Set tops 3 inches above finished surface elsewhere, unless otherwise indicated.

3.8 CATCH BASIN INSTALLATION

A. Construct catch basins to sizes and shapes indicated.

B. Set frames and grates to elevations indicated.

3.9 STORMWATER INLET AND OUTLET INSTALLATION

A. Construct inlet head walls, aprons, and sides of reinforced concrete, as indicated.

B. Construct riprap of broken stone, as indicated.

C. Install outlets that spill onto grade, anchored with concrete, where indicated.

D. Install outlets that spill onto grade, with flared end sections that match pipe, where indicated.

E. Construct energy dissipaters at outlets, as indicated.

3.10 CONCRETE PLACEMENT

A. Place cast-in-place concrete according to ACI 318/318R.

3.11 CONNECTIONS

A. Connect nonpressure, gravity-flow drainage piping in building's storm building drains.

B. Connect force-main pressure piping to building's storm drainage force mains.  Terminate piping where indicated.

1. Use commercially manufactured wye fittings for piping branch connections.  Remove section of existing pipe; install wye fitting into existing piping; and encase entire wye fitting, plus 6-inch overlap, with not less than 6 inches of concrete with 28-day compressive strength of 3000 psi.

2. Make branch connections from side into existing piping, NPS 4 to NPS 20.  Remove section of existing pipe; install wye fitting into existing piping; and encase entire wye with not less than 6 inches of concrete with 28-day compressive strength of 3000 psi.

3. Make branch connections from side into existing piping, NPS 21 or larger, or to underground manholes and structures by cutting opening into existing unit large enough to allow 3 inches of concrete to be packed around entering connection.  Cut end of connection pipe passing through pipe or structure wall to conform to shape of and be flush with inside wall, unless otherwise indicated.  On outside of pipe, manhole, or structure wall, encase entering connection in 6 inches of concrete for minimum length of 12 inches to provide additional support of collar from connection to undisturbed ground.

a. Use concrete that will attain a minimum 28-day compressive strength of 3000 psi, unless otherwise indicated.

b. Use epoxy-bonding compound as interface between new and existing concrete and piping materials.

4. Protect existing piping, manholes, and structures to prevent concrete or debris from entering while making tap connections.  Remove debris or other extraneous material that may accumulate.

C. Connect to sediment interceptors.

3.12 IDENTIFICATION

A. Materials and their installation are specified in Division 2 Section "Earthwork." Arrange for installation of green warning tape directly over piping and at outside edge of underground structures.

1. Use warning tape or detectable warning tape over ferrous piping.

2. Use detectable warning tape over nonferrous piping and over edges of underground structures.

3.13 FIELD QUALITY CONTROL

A. Inspect interior of piping to determine whether line displacement or other damage has occurred.  Inspect after approximately 24 inches of backfill is in place, and again at completion of Project.

1. Submit separate reports for each system inspection.

2. Defects requiring correction include the following:

a. Alignment:  Less than full diameter of inside of pipe is visible between structures.

b. Deflection:  Flexible piping with deflection that prevents passage of ball or cylinder of size not less than 92.5 percent of piping diameter.

c. Crushed, broken, cracked, or otherwise damaged piping.

d. Infiltration:  Water leakage into piping.

e. Exfiltration:  Water leakage from or around piping.

3. Replace defective piping using new materials, and repeat inspections until defects are within allowances specified.

4. Reinspect and repeat procedure until results are satisfactory.

B. Test new piping systems, and parts of existing systems that have been altered, extended, or repaired, for leaks and defects.

1. Do not enclose, cover, or put into service before inspection and approval.

2. Test completed piping systems according to authorities having jurisdiction.

3. Schedule tests and inspections by authorities having jurisdiction with at least 24 hours' advance notice.

4. Submit separate report for each test.

Retain test in first subparagraph and associated subparagraphs below only if required.

5. Gravity-Flow Storm Drainage Piping:  Test according to requirements of authorities having jurisdiction, UNI-B-6, and the following:

a. Exception:  Piping with soiltight joints unless required by authorities having jurisdiction.

b. Option:  Test plastic piping according to ASTM F 1417.

C. Leaks and loss in test pressure constitute defects that must be repaired.

D. Replace leaking piping using new materials, and repeat testing until leakage is within allowances specified.

3.14 CLEANING

A. Clean interior of piping of dirt and superfluous materials and Flush with potable water.
END OF DOCUMENT 221400
STORM DRAINAGE

221400 - 17

