ST. TAMMANY FIRE PROTECTION DISTRICT NO. 1

FIRE STATION #10

2745 LAKESHORE VISTA BLVD

SLIDELL, LA 70461


Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233800
RESIDENTIAL STYLE-KITCHEN HOODS WITH ANSUL
This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY – NOT USED

1.2 ACTION SUBMITTALS

A. Product Data: For the following:

1. Fire-suppression systems.

2. Lighting fixtures.

Retain paragraph and subparagraphs below if products are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review engineering data as another way to verify product's compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

1.3 QUALITY ASSURANCE

Retain first paragraph below if welding is required. Retain "Welding certificates" Paragraph in "Informational Submittals" Article if retaining below. AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

A. Welding: Qualify procedures and personnel according to AWS D1.1/D 1.1M, "Structural Welding Code - Steel," for hangers and supports; and AWS D9.1/D9.1M, "Sheet Metal Welding Code," for joint and seam welding.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

PART 2 -  PRODUCTS

2.1 EXHAUST HOOD FABRICATION

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below for listed hoods. See Section 016000 "Product Requirements."
A. Basis-of-Design Product: Subject to compliance with requirements, provide Accurex Model XRRS or a comparable product by one of the following:
1. Greenheck Model GRRS.
B. Hood System shall be constructed with 304 stainless steels, having a fire suppression system pre-engineered into the design of the hood.  Actuation of the fire suppression system shall be mechanically based on industry standard “fail safe” fusible link technology.  

C. The system shall have an Advanced Programmable Logic Control Driven Self-Monitoring System that interacts with the cooking environment to minimize the risk of a fire event while also monitoring the suppression system for continuity. 
2.2 FIRE-SUPPRESSION SYSTEM

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of first three paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."
A. System shall be fully integrated, self-contained Fire Suppression Range Hood for Residential Appliances for use in protecting Residential-grade appliances when used in public or otherwise commercial spaces.  The system shall use a wet chemical agent, tested and demonstrated to conform to UL subject 300A.
PART 3 -  EXECUTION

3.1 INSTALLATION

Indicate field joints and methods of connection on Drawings. Coordinate with NSF requirements.

A. Complete field assembly of hoods where required.

1. Make closed butt and contact joints that do not require filler.

2. Grind field welds on stainless-steel equipment smooth, and polish to match adjacent finish. 

Verify maintenance clearance requirements of authorities having jurisdiction. Indicate minimum clearances on Drawings and revise paragraph below to suit Project.

B. Install hoods and associated services with clearances and access for maintaining, cleaning, and servicing hoods, filters/baffles, grease extractor, and fire-suppression systems according to manufacturer's written instructions and requirements of authorities having jurisdiction.

Retain first paragraph below if Type I hoods and associated services require on-site modification.

C. Make cutouts in hoods where required to run service lines and to make final connections, and seal openings according to UL 1978.

D. Securely anchor and attach items and accessories to walls, floors, or bases with stainless-steel fasteners, unless otherwise indicated.

E. Install hoods to operate free from vibration.

Retain first paragraph below and verify requirements of authorities having jurisdiction if Project requires seismic design.

F. Install trim strips and similar items requiring fasteners in a bed of sealant. Fasten with stainless-steel fasteners at 48 inches o.c. maximum.

G. Install sealant in joints between equipment and abutting surfaces with continuous joint backing, unless otherwise indicated. Provide airtight, watertight, vermin-proof, sanitary joints.

H. Install lamps, with maximum recommended wattage, in equipment with integral lighting.

I. Set initial temperatures, and calibrate sensors.

J. Set field-adjustable switches.

K. Connect ducts according to requirements in Section 23330 "Air Duct Accessories." Install flexible connectors on makeup air supply duct(s). Weld exhaust-duct connections with continuous liquid-tight joint.

L. Install fire-suppression piping for remote-mounted suppression systems according to NFPA 17A, "Wet Chemical Extinguishing Systems."

3.2 FIELD QUALITY CONTROL

Retain one of first two paragraphs below that identify who shall perform tests and inspections.

Retain paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections. Report results in writing.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

C. Tests and Inspections:

1. Test each equipment item for proper operation. Repair or replace equipment that is defective, including units that operate below required capacity or that operate with excessive noise or vibration.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

3. Perform hood performance tests required by authorities having jurisdiction.

4. Perform fire-suppression system performance tests required by authorities having jurisdiction.

D. Prepare test and inspection reports.

END OF SECTION 233800
	RESIDENTIAL STYLE-KITCHEN HOODS WITH ANSUL
	233800 - 2



