December 15, 2003

Mr. David Copenal

Parish of St. Tammany

P.O. Box 628

Covington, LA  70434

RE:
59 Barn – North Street, Abita Springs

Here is a list of items that the contractor has not finished with the schedule of values.

1) The hose reel pipes located in the service area are connected backwards on the column (air & oil). Also the underground pipes connecting the hose reel from the fuel shed are leaking. At the time of inspection the sub contractor was contacted to make the repairs. $400.00

2) The electrical waste oil pneumercator located in the service area is not hooked up. $100.00

3) All of the steel pipe for the supply oil, waste oil and air lines need to be painted. $250.00

4) The painted steel stairs located in the service area need to be touched up. $75.00

5) The trap primer drain in the 1st floor bathroom needs to be uncovered and the trap primer adjusted. $75.00

6) The ADA grab bar behind the toilet needs to be reinstalled with a 36” grab bar. $100.00

7) Clean and touchup paint all doors and jambs. $150.00

8) Touchup paint on all interior walls. $125.00

9) Reinstall baseboard in the office areas. $75.00

10) The Fire Alarm & Security Alarm needs to be completely hooked up. $325.00

11) The maintenance area roof has two leaks; these holes need to be repaired. Due to these leaks the vinyl back insulation has fallen. Also two down spouts are leaking. $275.00

12) All plumbing vent stacks in the main bldg. do not have any pipe boots. Also some of the elbows were noted not to be glued together. $225.00

13) The vent/light in the 2nd floor shower area needs a light bulb and the cover installed. $25.00

14) The 2nd floor shower area needs to be cleaned. $125.00

15) The mechanical room up stairs needs to be cleaned and all floor penetrations shall be sealed. $200.00

16) All doors need to be re keyed. $75.00

17) Tag all Fire Extinguishers. $25.00

18) One Weatherproof exterior light on the fuel shed was noted to be burned out with water inside of it. $100.

19) All end caps on the fuel-shed roof are missing. $275.00 

If you have any questions, or require any further information, please call.

Sincerely,

Chuck Dammon/Project Manager

