June 1, 2004

Mr. Kenneth Mc Cants

State of Louisiana

Department of Public Safety and Corrections

Office of State Fire Marshal Code Enforcement

 And Building Safety.

5150 Florida Blvd.

Baton Rouge, Louisiana 70806

RE: P0263012

       Laura Maffie Dance Works

       Slidell, La. 70458

Dear Mr. Mc Cants

I spoke to you last week about a problem with the position of the skylights we have for this job. Our original design was to have the skylights in the center of the hall, between the firewalls. Subsequently the contractor has installed the four skylights over the firewalls. Please see the attached sketch.

Using UL#U432 for the fire rating, it states to connect to the floor and ceiling assembly with steel fasteners spaced 24” O.C. It does not state that the floor or ceiling has to be rated. The contractor will install clips on the skylight to secure the stud per the UL. Also he will run the sheet rock tight to the skylight and fire caulk the where the two meet.

We are asking for your approval of this installation. Please call me with any question you may have.

Sincerely,

Chuck Dammon

VP/Project Manager

